NBSIR 85-3144-1

ASET-B: A ROOM FIRE PROGRAM

FOR PERSONAL COMPUTERS

William D. Walton

U.S. DEPARTMENT OF COMMERCE

National Bureau of Standards

National Engineering Laboratory

Center for Fire Research

Gaithersburg, MD 20899

Revised December 1985

Supported in part by:

National Park Service

Washington, DC

and

Department of Health and Human Services

Washington, DC

TABLE OF CONTENTS

Page

LIST OF FIGURES  . . . . . . . . . . . . . . . . . . . . . . . iv

Abstract   . . . . . . . . . . . . . . . . . . . . . . . . . .  1

1.  INTRODUCTION   . . . . . . . . . . . . . . . . . . . . . .  2

2.  DESCRIPTION OF THE MODEL   . . . . . . . . . . . . . . . .  4

3.  SOLUTION OF THE EQUATIONS  . . . . . . . . . . . . . . . .  7

4.  STRUCTURE OF THE COMPUTER PROGRAM  . . . . . . . . . . . . 10

4.1  General Structure  . . . . . . . . . . . . . . . . . 10

4.2  Program Sections   . . . . . . . . . . . . . . . . . 11

4.2.1  Input and Initialization Section  . . . . . . 11

4.2.2  Equation Solving Section  . . . . . . . . . . 13

4.2.3  Subroutine to Calculate Heat Release Rate   . 13

4.2.4  Output Subroutine   . . . . . . . . . . . . . 14

5.  RUNNING THE PROGRAM  . . . . . . . . . . . . . . . . . . . 15

5.1  General Instructions   . . . . . . . . . . . . . . . 15

5.2  Program Inputs   . . . . . . . . . . . . . . . . . . 16

5.2.1  Title   . . . . . . . . . . . . . . . . . . . 16

5.2.2  Heat Loss Fraction  . . . . . . . . . . . . . 16

5.2.3  Height if the Base of the Fire  . . . . . . . 17

5.2.4  Room Ceiling Height and Floor Area  . . . . . 18

5.2.5  Maximum Time  . . . . . . . . . . . . . . . . 18

5.2.6  Heat Release Rate   . . . . . . . . . . . . . 18

5.3  Program Outputs  . . . . . . . . . . . . . . . . . . 21

6.  USE AND LIMITATIONS OF THE ASET-B RESULTS  . . . . . . . . 21

6.1  Evaluating Fire Safety Objectives  . . . . . . . . . 21

6.2  Using ASET-B for Multiple Rooms  . . . . . . . . . . 23

6.3  Program Limitations  . . . . . . . . . . . . . . . . 23

6.4  Program Verification   . . . . . . . . . . . . . . . 25

7.  TRANSPORTING THE PROGRAM . . . . . . . . . . . . . . . . . 25

8.  ACKNOWLEDGEMENTS   . . . . . . . . . . . . . . . . . . . . 27

9.  REFERENCES   . . . . . . . . . . . . . . . . . . . . . . . 27

APPENDIX A:  ASET-B PROGRAM LISTING  . . . . . . . . . . . . . 29

APPENDIX B:  VARIABLE NAMES USED IN ASET-B   . . . . . . . . . 31

APPENDIX C:  SAMPLE RUN OF ASET-B PROGRAM  . . . . . . . . . . 34

APPENDIX D:  HEAT RELEASE RATE FOR THE SEMI-UNIVERSAL FIRE . . 36

iii

LIST OF FIGURES

Page

Figure 1.  Schematic of fire phenomena   . . . . . . . . . . . 28

iv

ASET-B: A ROOM FIRE PROGRAM FOR PERSONAL COMPUTERS

William D. Walton

ABSTRACT

ASET-B,  a personal computer program for predicting the fire

environment  in a single room,  is presented.  ASET-B solves  the

same  differential equations as the previously developed computer

program,  ASET  (Available  Safe Egress Time),  using  a  simpler

numerical technique. ASET-B requires as input the height and area

of the room,  the elevation of the fire above the floor,  a  heat

loss factor,  and a fire specified in terms of heat release rate.

The program predicts the thickness and the temperature of the hot

smoke layer as a function of time. ASET-B is written in BASIC and

is not subject to copyright. This paper describes the program and

its use.  Included are a listing of the program, program variable

name listing and a sample run. A discussion of user modifications

also is given.

Key Words: compartment fires; computer programs; evacuation; fire

growth; manuals; mathematical models; room fires; smoke.

1

1.  INTRODUCTION

In  1980  L.  Y.  Cooper  of the Center for  Fire  Research,

National  Bureau  of Standards introduced  ASET,  a  mathematical

model for estimating Available Safe Egress Time in fires [1]*. In

1982,  Cooper  with  D.  Stroup published a computer  program  to

perform the calculations in the mathematical model [2], thus, the

computer  program  also  became known  as  ASET.   ASET  was  not

specifically   written  for  the  personal  computer  environment

because  at the time it was being developed,  personal  computers

were  just emerging as a tool for use in the engineering  office.

Since the introduction of ASET, the use of personal computers has

become  widespread  and there has been  significant  interest  in

running ASET on personal computers. In response to this interest,

this  paper introduces ASET-B,  a program for personal  computers

based  on the original ASET mathematical model.  The B is used to

indicate basic, brief, BASIC and Beta.

Most  larger personal computers,  when properly  configured,

can  run the original ASET program.  There are  however,  several

reasons  why  ASET  is not the most appropriate program  for  the

personal computers widely used today.  ASET is written in FORTRAN

and  consists  of over 1500 program lines.  Although  FORTRAN  is

available  on many personal computers,  BASIC is by far the  most

popular programming language.   To make ASET-B easy to distribute

______________________________

*  Figures in brackets indicate literature references at the  end

of this report.

2

and allow the user to make modifications,  it has been written in

BASIC.  A second reason that ASET may not be appropriate for some

personal  computers,  is its size and run time.  ASET has a  wide

variety  of features which allow the user to run multiple  cases,

identify  endpoints and calculate species  concentrations.  These

features increase program size,  input ,  output and run time. In

developing  ASET-B  it was decided to make the program as  simple

and fast as possible,  while providing the same essential  output

information produced by ASET. While ASET-B can be used to address

a wide variety of problems,  it can also serve as an introduction

to the more comprehensive ASET.

ASET-B  as a program looks very different from the  original

ASET.  ASET-B  consists  of approximately 100  program  lines  in

BASIC.  Most  of the variable names have been changed in order to

make the program more compact and easier to follow.  The multiple

run  options  have  been eliminated as well  as  the  ability  to

calculate   species  concentrations  and  automatically  identify

endpoints. With these exceptions, the primary equations solved by

ASET  and ASET-B are identical.  The most significant  change  in

ASET-B  is the use of a different mathematical procedure to solve

the primary equations.  ASET-B employs an equation solver that is

at least 5 times faster than that used in ASET,  while  retaining

mathematical  agreement  to within a fraction of  a  percent.  It

reduces  the time for an average run on a typical 16 bit personal

computer from over 5 minutes to under 1 minute.

3

2.  DESCRIPTION OF THE MODEL

The mathematical model which is the basis for ASET and  thus

ASET-B has been presented in detail by Cooper [1,3],  and will be

only  summarized here.  It is based on a single room or enclosure

with all doors,  windows or vents closed except for a small  leak

at  floor level.  This leak prevents the pressure from increasing

in the room.  A fire starts at some point  below the ceiling  and

releases  energy  and products of combustion.  The rate at  which

energy  and products of combustion are released may  change  with

time.  The hot products of combustion form a plume,  which due to

buoyancy, rises towards the ceiling. As the plume rises, it draws

in cool air from the room which decreases the plume's temperature

and  increases its volume flow rate.  When the plume reaches  the

ceiling it spreads out and forms a hot gas layer,  which descends

with time as the plume's gases continue to flow into it. There is

a relatively sharp interface between the hot upper layer and  the

air in the lower part of room,  which in this model is considered

to  be  at ambient temperature.  The only interchange between the

air  in  the lower part of the room and the hot  upper  layer  is

through  the  plume.  ASET could therefore be described as a  two

layer  or  zone  model.   The  basic  fire  phenomena  are  shown

schematically in figure 1.

The  two unknowns in ASET-B are the height of the hot  layer

interface above the fire,  Z,  and the average temperature of the

upper layer,  P.  It should be noted that  the notation used here

to describe the model is consistent with the variable names  used

4

in  the  computer  program.  The unknowns,  Z and  P,  are  often

referred to as the (dimensionless) height and temperature of  the

smoke layer since,  consistent with the model formulation,  smoke

can only be found in the plume and the hot upper layer. The known

quantities  are  the area and height of the room,  A and  H,  the

height  of  the base of the fire above  the  floor,  F,  and  the

acceleration  due  to  gravity,   G.  In  addition,  the  ambient

temperature,  PA, density, DA, and specific heat, CP, of air must

be  known.  The final known quantities are the rate at which heat

is released by the fire as a function of time,  QT,  the fraction

of  the total heat release which is given off as  radiation,  LR,

and the fraction of total heat release rate which is lost to  the

contents and surrounding surfaces of the room, LC.

The  unknown height and temperature are determined by  using

conservation  of  mass and energy in conjunction  with  equations

describing  the  plume.  Since the height and temperature of  the

smoke layer will vary with time,  T, their solutions are obtained

by  solving   two  differential  equations.   In  developing  the

original  equations for ASET [1,3],  two dimensionless groups  of

problem parameters,  C1 and C2,  were introduced. Also introduced

were  dimensionless  forms  of the  variables  time,  height  and

temperature  of  the smoke layer,  initial height  of  the  smoke

layer,  height  of  the  base of the fire and the  rate  of  heat

release.  These variables are made dimensionless by dividing them

by  a characteristic quantity with the same dimensions or  units.

Thus the dimensionless temperature,  P, is the actual temperature

5

of the smoke layer,  PF (converted to R),  divided by the ambient

temperature,  PA (R).  Similarly,  the dimensionless rate of heat

release, QT, is the actual rate of heat release, QA (kW), divided

by  the  initial rate of heat  release,  Q0  (kW).  Finally,  the

dimensionless variables,  height of the smoke layer,  Z,  initial

height  of  the smoke layer,  Z0,  and height of the base of  the

fire,  F,  are the dimensional values for these variables in feet

divided by a characteristic length CL which is also in feet. Here

as in the ASET program,  CL is simply taken as one foot. Thus the

dimensionless lengths Z,  Z0 and F are the same as their physical

lengths in feet.  The dimensionless time,  T,  is the actual time

divided  by  a  characteristic  time,  CT,  of  one  second.  The

dimensionless  time,  T,  is therefore numerically equal  to  the

actual  time  in seconds.  Since engineering units are   used  in

ASET,  this  convention has been continued here for  consistency.

Conversion to SI units is provided in the computer program.

The  differential equations for the dimensionless height  of

the  layer  above the fire,  Z,  and average temperature  of  the

layer, P, are given below.

dZ     -C1*QT-C2*QT^(1/3)*Z^(5/3)   0<Z<=Z0

-- =   -C1*QT                       -F<Z<=0

dT      0                           Z=-F

dP      P*[C1*QT-(P-1)*C2*QT^(1/3)*Z^(5/3)]/(Z0-Z)   0<Z<Z0

-- =    P*C1*QT/(Z0-Z)                               -F<=Z<=0

dT

C1=(1-LC)*Q0*CT/(DA*CP*PA*A*CL)

C2=(0.21*CT/A)[(1-LR)*Q0*G*CL^2/(DA*CP*PA)]^(1/3)

6

In  order  to  solve the equations for Z and P  the  initial

conditions  must be known.  One set of initial  conditions  which

were  derived in [1,3],  and will be used here,  assume that  the

fire  starts  with a small heat release rate,  Q0,  at time  T=0.

Under such conditions the initial conditions are.

Z=Z0

P=1+Z0^(-5/3)*C1/C2

Although dP/dT is indeterminate in the above equation at T=0  its

actual value has been found in [1,3] to be.

dP/dT=(C1/C2)[2*DQ0+5*(C1+C2*Z0^(5/3))]/(6*Z0^(8/3))

Where DQ0=dQT/dT at time T=0.

3.   SOLUTION OF THE EQUATIONS

In general, the differential equations for Z and P cannot be

solved  explicitly,  that is,  an algebraic expression cannot  be

written which describes Z and P at any time T.  As a result,  the

equations   must   be  solved  numerically.   ASET   solves   the

differential  equations  using  a variation of  the  fourth-order

Runge-Kutta method with variable time step. While this method has

a  high  degree  of accuracy,  it has been  determined  that  the

improved Euler's method has sufficient accuracy for this problem.

The improved Euler's method is a simple predictor-corrector  type

and  is  described in most books on numerical  methods  [4].  The

improved  Euler's  method used in ASET-B  requires  substantially

fewer  calculations  than the method used in ASET,  resulting  in

ASET-B running much faster than ASET.

7

The  improved  Euler's  method  as  applied  in  ASET-B   is

basically  a technique for stepping the solution forward in time.

Given the values of Z and P at a particular time,  T,  the method

is used to determine the values of Z and P at time,  T+DT,  where

DT is a small time increment. This process is started at time T=0

and  continued until Z and P are known at all times of  interest.

In the case of ASET-B an increment of 1 second has been found  to

yield  results  which  agree  well  with  ASET  for  problems  of

practical interest.

In ASET-B,  Z1 and P1,  are used to indicate the values of Z

and P at time, T. For the first step these are the initial values

at time,  T=0. Z2 and P2 are used to indicate the values of Z and

P  to be calculated at time,  T+DT.  To determine Z2 and P2 it is

observed  that the differential equations for Z and  P  represent

the  time  rate of change of these quantities.  The time rate  of

change multiplied by the time step yields the change which occurs

over  the  time  step.  This  would be an  exact  result  if  the

equations  were linear or the time steps were  infinitely  small.

Since the equations are nonlinear,  and it is impractical to make

the time step infinitely small, an approximation must be used. In

the improved Euler's method,  Z2 and P2 are first predicted using

the  derivatives  evaluated  at time,  T.  Using Z2  and  P2  the

derivatives are then evaluated at time, T+DT. Corrected values of

Z2   and  P2  are  then  calculated  using  the  average  of  the

derivatives  evaluated  at times T,  and,  T+DT.  Z2 and  P2  are

predicted by

8

Z2=Z1+DZ1*DT

P2=P1+DP1*DT

where DZ1=dZ/dT and DP1=dP/dT are evaluated using Z=Z1 and  P=P1.

The derivatives at time T+DT,  DZ2=dZ/dT and DP2=dP/dT,  are then

evaluated using Z=Z2 and P=P2. Corrected values for Z2 and P2 are

calculated using the average derivatives.

Z2C=Z1+[(DZ1+DZ2)/2]*DT

P2C=P1+[(DP1+DP2)/2]*DT

The  predicted  values of Z and P are then compared  to  the

corrected  values.  In  ASET-B  if  the  absolute  value  of  the

difference  between  the predicted and corrected values  is  less

than 0.001,  the solution is considered to have converged and the

program  proceeds  to the next time step.  If the  difference  is

greater  than  0.001  the predicted values become  the  corrected

values and the derivatives at time,  T+DT,  are recalculated. New

corrected values are then calculated. In ASET-B this procedure is

repeated  for a maximum of thirty times.  If the differences  are

still greater than 0.001,  a warning is printed,  and the program

proceeds to the next time step.

The  evaluation of the derivatives of Z and P  requires  the

dimensionless heat release rate,  QT,  be known for all times, T.

For  heat release rates which are not constant with time,  ASET-B

requires  the heat release be specified for each one second  time

interval. To simplify this procedure, ASET-B uses point specified

heat release rates with linear interpolation.  Heat release rates

9

can  be  specified  at as many as  100  different  times.  Linear

interpolation  is  then performed to determine the  heat  release

rate at each time step.

4.  STRUCTURE OF THE COMPUTER PROGRAM

4.1  General Structure

ASET-B  is structured to be easy to understand  and  modify,

while  being adaptable to a variety of computers.  In some  cases

these  objectives  conflict  since  BASIC  is  not  a  structured

programming language and the implementation of BASIC varies among

computers. As a result, some of the so called rules of structured

programming have not been followed in favor of a program that can

be  adapted  to most forms of the BASIC programming  language.  A

listing  of  the program is given in appendix A and an  index  of

variable  names  in  appendix B.  In order to  make  the  listing

compact, all documentation is provided in the text of this paper.

ASET-B  is designed to be easy to modify as well as easy  to

use. It is intended to serve as a base program which the user can

modify to meet a particular set of needs.  Although the number of

possible  user  modifications is almost  unlimited,  comments  on

several typical modifications have been provided with the program

description.  If  user modifications are made to the  program,  a

comment  should  be added to the header printed in lines  10  and

440.  This will indicate that the program has user  modifications

and is not the standard program.

10

4.2  Program Sections

The  program  consists of four major  sections.  The  first,

lines  10-530,  reads  and writes the required input  data,  sets

initial parameters and performs initial calculations. The second,

lines 540-870,  consists of the calculations required to step the

solution through time. Finally, lines 880 to 960 are a subroutine

which calculates the rate of heat release of the fire,  and lines

970  to  1080  a  subroutine  which  writes  results.   A   brief

description of each of the sections is provided below.

4.2.1 Input and Initialization Section

The  first  section  of  the program can  be  subdivided  by

function. The input data is read, and unit conversions performed,

in lines 10-250. The units of input lengths and area are feet and

square  feet  respectively with conversion to meters  and  square

meters in lines 110-130. The units of these inputs may be changed

to meters and square meters by reversing the input variable names

and conversion factors in lines 80-130.  In line 60, the fraction

of  the  heat release rate of the fire which  is  instantaneously

lost by radiation for the combustion zone,  LR,  is set equal  to

0.35.  A  discussion  of this parameter which is called ALAMR  in

ASET can be found in [1].

The  input heat release rates are read and stored  in  lines

150-250.  The rate of heat release at time zero, Q0, has been set

11

at  0.1 kilowatts in line 150,  corresponding to an initial  fire

size  which approaches zero.  This value can be increased by  the

user  if needed.  ASET-B can accommodate 100 pairs of input times

and heat release rates.  While this number should be adequate for

most  cases it can be changed by substituting the new number  for

100  in  lines 40,  170 and 230.  The units for  the  input  heat

release  rates are kilowatts and may be changed to other units by

placing conversion factors in lines 200 and 210.

Lines 260-420 initialize variable values and perform initial

calculations. Several of the variables defined in these lines may

be modified to suit the user.  This may be accomplished by either

changing  the values within the program or by creating new prompt

questions and assigning the variables with input values. In lines

260 and 270 the ambient temperature,  PA, and density, DA, of air

may  be changed  to reflect an initial  temperature  other   than

70  F.  In line 410 the time interval for printing,  OI,  may  be

changed  from  its default value of 5 seconds.  The  results  are

calculated  for  every  second but are printed only at  the  time

interval specified by OI.

Lines  430-530  write out a summary of the input  data,  the

column headings for the subsequent output and the initial output.

Some users may desire this output to be sent to a printer or disk

file in addition to,  or in place of,  the output to the  screen.

The  techniques for accomplishing this vary with computer but the

most common are the use of LPRINT and PRINT#.  Similar techniques

may be used to read the input data from a disk file.

12

4.2.2  Equation Solving Section

The second section of the program, lines 540-870, solves the

differential equations following the methodology outlined earlier

in this report.  This section consists of two primary loops.  The

outer  loop  beginning  at  line  540  and  ending  at  line  860

corresponds  to a single time step.  The inner loop beginning  at

line 620 and ending at line 800 is repeated only if the  absolute

value  of  the  difference between the  predicted  and  corrected

values of either Z or P is greater than 0.001. This comparison is

made in line 750.

At  the  beginning  of  the  outer loop  are  two  checks  to

determine if the solution process should be terminated.  In  line

560 the current time,  T2, is compared to the maximum input time,

TL,  and  in  line 570 to the last time for which a heat  release

rate is specified,  TQ(NQ).  If the current time is greater  than

either  of  these  two  time limits the run  is  terminated  with

transfer to line 870.

4.2.3  Subroutine to Calculate Heat Release Rate

The  third section of the program consists of a  subroutine,

lines  880-960,  which calculates the rate of heat release of the

fire  and is called from the outer calculation loop at line  580.

This  subroutine  utilizes  the input rates of  heat  release  at

13

specified  times and performs linear interpolation  to  determine

the rate of heat release at each time step.  Although this method

of specifying the heat release rate is the most general, the user

may  wish  to modify the program to accept other models  of  fire

heat release. The ASET program for example can accommodate multi-

point exponential fire growth input. Other fire growth models can

be  inserted in place of,  or in addition to,  the existing point

specified  model.  This  is accomplished by modifying  the  input

section in lines 160-250 and subroutine in lines 880-960.

4.2.4  Output Subroutine

The second subroutine,  lines 970-1080,  is called from  the

outer calculation loop at line 850.  This subroutine converts the

dimensionless  variables  to  ones  with  units  and  writes  the

results. The particular variables printed in this subroutine have

been  selected to satisfy the needs of most users.  The speed  of

program  execution may be affected by the quantity of the output,

particularly if a printer is used. As a result, the user may want

to reduce the quantity of output to reduce the run time.  This is

accomplished  by eliminating the variables to be printed in  line

1070 and the corresponding column headings in lines 510 and  520.

There are two values calculated in this subroutine which have not

been  printed.  These are the rate of rise of temperature in  the

upper layer in degrees Fahrenheit,  RRF,  and Celsius,  RRC,  per

minute.  These  values  may be printed by adding  their  variable

names  to  the output list and including the  appropriate  column

14

headings. It should be noted that rate of rise of the upper layer

is  not  the same as the rate of rise in  a  heat  detector.  The

temperature of the heat sensing element is a function of the heat

transfer between the hot gas and the element.

ASET-B  produces  only  tabular output and has  no  specific

provisions for graphics. The reason is that graphics commands are

generally  dependent on the device which produces  the  graphics.

There  are however several methods by which graphics can be added

to ASET-B. The user may write the tabular results to a file which

can   be  read as input by a  commercial  graphics  routine.  The

results  can then be presented using the graphics commands in the

commercial routine.  Alternatively, the user may write a graphics

routine into the ASET-B program.

5.  RUNNING THE PROGRAM

5.1  General Instructions

ASET-B is written as an interactive program,  that  is,  the

program  prompts  the  user  with  questions.  The  mechanics  of

answering  the  questions is very  straightforward,  however  the

selection  of  the input data requires further  explanation.  The

procedure for loading and running the program will not be covered

in this paper, but can be found in the user's guide included with

the computer. When the program is started it will initially print

the program name,  a version number and a copyright  notice.  The

program will then print the first of seven questions and wait for

15

a  response  to  that question.  After the user  has  answered  a

question,  a  return or enter key is typed to register the answer

and  proceed to the next question.  No special error checking  is

provided  in the program so the user should carefully verify  all

entries. If an error is detected after the data has been entered,

the program must be terminated and restarted.

5.2  Program Inputs

5.2.1  Title

The  first  prompt question or input is a  run  title.  This

title  is used to identify the run and may consist of  characters

and/or numbers. The title will be printed at the beginning of the

output.

5.2.2  Heat Loss Fraction

The  second input is the  heat loss fraction.  This quantity

is  the  instantaneous faction of the heat release  rate  of  the

fire  which is lost to the bounding surfaces of the room and  its

contents.  Cooper  has  provided guidelines  for  selecting  this

parameter which is called Lambda C or ALMAC in ASET [1,3]. He has

determined  that  the approximate range is 0.6 - 0.9.  The  lower

value  corresponds to high aspect ratio spaces (ratio of  ceiling

span  to room height) with smooth ceilings and  fires  positioned

far  away  from  the  walls.  The  intermediate  to  high  values

16

correspond  to  low  aspect ratio spaces,  rooms  with  irregular

surfaces  or rooms in which the fire is within one ceiling height

of the wall.  The temperature of the upper layer is a function of

the heat loss fraction and the heat release rate of the fire. The

greater  the heat loss fraction the lower the temperature in  the

upper  layer.  The heat loss fraction for a room  with  insulated

walls  will  be  lower than the fraction for the same  room  with

uninsulated walls.

Both  ASET  and ASET-B treat the heat loss  parameter  as  a

constant.  That  is,  the  heat lost from the room is a  constant

fraction  of  the  heat release rate of the  fire.  As  the  heat

release  rate of the fire changes the quantity of heat lost  will

also change but in direct proportion to the fire.  Therefore  the

room  will not cool down even though the heat release rate of the

fire goes to zero.

5.2.3  Height of the Base of the Fire

The  third input is the height of the base of the fire above

the floor in feet.  For fuel items of relatively uniform  surface

height,  such as beds,  this is simply the height of the surface.

For  three  dimensional fuel items,  such as  sofas,  an  average

height weighted to reflect the distribution of surfaces should be

used. The rate of growth of the upper layer is strongly dependent

on  the difference between the height of the base of the fire and

the height of the smoke layer interface.

17

5.2.4  Room Ceiling Height and Floor Area

The  fourth and fifth inputs are the room ceiling height  in

feet and the floor area in square feet.  According to  references

[1,3]  the  calculations  may not be valid when applied  to  room

length-to-width aspect ratios greater than 10:1,  or with a ratio

of  height  to minimum horizontal dimension  exceeding  one.  The

equations  are  based on the assumption that the upper  layer  is

well  mixed and at a uniform temperature.  Therefore the  results

for a square room and a rectangular room of equal height and area

will be the same.

5.2.5  Maximum Time

The  sixth input is the maximum time for the  simulation  in

seconds.  The results of the calculations will be printed at five

second  intervals until the maximum time or until the end of  the

heat release data.

5.2.6  Heat Release Rate

The  final input is the description of heat release rate  of

the fire.  As described earlier the program can accommodate up to

100  pairs  of times and corresponding heat  release  rates.  The

program  performs  a linear interpolation between  the  specified

points  to determine the heat release rates at the required times

18

during the calculations.  The data is entered by typing the  time

in  seconds,  followed by a comma,  followed by the heat  release

rate in kilowatts.  A return or enter is then typed to proceed to

the  next  line.  Heat  release rates entered as  less  than  0.1

kilowatts  will  be  converted to that value.  The  program  will

automatically assume a starting value 0.1 kilowatts at time zero.

A  heat  release rate at time zero does not have  to  be  entered

unless a greater initial heat release rate is required.  When all

of  the desired times and heat release rates have been entered  a

-9,-9 followed by a return is entered to terminate the data entry

and begin the calculations.  Actually any negative time  followed

by a heat release rate will result in the same action.

Heat  release data for some furniture items can be found  in

[5].  These data can be entered directly by selecting a number of

the  points  which  represent  the general shape  of  the  curve.

Equations  for  the  growth  rate  of  a  number  of   industrial

commodities  can  be  found in NFPA 72E  and  204M  [6,7].  These

equations  can  be  solved  to yield the  heat  release  rate  at

selected  times,  which can then be entered into the program.  In

addition,   correlations  of  pool  and  crib  fires  have   been

summarized in appendix B of reference [8].

In many cases there is insufficient knowledge of the fuel or

no  data on which to determine a heat release rate for the  fuel.

One  possibility  in  this  case is to use the  so  called  semi-

universal fire developed by Cooper [1,3].  Most fires, other than

19

rapid growth fires such as flammable liquids,   have heat release

rates less than the semi-universal fire. The semi-universal  fire

is  based  on the same Factory Mutual data used in NFPA 204M  and

72E .  Initially it simulates a fire  on a polyurethane mattress,

at   148  seconds  it  begins  to  simulate  burning   wood   and

polyurethane  pallets,  and  at  349 seconds   a  fire  spreading

through commodities in paper cartons and stacked on pallets.  The

mathematical  description of the semi-universal fire is  provided

in  appendix D.  The semi-universal fire will  generally  provide

conservative  results  when used in ASET-B to predict the  height

and temperature of the upper layer. If the semi-universal fire is

used to predict time to detection,  it may predict detection  too

quickly.

ASET-B  cannot  change  the burning rate of the  fire  as  a

function  of the conditions in the room.  ASET-B cannot determine

if  there  is sufficient oxygen present for the fire to  burn  as

prescribed and it cannot increase the burning rate as a result of

thermal radiation to the fuel.  The burning rate data  referenced

above  is  based  on free burn conditions,  that is with  a  free

supply  of  ambient  air  and no  thermal  enhancement  from  the

surroundings. The use of free burn data should prove satisfactory

at  least  up  to  the  time when  ASET-B  predicts  upper  layer

temperatures of approximately 350-450 C.  Beyond that time ASET-B

will  continue to calculate layer heights and temperatures  based

on  the  input  fire even though the results  may  be  physically

impossible.

20

5.3  Program Outputs

The  output of the ASET-B program is a summary of the  input

data  and a table of the conditions in the room as a function  of

time.  The  first  column in the table is the simulation time  in

seconds.  The second and third columns are the temperature in the

upper  layer in degrees Fahrenheit and Celsius.  The  fourth  and

fifth  columns  are the height above the floor of  the  interface

between the upper and lower layers. The sixth and seventh columns

are  the  heat release rate of the fire in kilowatts and BTU  per

second.  Because  of  the  formatting limitations  in  the  BASIC

language,  some columns may show more significant digits than are

meaningful.

6.  USE AND LIMITATIONS OF THE ASET-B RESULTS

6.1  Evaluating Fire Safety Objectives

Fire  simulation computer programs such as ASET-B  generally

provide a description of the environment within an enclosure  and

not  a  direct evaluation of the fire safety.  While  a  complete

discussion of the use of these programs in evaluating fire safety

is beyond the scope of this paper a few examples will be given.

A common objective in fire safety design is to determine the

time  available  for safe egress.  In fact,  ASET was  originally

written  with  this objective in mind [9].  Although  the  design

objective may be stated in different ways,  one such statement is

21

as follows.  Given a particular room and fire,  how long does  it

take  to reach untenable conditions within the room?  To evaluate

this objective,  the limits of tenability must be established  in

terms of the program results.  For example,  the room will become

untenable  when the smoke layer reaches head height,  or when the

temperature in the layer reaches a particular value.  Using these

tenability limits and the program results,  the time to untenable

conditions can be evaluated.

A second common fire safety design objective is to determine

if  equipment  or  products  will  sustain  damage  in  the  fire

environment.  Equipment  damage thresholds can be established  in

the same manner as human tenability limits. The damage thresholds

can be compared to the predictions to determine if equipment will

be damaged and the time to the onset of damage.  The results  can

then   be  evaluated  based  on  estimates  of  detection   time,

suppression effectiveness and salvage capability.

In  addition to determining the time to untenable conditions

or damage,  ASET-B can be used to evaluate the impact of changing

one or more of the input variables.  For example, the sensitivity

of the resultant fire environment to room size can be examined by

making  multiple runs with different room sizes while holding the

other input values constant.

22

6.2  Using ASET-B For Multiple Rooms

Although  the ASET-B program is based on a single room  with

closed  doors and windows,  it is possible to use the program  to

make  approximations for rooms with open doors or windows or even

multiple rooms. The results of the closed room ASET-B program are

generally  valid for rooms with open doors or windows  until  the

interface drops to the top of the door or window. For the case of

a door opening into another closed room, a second run can be made

using  the  area of the two rooms combined.  The first run  (with

floor  area of single room) is used to predict  conditions  until

the interface drops to the top of the door.  The second run (with

floor  area  of combined rooms) is used from the time  the  newly

computed  interface drops to the top of the door until the end of

the simulation. Although there will be a time gap between the two

runs,  this  technique will provide satisfactory results in  many

cases,  especially  where door openings are relatively large  and

where fire heat release rates are relatively small.

6.3  Program Limitations

The  use  of ASET-B or any design aid  requires  the  design

engineer  to make the final evaluation as to the  appropriateness

of   the   design.   ASET-B  is  based  on  certain   engineering

approximations  of  the fire environment and should  be  used  to

supplement  rather than replace sound engineering judgement.  The

program results should be treated as approximate and the user  is

encouraged  to  become  familiar with how changes  in  the  input

23

variables  effect  the program results.  The temperature  of  the

upper  layer and the height of the interface respond  differently

to  changes  in  the input data.  Appropriate factors  of  safety

should  be  applied  to  either the input  data  or  the  program

results.

Some  of the limitations of the program have been  presented

in  conjunction  with  the input  data  requirements.  There  are

however,  some additional limitations. The mathematical procedure

used  in  ASET-B  is very hardy,  that  is,  the  procedure  will

normally converge and produce results.  There are combinations of

input data for which the program will either fail to converge  or

halt  due to an illegal mathematical operation.  If the procedure

for  solving the equations fails to converge,  a warning will  be

printed  and the solution will continue.  The  results  following

this  message may be in error and should be treated as such.  The

failure  to converge is usually a result of a heat release  value

which  changes  too rapidly.  In most cases this problem  can  be

corrected by minor smoothing of the input heat release curve.

There  are combinations of input data which will  result  in

the  program attempting to execute mathematical operations  which

are  invalid  in  the BASIC language.  These  operations  include

dividing  by  zero  and raising numbers to very  small  or  large

powers.  Operations of this type will be flagged by the  computer

and  subsequent  results should be considered in  error.  Invalid

operations  are usually caused by errors in  input  data.  ASET-B

24

does not check the input data for possible errors which can cause

illegal machine operations or produce unrealistic results such as

negative temperatures or interface heights above the ceiling.  As

indicated  previously  ASET-B may predict  physically  impossible

temperatures if very large fires are placed in small rooms.

6.4  Program Verification

Results  of the ASET program have been compared to data from

a  limited  number  of  actual  fire  experiments  [1,3].   These

comparisons  can  be  extended to the  ASET-B  program  since  it

produces results which are within a few percent of those produced

by  ASET.  The fire experiments considered a mockup of a hospital

room-corridor  building  space.  Comparisons  were  found  to  be

generally  favorable.  This  does not necessarily mean  that  the

comparison  will be favorable in all  cases.  Clearly  additional

studies are required in this area and that work is ongoing.

7.  TRANSPORTING THE PROGRAM

An  important  aspect  of  using  any  computer  program  is

obtaining  a copy of the program for the computer where it is  to

be used.  The program must not only run,  but it must produce the

correct  results.  Although  a  listing  of ASET-B  is  given  in

appendix A, it is not recommended the user attempt to type in the

program.  A  typographical error is generally very  difficult  to

track  down  and may result in a program error that  occurs  only

with certain combinations of input data.  Instead the user should

25

obtain  the program in machine readable form.  Since ASET-B is in

the public domain it may be freely copied.

A  sample run of the ASET-B program is shown in appendix  C.

Although the program cannot be thoroughly tested by comparing the

output  of  a  single  run,  this example has  been  selected  to

exercise most of the computer program. Results from a copy of the

program  which  do not compare exactly with  this  sample  output

probably indicate the program is in error.

The output of the ASET-B program will not agree exactly with

the output of the ASET program.  This results from the difference

in  the  mathematical procedures used.  Also,  the  ASET  program

listed  in  [2]  contains an error which  causes  the  calculated

temperatures to be approximately one percent too high.

ASET-B  was written for Microsoft* interpreted and  complied

BASIC  and has run successfully on IBM** and compatible  personal

computers operating under MS-DOS*. ASET-B has not yet been tested

on  other  personal  computers,   but  it  should  run  with   no

difficulties.

______________________________

*  Microsoft  and MS are trademarks of Microsoft Corporation  and

do  not  represent  an endorsement by the National  Bureau  of

Standards

** IBM   is  a  trademark  of  International  Business   Machines

Corporation  and  does  not represent an  endorsement  by  the

National Bureau of Standards

26

8.  ACKNOWLEDGEMENTS

Appreciation is extended to Dr. Leonard Cooper and Mr. David

Stroup for their assistance in preparing this report.

9.  REFERENCES

[1]  Cooper,  L.Y.,  Estimating Safe Available Egress  Time  from

Fires.  Nat.  Bur.  Stand. (U.S.) NBSIR 80-2172;  1981  February.

72 p.

[2]  Cooper,  L.Y.;  Stroup,  D.W.  Calculating Safe Egress  Time

(ASET) - A Computer Program and User's Guide.  Nat.  Bur.  Stand.

(U.S.) NBSIR 82-2578;  1982 September.  137 p.  also to appear in

Fire Safety Jour.

[3]  Cooper,  L.Y.  A Mathematical Model for Estimating Available

Safe Egress Time in Fires.  Fire  Mater.  6(3/4):  135-144;  1982

September/December.

[4] Carhanan,  B.;  Luther,  H.A.; Wilkes, J.O. Applied Numerical

Methods. New York: John Wiley & Sons; 1969. 604 p.

[5]  Lawson,   J.R.;   Walton,   W.D.;  and  Twilley,  W.H.  Fire

Performance  of  Furnishings  As Measured in  the  NBS  Furniture

Calorimeter.  Part 1. Nat. Bur. Stand. (U.S.) NBSIR 83-2787; 1983

August. 133 p.

[6] Standard on Automatic Fire Detectors 72E.  Boston:  Nat. Fire

Prot. Assn.; 1984.

[7]  Guide for Smoke and Heat Venting  204M.  Boston:  Nat.  Fire

Prot. Assn.; 1982.

[8] Quintiere J.G.;  Baum H.R.; Lawson J.R. Fire Growth In Combat

Ships. Nat. Bur. Stand. (U.S.) NBSIR; To be published.

[9]  Cooper L.Y.  A Concept for Estimating Available Safe  Egress

Time in Fires. Fire Safety Jour. 5(2): 135-144; 1983.

27

Figure 1. Schematic of Fire Phenomena

(figure not included)

28

APPENDIX A:  ASET-B PROGRAM LISTING

10 PRINT"ASET-B  VERSION 1.0   WRITTEN BY W.D. WALTON  1985"

20 PRINT"CONTRIBUTION OF THE NATIONAL BUREAU OF STANDARDS (U.S.)."

30 PRINT"NOT SUBJECT TO COPYRIGHT."

40 DIM TQ(100),Q(100)

50 INPUT"ENTER RUN TITLE";TITLE$

60 LR=.35

70 INPUT"HEAT LOSS FRACTION";LC

80 INPUT"FIRE HEIGHT (ft)";F

90 INPUT"ROOM CEILING HEIGHT (ft)";H

100 INPUT"ROOM FLOOR AREA (sq ft)";A

110 FM=F*.3048

120 HM=H*.3048

130 AM=A*.0929

140 INPUT"MAXIMUM TIME (sec)";TL

150 Q0=.1

160 PRINT"INPUT FIRE TIMES AND HEAT RELEASE RATES (use -9,-9 to end input)"

170 FOR N=1 TO 100

180 INPUT"TIME (sec), HEAT RELEASE RATE (kW)";TQ(N),QI

190 IF TQ(N) < 0 GOTO 240

200 IF QI < Q0 THEN Q(N)=Q0

210 Q(N)=QI/Q0

220 NEXT N

230 PRINT"MAXIMUM OF 100 INPUT VALUES REACHED"

240 NQ=N-1

250 IF TQ(1)<.1 THEN TQ(1)=.1

260 PA=530.

270 DA=.0735

280 CP=.24

290 C1=(1.-LC)*Q0/(DA*CP*PA*A*1.054)

300 C2=.21/A*((1.-LR)*Q0*32./(DA*CP*PA*1.054))^(1./3.)

310 DQ0=(Q(1)-1.)/TQ(1)

320 Z0=H-F

330 Z1=Z0

340 DZ1=-C1-C2*Z0^(5./3.)

350 P1=1.+C1/C2*Z0^(-5./3.)

360 DP1=C1/C2*(2.*DQ0+5.*(C1+C2*Z0^(5./3.)))/(6.*Z0^(8./3.))

370 T1=0.

380 T2=0.

390 DT=1.

400 QT=1.

410 OI=5.

420 OT=0.

430 PRINT" "

440 PRINT"ASET-B  VERSION 1.0"

450 PRINT TITLE$

460 PRINT"HEAT LOSS FRACTION=";LC

470 PRINT"FIRE HEIGHT=";F;"ft   ";FM;"m"

480 PRINT"ROOM HEIGHT=";H;"ft   ";HM;"m"

490 PRINT"ROOM AREA=";A;"sq ft   ";AM;"sq m"

500 PRINT" "

510 PRINT"    TIME      TEMP      TEMP     LAYER     LAYER      FIRE      FIRE"

520 PRINT"     sec         F         C        ft         m        kW     BTU/s"

530 GOSUB 970

29

540 T1=T2

550 T2=T1+DT

560 IF T2>TL THEN PRINT"RUN COMPLETE":GOTO 870

570 IF T2>TQ(NQ) THEN PRINT"END OF INPUT FIRE":GOTO 870

580 GOSUB 880

590 Z2=Z1+DZ1*DT

600 P2=P1+DP1*DT

610 IER=0

620 IF Z2<=0. GOTO 670

630 K=C2*QT^(1./3.)*Z2^(5./3.)

640 DZ2=-C1*QT-K

650 DP2=P2*(C1*QT-(P2-1.)*K)/(Z0-Z2)

660 GOTO 720

670 DP2=(P2*C1*QT)/(Z0-Z2)

680 IF Z2<=-F GOTO 710

690 DZ2=-C1*QT

700 GOTO 720

710 DZ2=0.

720 Z2C=Z1+(DZ1+DZ2)/2.*DT

730 P2C=P1+(DP1+DP2)/2.*DT

740 IF Z2C<-F THEN Z2=-F:Z2C=-F

750 IF ABS(Z2C-Z2)<.001 AND ABS(P2C-P2)<.001 GOTO 810

760 IF IER>30 THEN PRINT"WARNING! SOLUTION DID NOT CONVERGE":GOTO 810

770 Z2=Z2C

780 P2=P2C

790 IER=IER+1

800 GOTO 620

810 Z1=Z2C

820 P1=P2C

830 DZ1=DZ2

840 DP1=DP2

850 GOSUB 970

860 GOTO 540

870 END

880 IF T2>TQ(1) GOTO 910

890 QT=Q(1)-((Q(1)-1.)/TQ(1))*(TQ(1)-T2)

900 RETURN

910 FOR N=1 TO NQ

920 IF T2>TQ(N) GOTO 950

930 QT=Q(N)-((Q(N)-Q(N-1))/(TQ(N)-TQ(N-1)))*(TQ(N)-T2)

940 RETURN

950 NEXT N

960 RETURN

970 IF T2<OT THEN RETURN

980 OT=OT+OI

990 QK=QT*Q0

1000 QB=QK*.9485

1010 PF=(P1*PA)-460.

1020 PC=(PF-32.)/1.8

1030 RRF=DP1*31800.

1040 RRC=RRF/1.8

1050 X=Z1+F

1060 XM=X*.3048

1070 PRINT USING"######.#  ";T2;PF;PC;X;XM;QK;QB

1080 RETURN

30

APPENDIX B:  VARIABLE NAMES USED IN ASET-B

Quantities without units are dimensionless

A       area of room (ft^2)

AM      area of room (m^2)

C1      dimensionless group 1

C2      dimensionless group 2

CP      specific heat of air (BTU/lb/F)

DA      density of air (lb/ft^3)

DP1     derivative of upper layer temperature with respect to

time at the present time step

DP2     derivative of upper layer temperature with respect to

time at the next time step

DQ0     derivative of the rate of heat release with respect to

time at the initial time

DT      time step

DZ1     derivative of height of upper layer above fire with

respect to time at present time step

DZ2     derivative of height of upper layer above fire with

respect to time at next time step

F       height of base of fire (ft)

FM      height of base of fire (m)

H       height of room (ft)

HM      height of room (m)

IER     counts number of predictions-corrections

K       intermediate value used in evaluating derivatives

LC      fraction of heat release lost to contents and surroundings

LR      fraction of heat release radiated from fire

N       counts number of input rates of heat release

NQ      number of input rates of heat release

OI      output time interval (s)

31

OT      time for next output (s)

P1      temperature of upper layer at present time step

P2      predicted temperature of upper layer at next time step

P2C     corrected temperature of upper layer at next time step

PA      ambient temperature (R)

PC      temperature of upper layer (C)

PF      temperature of upper layer (F)

Q       rate of heat release specified at time TQ

Q0      rate of heat release at initial time step (kW)

QB      rate of heat release at next time step (BTU/s)

QI      rate of heat release specified at time TQ (kW)

QK      rate of heat release at next time step (kW)

QT      rate of heat release at next time step

RRC     rate of rise of temperature in upper layer (C/min)

RRF     rate of rise of temperature in upper layer (F/min)

T1      present time step

T2      next time step

TITLE$  run title

TL      limit of simulation time (s)

TQ      time for specified rate of heat release Q (s)

X       height of interface above floor (ft)

XM      height of interface above floor (m)

Z0      height of interface above fire at initial time step

Z1      height of interface above fire at present time step

Z2      predicted height of interface above fire at next time step

Z2C     corrected height of interface above fire at next time step

32

Variable names used in report but not in program

CL      characteristic length (1 ft)

CT      characteristic time (1 s)

P       temperature of upper layer

Z       height of interface above the fire

__________________________________________

Note: The symbol 0 is the number zero and the symbol O is the

letter O

33

APPENDIX C:  SAMPLE RUN OF ASET-B PROGRAM

ASET-B  VERSION 1.0   WRITTEN BY W.D. WALTON  1985

CONTRIBUTION OF THE NATIONAL BUREAU OF STANDARDS (U.S.).

NOT SUBJECT TO COPYRIGHT.

ENTER RUN TITLE? SAMPLE RUN OF ASET-B

HEAT LOSS FRACTION? .8

FIRE HEIGHT (ft)? 1

ROOM CEILING HEIGHT (ft)? 9

ROOM FLOOR AREA (sq ft)? 225

MAXIMUM TIME (sec)? 180

INPUT FIRE TIMES AND HEAT RELEASE RATES (use -9,-9 to end input)

TIME (sec), HEAT RELEASE RATE (kW)? 20,40

TIME (sec), HEAT RELEASE RATE (kW)? 100,200

TIME (sec), HEAT RELEASE RATE (kW)? 180,500

TIME (sec), HEAT RELEASE RATE (kW)? -9,-9

ASET-B  VERSION 1.0

SAMPLE RUN OF ASET-B

HEAT LOSS FRACTION= .8

FIRE HEIGHT= 1 ft    .3048 m

ROOM HEIGHT= 9 ft    2.7432 m

ROOM AREA= 225 sq ft    20.9025 sq m

TIME      TEMP      TEMP     LAYER     LAYER      FIRE      FIRE

sec         F         C        ft         m        kW     BTU/s

0.0      70.3      21.3       9.0       2.7       0.1       0.1

5.0      74.2      23.4       8.7       2.7      10.1       9.6

10.0      76.7      24.9       8.3       2.5      20.0      19.0

15.0      79.3      26.3       7.8       2.4      30.0      28.5

20.0      81.8      27.7       7.3       2.2      40.0      37.9

25.0      84.6      29.2       6.9       2.1      50.0      47.4

30.0      87.5      30.8       6.5       2.0      60.0      56.9

35.0      90.6      32.6       6.0       1.8      70.0      66.4

40.0      93.9      34.4       5.7       1.7      80.0      75.9

45.0      97.5      36.4       5.3       1.6      90.0      85.4

50.0     101.4      38.6       5.0       1.5     100.0      94.9

55.0     105.6      40.9       4.7       1.4     110.0     104.3

60.0     110.0      43.3       4.4       1.3     120.0     113.8

65.0     114.7      46.0       4.1       1.2     130.0     123.3

70.0     119.8      48.8       3.9       1.2     140.0     132.8

75.0     125.2      51.8       3.6       1.1     150.0     142.3

80.0     130.9      55.0       3.4       1.0     160.0     151.8

85.0     137.0      58.3       3.2       1.0     170.0     161.2

90.0     143.5      61.9       3.0       0.9     180.0     170.7

95.0     150.4      65.8       2.8       0.9     190.0     180.2

100.0     157.6      69.8       2.6       0.8     200.0     189.7

105.0     165.5      74.2       2.5       0.8     218.8     207.5

110.0     174.2      79.0       2.3       0.7     237.5     225.3

115.0     183.7      84.3       2.1       0.7     256.3     243.1

120.0     194.0      90.0       2.0       0.6     275.0     260.8

125.0     205.1      96.2       1.8       0.6     293.8     278.6

130.0     217.2     102.9       1.7       0.5     312.5     296.4

135.0     230.1     110.1       1.5       0.5     331.3     314.2

34

140.0     243.9     117.7       1.3       0.4     350.0     332.0

145.0     258.7     125.9       1.2       0.4     368.8     349.8

150.0     274.3     134.6       1.0       0.3     387.5     367.5

155.0     290.7     143.7       0.8       0.2     406.3     385.3

160.0     307.9     153.3       0.6       0.2     425.0     403.1

165.0     325.9     163.3       0.4       0.1     443.8     420.9

170.0     344.6     173.7       0.2       0.1     462.5     438.7

175.0     364.2     184.5       0.0       0.0     481.3     456.5

180.0     384.7     195.9       0.0       0.0     500.0     474.3

RUN COMPLETE

_________________________________

Note: The input heat release rate was selected to exercise

various sections of the program and does not necessarily

represent an actual fire.

35

APPENDIX D:  HEAT RELEASE RATE FOR THE SEMI-UNIVERSAL FIRE.

The  expressions given below are used to determine the  heat

release  rate for the semi-universal fire at a given  time.   The

first  expression is used for times less than 147.6 seconds,  the

second for times between 147.6 and 349 seconds and the third  for

times greater than 349 seconds.  The first and second expressions

will  produce the same heat release rate at 147.6 seconds and the

second  and third expressions will produce the same heat  release

rate at 349 seconds.

Q=10 EXP[0.025(TIME)]         0<=TIME<=147.6

Q=400 EXP[0.01(TIME-147.6)]   147.6<=TIME<=349

Q=3000 EXP[0.005(TIME-349)]   349<=TIME

Q - Heat release rate in kW

TIME - Time in seconds

EXP - Indicates number raised to the power of e, the base for

natural logarithms.

36

####################################