## WithoutAirBarrier
Infiltration inputs for five buildings in eight climate zones for buildings without an air barrier
| Hospital | Medium Office | Primary School | Small Hotel | Stand Alone Retail
Airtightness @ 75 Pa (m3/h/m2) - 5 sided | 13.8
Idesign @ 4 Pa (m3/s/m2) - 5 sided | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896
|  | Hospital |  |  | Medium Office |  |  | Primary School |  |  | Small Hotel |  |  | Stand Alone Retail
|  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.024745 | 0.0075905 | #N/A | 0.029127 | 0.032099 | #N/A | 0.042591 | 0.037553 | #N/A | 0.06 | 0.032652 | #N/A | 0.042984 | 0.04007 | #N/A
| EP (correl) (h-1) | 0.020112 | 0.0068505 | 0.20415 | 0.039816 | 0.036391 | 0.30862 | 0.042468 | 0.030239 | 0.37173 | 0.063876 | 0.03111 | 0.50761 | 0.044491 | 0.036333 | 0.51781
| EP (original) (h-1) | 0.019159 | 0.0097327 | -0.32481 | 0.039796 | 0.016617 | 0.37482 | 0.048206 | 0.020006 | 0.36558 | 0.12623 | 0.064111 | -5.216 | 0.046415 | 0.029435 | -0.028836
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.060568 | 0.033242 | #N/A | 0.057479 | 0.035743 | #N/A | #N/A | #N/A | #N/A | 0.068175 | 0.043429 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.050066 | 0.042841 | -0.033523 | 0.044205 | 0.036273 | 0.347 | #N/A | #N/A | #N/A | 0.047226 | 0.04203 | 0.12428
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.11428 | 0.071509 | -4.7267 | 0.15029 | 0.083623 | -8.8216 | #N/A | #N/A | #N/A | 0.093619 | 0.069805 | -1.3844
Phoenix (CZ 2) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.02095 | 0.004291 | #N/A | 0.0086353 | 0.018446 | #N/A | 0.016181 | 0.024521 | #N/A | 0.05 | 0.023201 | #N/A | 0.020936 | 0.022418 | #N/A
| EP (correl) (h-1) | 0.016128 | 0.0032497 | -1.0417 | 0.012995 | 0.018783 | 0.13444 | 0.015522 | 0.018523 | 0.24986 | 0.0559 | 0.018994 | 0.52978 | 0.020664 | 0.01715 | 0.23216
| EP (original) (h-1) | 0.01281 | 0.0073262 | -4.9548 | 0.025484 | 0.013687 | -0.58404 | 0.03101 | 0.016369 | -0.12919 | 0.084367 | 0.048289 | -4.435 | 0.030093 | 0.025684 | -0.85177
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.053605 | 0.02503 | #N/A | 0.042413 | 0.022421 | #N/A | #N/A | #N/A | #N/A | 0.053948 | 0.026605 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.050257 | 0.031514 | -0.64699 | 0.039288 | 0.023592 | 0.10445 | #N/A | #N/A | #N/A | 0.043717 | 0.029344 | -0.51793
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.079837 | 0.051615 | -4.3923 | 0.10365 | 0.061178 | -12.3654 | #N/A | #N/A | #N/A | 0.065697 | 0.049316 | -2.6883
Memphis (CZ 3) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.025149 | 0.0094096 | #N/A | 0.028641 | 0.036712 | #N/A | 0.048421 | 0.04444 | #N/A | 0.07 | 0.045481 | #N/A | 0.045782 | 0.047455 | #N/A
| EP (correl) (h-1) | 0.021049 | 0.0085659 | 0.42195 | 0.039262 | 0.04129 | 0.46763 | 0.053858 | 0.041186 | 0.5757 | 0.08223 | 0.047554 | 0.70747 | 0.050558 | 0.043833 | 0.64286
| EP (original) (h-1) | 0.017429 | 0.0095638 | -0.39364 | 0.034791 | 0.016514 | 0.42501 | 0.042325 | 0.020012 | 0.45143 | 0.11426 | 0.062422 | -0.8891 | 0.039601 | 0.02437 | 0.12056
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.081472 | 0.043041 | #N/A | 0.077193 | 0.045291 | #N/A | #N/A | #N/A | #N/A | 0.092632 | 0.053667 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.079665 | 0.059076 | 0.19934 | 0.077901 | 0.055518 | 0.51839 | #N/A | #N/A | #N/A | 0.079002 | 0.063985 | 0.37414
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.10727 | 0.07032 | -1.3965 | 0.14003 | 0.082697 | -2.6323 | #N/A | #N/A | #N/A | 0.089986 | 0.071093 | -0.27151
Baltimore (CZ4) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.027029 | 0.011475 | #N/A | 0.036367 | 0.039486 | #N/A | 0.05454 | 0.043868 | #N/A | 0.09 | 0.050355 | #N/A | 0.059914 | 0.055222 | #N/A
| EP (correl) (h-1) | 0.023189 | 0.01089 | 0.61418 | 0.048669 | 0.046307 | 0.51768 | 0.062201 | 0.043108 | 0.56069 | 0.094867 | 0.054258 | 0.7809 | 0.0661 | 0.055802 | 0.75816
| EP (original) (h-1) | 0.018946 | 0.010286 | -0.0092564 | 0.037754 | 0.017468 | 0.47695 | 0.045635 | 0.020707 | 0.41165 | 0.12385 | 0.066915 | -0.52244 | 0.043757 | 0.028782 | 0.12584
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.099237 | 0.046857 | #N/A | 0.087978 | 0.045416 | #N/A | #N/A | #N/A | #N/A | 0.10919 | 0.055574 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.099218 | 0.06825 | 0.23994 | 0.092518 | 0.060369 | 0.48212 | #N/A | #N/A | #N/A | 0.09541 | 0.068487 | 0.38526
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.11663 | 0.076719 | -0.92013 | 0.15297 | 0.09125 | -3.0511 | #N/A | #N/A | #N/A | 0.09636 | 0.073085 | -0.271
Chicago (CZ 5) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.031098 | 0.013955 | #N/A | 0.052272 | 0.046039 | #N/A | 0.075486 | 0.05157 | #N/A | 0.1 | 0.052284 | #N/A | 0.077633 | 0.059093 | #N/A
| EP (correl) (h-1) | 0.027459 | 0.013086 | 0.58776 | 0.080903 | 0.053737 | 0.17722 | 0.082522 | 0.050774 | 0.54493 | 0.11391 | 0.056785 | 0.71319 | 0.085231 | 0.058695 | 0.65041
| EP (original) (h-1) | 0.022272 | 0.010721 | 0.035393 | 0.021096 | 0.009057 | -0.21031 | 0.053283 | 0.022676 | 0.23497 | 0.14535 | 0.069638 | -0.79626 | 0.050794 | 0.031864 | -0.11207
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.11804 | 0.04535 | #N/A | 0.10988 | 0.046984 | #N/A | #N/A | #N/A | #N/A | 0.12536 | 0.052632 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.11753 | 0.067547 | 0.1678 | 0.11238 | 0.064109 | 0.35299 | #N/A | #N/A | #N/A | 0.11019 | 0.070489 | 0.19424
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.066397 | 0.037907 | -1.2357 | 0.18037 | 0.091795 | -3.367 | #N/A | #N/A | #N/A | 0.11592 | 0.079712 | -0.84501
Helena (CZ 6) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.024924 | 0.0081081 | #N/A | 0.029713 | 0.030977 | #N/A | 0.045488 | 0.034436 | #N/A | 0.08 | 0.036945 | #N/A | 0.053737 | 0.041685 | #N/A
| EP (correl) (h-1) | 0.021108 | 0.0074265 | 0.2735 | 0.037005 | 0.036218 | 0.36994 | 0.050817 | 0.032879 | 0.40157 | 0.090372 | 0.039633 | 0.68197 | 0.057737 | 0.041667 | 0.57141
| EP (original) (h-1) | 0.015929 | 0.011623 | -1.9534 | 0.033347 | 0.022653 | 0.3861 | 0.040295 | 0.027735 | 0.25274 | 0.10398 | 0.075744 | -3.0622 | 0.039333 | 0.03362 | -0.18526
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.1009 | 0.030229 | #N/A | 0.081033 | 0.028076 | #N/A | #N/A | #N/A | #N/A | 0.10006 | 0.033052 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.09659 | 0.045181 | -0.41152 | 0.086167 | 0.037708 | 0.18378 | #N/A | #N/A | #N/A | 0.091863 | 0.044799 | -0.11269
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.092562 | 0.07222 | -5.2996 | 0.12321 | 0.090252 | -9.7435 | #N/A | #N/A | 2.8083 | 0.078891 | 0.068859 | -3.2765
Duluth (CZ 7) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.033677 | 0.015496 | #N/A | 0.057423 | 0.047031 | #N/A | 0.079944 | 0.050832 | #N/A | 0.12 | 0.054508 | #N/A | 0.088605 | 0.061712 | #N/A
| EP (correl) (h-1) | 0.030295 | 0.014972 | 0.73478 | 0.071799 | 0.056025 | 0.57169 | 0.089437 | 0.053935 | 0.5938 | 0.12855 | 0.062093 | 0.78018 | 0.097008 | 0.066389 | 0.76822
| EP (original) (h-1) | 0.023158 | 0.011009 | -0.0022171 | 0.044894 | 0.019924 | 0.37326 | 0.054193 | 0.024424 | 0.18609 | 0.14949 | 0.070645 | -0.46288 | 0.051387 | 0.031931 | -0.21833
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.13593 | 0.046867 | #N/A | 0.12052 | 0.045026 | #N/A | #N/A | #N/A | #N/A | 0.14518 | 0.057381 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.132 | 0.069453 | 0.25223 | 0.12564 | 0.063703 | 0.44844 | #N/A | #N/A | #N/A | 0.13437 | 0.074701 | 0.46426
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.14509 | 0.078401 | -1.276 | 0.19014 | 0.091748 | -3.733 | #N/A | #N/A | #N/A | 0.12335 | 0.082596 | -0.635
Fairbanks (CZ 8) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.034361 | 0.014361 | #N/A | 0.05172 | 0.040372 | #N/A | 0.067122 | 0.037932 | #N/A | 0.12 | 0.053676 | #N/A | 0.078628 | 0.048658 | #N/A
| EP (correl) (h-1) | 0.02967 | 0.012585 | 0.72892 | 0.059231 | 0.042117 | 0.72769 | 0.075871 | 0.044823 | 0.50362 | 0.13316 | 0.062181 | 0.83674 | 0.086815 | 0.054525 | 0.73335
| EP (original) (h-1) | 0.012333 | 0.0090487 | -2.9213 | 0.023496 | 0.016995 | -0.68105 | 0.027402 | 0.019895 | -1.2924 | 0.0789 | 0.057859 | -2.06 | 0.029098 | 0.031155 | -1.4225
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.14415 | 0.043448 | #N/A | 0.11599 | 0.036487 | #N/A | #N/A | #N/A | #N/A | 0.13924 | 0.041273 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.13377 | 0.062253 | 0.19139 | 0.12085 | 0.053833 | 0.39274 | #N/A | #N/A | #N/A | 0.13213 | 0.063228 | 0.22251
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.079615 | 0.06235 | -4.6564 | 0.10525 | 0.077402 | -3.5082 | #N/A | #N/A | #N/A | 0.067681 | 0.059214 | -4.5458

## WithAirBarrier
Infiltration inputs for five buildings in eight climate zones for buildings with an air barrier
| Hospital | Medium Office | Primary School | Small Hotel | Stand Alone Retail
Airtightness @ 75 Pa (m3/h/m2) - 6 sided | 5
Volume (m3) | 79802 | 19741.41 | 27484 | 11621.72 | 13984.18
Exterior surface area - 5-sided (m2) | 8936.73 | 3638.45 | 9383 | 2698.13 | 3471
Exterior surface area - 6-sided (m2) | 13107.26 | 5299.18 | 16254 | 3701.53 | 5764.99
Idesign @ 4 Pa (m3/s/m2) - 5 sided | 0.00030388 | 0.00030176 | 0.00035891 | 0.00028424 | 0.00034412
|  | Hospital |  |  | Medium Office |  |  | Primary School |  |  | Small Hotel |  |  | Stand Alone Retail
Miami (CZ 1) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.019927 | 0.0024704 | #N/A | 0.0054868 | 0.032099 | #N/A | 0.020012 | 0.037553 | #N/A | 0.03 | 0.032652 | #N/A | 0.019161 | 0.04007 | #N/A
| EP (correl) (h-1) | 0.015303 | 0.0021877 | -2.9372 | 0.0094833 | 0.036391 | 0.24555 | 0.0040367 | 0.030239 | -0.28374 | 0.030725 | 0.03111 | 0.51623 | 0.01955 | 0.036333 | 0.37328
| EP (original) (h-1) | 0.010233 | 0.0051985 | -16.7415 | 0.021108 | 0.016617 | -2.0488 | 0.030411 | 0.020006 | 0.12598 | 0.063073 | 0.064111 | -8.132 | 0.028073 | 0.029435 | -1.3923
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.033097 | 0.033242 | #N/A | 0.03609 | 0.035743 | #N/A | #N/A | #N/A | #N/A | 0.041432 | 0.043429 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.026689 | 0.042841 | -0.31668 | 0.035704 | 0.036273 | 0.32179 | #N/A | #N/A | #N/A | 0.028443 | 0.04203 | 0.027546
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.060637 | 0.071509 | -4.4184 | 0.094827 | 0.083623 | -8.9359 | #N/A | #N/A | #N/A | 0.056634 | 0.069805 | -1.4017
Phoenix (CZ 2) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.018501 | 0.0012255 | #N/A | 0.0011995 | 0.0055021 | #N/A | 0.0065595 | 0.013263 | #N/A | 0.03 | 0.010366 | #N/A | 0.014333 | 0.0076091 | #N/A
| EP (correl) (h-1) | 0.01384 | 0.00088299 | -14.3038 | 0.0027806 | 0.0047801 | -0.010345 | 0.0011463 | 0.0033735 | 0.022836 | 0.026954 | 0.0083882 | 0.45215 | 0.014119 | 0.0051233 | 0.076522
| EP (original) (h-1) | 0.0068426 | 0.0039132 | -98.2161 | 0.013517 | 0.0072595 | -5.7533 | 0.019563 | 0.010326 | -0.8398 | 0.04215 | 0.024121 | -5.9298 | 0.018201 | 0.015531 | -3.7284
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.029469 | 0.014937 | #N/A | 0.026646 | 0.014073 | #N/A | #N/A | #N/A | #N/A | 0.032859 | 0.016176 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.027681 | 0.017751 | -0.92296 | 0.05816 | 0.032791 | -8.2146 | #N/A | #N/A | #N/A | 0.027371 | 0.017488 | -0.464
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.042356 | 0.027375 | -3.6479 | 0.065399 | 0.038598 | -12.547 | #N/A | #N/A | #N/A | 0.039739 | 0.029827 | -2.7133
Memphis (CZ 3) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.01962 | 0.0023678 | #N/A | 0.0045851 | 0.011703 | #N/A | 0.022511 | 0.025977 | #N/A | 0.03 | 0.019774 | #N/A | 0.020793 | 0.018729 | #N/A
| EP (correl) (h-1) | 0.015323 | 0.0022502 | -2.7665 | 0.0087157 | 0.011755 | 0.31213 | 0.025079 | 0.023479 | 0.53651 | 0.037422 | 0.021062 | 0.68615 | 0.022527 | 0.016263 | 0.52322
| EP (original) (h-1) | 0.0093103 | 0.0051092 | -20.8241 | 0.018459 | 0.0087665 | -1.0689 | 0.026703 | 0.012626 | 0.44078 | 0.05714 | 0.031245 | -1.7483 | 0.023957 | 0.014747 | -0.10453
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.044085 | 0.02361 | #N/A | 0.048503 | 0.02846 | #N/A | #N/A | #N/A | #N/A | 0.056162 | 0.032471 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.04333 | 0.033237 | -0.15801 | 0.04937 | 0.035314 | 0.50452 | #N/A | #N/A | #N/A | 0.047195 | 0.039222 | 0.22149
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.056981 | 0.037389 | -1.4246 | 0.088401 | 0.052234 | -2.6906 | #N/A | #N/A | #N/A | 0.054474 | 0.043066 | -0.29822
Baltimore (CZ4) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.019834 | 0.0024458 | #N/A | 0.0062942 | 0.012997 | #N/A | 0.025306 | 0.025954 | #N/A | 0.04 | 0.02217 | #N/A | 0.025197 | 0.023123 | #N/A
| EP (correl) (h-1) | 0.015698 | 0.0023764 | -2.2807 | 0.011038 | 0.014275 | 0.42788 | 0.029092 | 0.024608 | 0.52515 | 0.042494 | 0.024329 | 0.76345 | 0.027575 | 0.022422 | 0.68419
| EP (original) (h-1) | 0.010122 | 0.005496 | -17.7168 | 0.020037 | 0.0092769 | -0.6171 | 0.028794 | 0.013068 | 0.44052 | 0.061965 | 0.033512 | -1.2512 | 0.02647 | 0.017418 | 0.099265
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.05345 | 0.025456 | #N/A | 0.055295 | 0.02854 | #N/A | #N/A | #N/A | #N/A | 0.066151 | 0.033638 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.054257 | 0.038677 | -0.1735 | 0.059049 | 0.038682 | 0.44516 | #N/A | #N/A | #N/A | 0.056704 | 0.042463 | 0.15857
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.062012 | 0.040858 | -1.0043 | 0.096607 | 0.057687 | -3.1259 | #N/A | #N/A | #N/A | 0.058344 | 0.04429 | -0.29684
Chicago (CZ 5) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.020762 | 0.0030527 | #N/A | 0.010665 | 0.017332 | #N/A | 0.036755 | 0.031357 | #N/A | 0.05 | 0.023747 | #N/A | 0.032036 | 0.02722 | #N/A
| EP (correl) (h-1) | 0.016806 | 0.0029121 | -1.1856 | 0.016954 | 0.019194 | 0.37824 | 0.040503 | 0.029791 | 0.50866 | 0.051069 | 0.02612 | 0.694 | 0.036395 | 0.027143 | 0.50516
| EP (original) (h-1) | 0.011899 | 0.005729 | -9.4855 | 0.023352 | 0.010014 | -0.055081 | 0.033619 | 0.01431 | 0.41682 | 0.072744 | 0.034884 | -1.5159 | 0.030723 | 0.019277 | -0.017007
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.063312 | 0.024635 | #N/A | 0.069057 | 0.029525 | #N/A | #N/A | #N/A | #N/A | 0.075885 | 0.03184 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.063344 | 0.039149 | -0.40691 | 0.071248 | 0.040823 | 0.328 | #N/A | #N/A | #N/A | 0.064335 | 0.044591 | -0.13873
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.07322 | 0.041735 | -1.687 | 0.11394 | 0.058038 | -3.4532 | #N/A | #N/A | #N/A | 0.070194 | 0.04831 | -0.87844
Helena (CZ 6) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.019247 | 0.0016582 | #N/A | 0.0051313 | 0.011335 | #N/A | 0.019244 | 0.020099 | #N/A | 0.04 | 0.016101 | #N/A | 0.021827 | 0.01673 | #N/A
| EP (correl) (h-1) | 0.015311 | 0.0014849 | -5.3935 | 0.0082414 | 0.012862 | 0.28591 | 0.021713 | 0.018077 | 0.36426 | 0.039216 | 0.017461 | 0.62742 | 0.02318 | 0.015703 | 0.44202
| EP (original) (h-1) | 0.0085104 | 0.0062105 | -53.1198 | 0.017699 | 0.012028 | -1.0065 | 0.025424 | 0.017501 | 0.16024 | 0.052031 | 0.037918 | -4.5241 | 0.023791 | 0.020339 | -0.67088
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.054301 | 0.017126 | #N/A | 0.050919 | 0.017654 | #N/A | #N/A | #N/A | #N/A | 0.060614 | 0.02002 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.053013 | 0.026413 | -1.0924 | 0.05472 | 0.024037 | 0.14494 | #N/A | #N/A | #N/A | 0.054253 | 0.028835 | -0.60029
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.049214 | 0.038428 | -4.9197 | 0.077806 | 0.057018 | -9.882 | #N/A | #N/A | #N/A | 0.047764 | 0.041713 | -3.3322
Duluth (CZ 7) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.021118 | 0.0032316 | #N/A | 0.011687 | 0.017708 | #N/A | 0.038107 | 0.030815 | #N/A | 0.05 | 0.025227 | #N/A | 0.036378 | 0.029158 | #N/A
| EP (correl) (h-1) | 0.017495 | 0.0032656 | -0.66898 | 0.018241 | 0.020667 | 0.47933 | 0.042802 | 0.031 | 0.56171 | 0.057391 | 0.029039 | 0.75931 | 0.0402 | 0.030548 | 0.74797
| EP (original) (h-1) | 0.012373 | 0.0058831 | -8.2204 | 0.023837 | 0.010588 | 0.062328 | 0.034195 | 0.015413 | 0.43133 | 0.075435 | 0.035689 | -1.0811 | 0.031088 | 0.01933 | 0.044835
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.072776 | 0.025545 | #N/A | 0.075746 | 0.028282 | #N/A | #N/A | #N/A | #N/A | 0.087839 | 0.034709 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.071912 | 0.040212 | -0.30014 | 0.07969 | 0.0405 | 0.42098 | #N/A | #N/A | #N/A | 0.0791 | 0.04695 | 0.17768
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.07724 | 0.041813 | -1.3647 | 0.12014 | 0.058024 | -3.8408 | #N/A | #N/A | #N/A | 0.074722 | 0.050078 | -0.66521
Fairbanks (CZ 8) |  | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2 | Avg | SD | R2
ON | CONTAM (h-1) | 0.020883 | 0.0022486 | #N/A | 0.0079309 | 0.010667 | #N/A | 0.030081 | 0.022279 | #N/A | 0.05 | 0.024261 | #N/A | 0.032218 | 0.020586 | #N/A
| EP (correl) (h-1) | 0.017196 | 0.0025104 | -2.0184 | 0.010613 | 0.0094431 | 0.53046 | 0.034716 | 0.024064 | 0.46907 | 0.058355 | 0.028223 | 0.82344 | 0.035575 | 0.022089 | 0.69573
| EP (original) (h-1) | 0.0065885 | 0.0048345 | -44.9198 | 0.01247 | 0.0090225 | -0.83095 | 0.017289 | 0.012552 | -0.55701 | 0.040226 | 0.029515 | -1.9609 | 0.017603 | 0.018857 | -1.3408
OFF | CONTAM (h-1) | #N/A | #N/A | #N/A | 0.077146 | 0.023811 | #N/A | 0.07289 | 0.022907 | #N/A | #N/A | #N/A | #N/A | 0.08423 | 0.024898 | #N/A
| EP (correl) (h-1) | #N/A | #N/A | #N/A | 0.07287 | 0.036722 | -0.47289 | 0.076655 | 0.034076 | 0.3674 | #N/A | #N/A | #N/A | 0.077885 | 0.039959 | -0.19795
| EP (original) (h-1) | #N/A | #N/A | #N/A | 0.04235 | 0.033204 | -4.5443 | 0.066477 | 0.048918 | -3.5465 | #N/A | #N/A | #N/A | 0.040989 | 0.035884 | -4.5987