## Label Definitions
Schematic Label Number | Column Labels | Description
(if measured) | Filename | Original name of the file that includes this data
1 | ID_Xitron_VAC | Indoor airhandler power supply voltage (VAC)
2 | ID_Xitron_Amps | Indoor airhandler power supply current demand (Amps)
3 | ID_Xitron_Watts | Indoor airhandler power demand (W)
4 | OD_Xitron_VAC | Outdoor heat pump power supply voltage (VAC)
5 | OD_Xitron_Amps | Outdoor heat pump electrical current demand (Amps)
6 | OD_Xitron_Watts | Outdoor heat pump power demand (W)
7 | 1500_ODLiqSV_TempF | Outdoor unit liquid refrigerant line service valve temperature (oF)
8 | 1510_ODVapSV_TempF | Outdoor unit vapor refrigerant line service valve temperature (oF)
9 | 1526_Coriolis_IDSide_TempF | Liquid refrigerant line surface temperature near coriolis mass flowmeter closest to the indoor unit (oF)
10 | 1527_Coriolis_ODSide_TempF | Liquid refrigerant line surface temperature near coriolis mass flowmeter closest to the outdoor unit (oF)
11 | 1529_ODAir#1_TempF | Outdoor air temperature measured on an air inlet face of the outdoor unit (oF)
12 | 1530_ODAir#2_TempF | Outdoor air temperature measured on an air inlet face of the outdoor unit (oF)
13 | 1600_IDVap_TempF | Vapor refrigerant line surface temperature near the indoor unit (oF)
14 | 1601_IDLiq_TempF | Liquid refrigerant line, before the TXV, surface temperature near the indoor unit (oF)
15 | 1602_ID2phase_Cool#1_TempF | Two-phase refrigerant distribution line surface temperature after the TXV (oF)
16 | 1603_ID2Phase_Cool#2_TempF | Two-phase refrigerant distribution line surface temperature after the TXV (oF)
17 | 1608_CompSuct_TempF | Refrigerant line surface temperature at the suction of the compressor (oF)
18 | 1609_ODAir#3_TempF | Outdoor air temperature measured on an air inlet face of the outdoor unit (oF)
19 | 1610_ODCoilAirExit#1_F | Air temperature on top of outdoor unit at fan exit (oF)
20 | 1611_ODAir#4_TempF | Outdoor air temperature measured on an air inlet face of the outdoor unit (oF)
21 | 1612_OD2PhaseHeat_F | Outdoor heat exchanger return bend surface temperature, two-phase in the heating mode (oF)
22 | 1614_ODCoilAirExit#2_F | Air temperature on top of outdoor unit at fan exit (oF)
23 | 1617_CompDisch_TempF | Compressor discharge line surface temperature at exit of compressor (oF)
24 | 1618_ID2Phase_Heat#2_F | Indoor unit heat exchanger return bend surface temperature, two-phase in heating mode (oF)
25 | 1622_OD2PhaseCool_F | Outdoor heat exchanger return bend surface temperature, two-phase in the cooling mode (oF)
26 | 1630_ID2Phase_Heat#1_F | Indoor unit heat exchanger return bend surface temperature, two-phase in heating mode (oF)
27 | 1701_ODVapSV_psia | Outdoor unit vapor refrigerant line service valve pressure (psia)
28 | 1703_VDC_KahnDewTempF | Indoor unit inlet air primary dewpoint temperature (oF)
29 | 1704_VDC_KahnDrybulbF | Indoor unit inlet air drybulb temperature measured at the dewpoint sensor (oF)
30 | 1705_VDC_EdgeTech_ODDewF | Outdoor air dewpoint temperature (oF)
31 | 1707_IDVap_psia | Vapor refrigerant line pressure near the indoor unit (psia)
32 | 1708_VDC_VaisalaHMT100_DEW(F) | Indoor unit inlet air secondary dewpoint temperature (oF)
33 | 1710_ODSuctPort_psia | Outdoor unit refrigerant pressure at the compressor suction service port (psia)
34 | 1711_ID-EXIT_Dewtemp_F | Indoor unit exit air dewpoint temperature (oF)
35 | 1712_RotoMass_Massflow_lb/min | Coriolis meter refrigerant mass flow rate (lbm min-1)
36 | 1713_RotoMass_Density_lbm/ft3 | Coriolis meter refrigerant density(lbm ft-3)
37 | 1722_HMT331_Output1_DewF | Outdoor air secondary dewpoint temperature (oF)
38 | 1731_HMT331_Output2_DryF | Outdoor air drybulb temperature at the secondary dewpoint sensor (oF)
39 | 2317_VDC_NozDP#1_0to2p5inH2O | Airflow chamber nozzle plate pressure drop sensor number one (inches of water gage, inH2O)
40 | 2318_VDC_Barometer_inHg | Barometric pressure (inches of Mercury, inHg)
41 | 2320_VDC_NozDP#2_0to1inH2O | Airflow chamber nozzle plate pressure drop sensor number two (inches of water gage, inH2O)
42 | 2321_VDC_MamacDP_0to1inH2O | Indoor unit external static pressure (inH2O)
43 | 2322_VDC_SetraDP_0to2.5inH2O | Nozzle chamber and airhandler connecting duct pressure drop (inH2O)
44 | Inlet TC Grid AVG Temp (F) | Indoor unit/airhandler inlet air, thermocouple grid average drybulb temperature (oF)
45 | Exit TC Grid AVG Temp (F) | Indoor airhandler exit air, thermocouple grid average drybulb temperature (oF)
46 | TC Grid DT Temp (F) | Indoor unit air drybulb temperature change (oF)
47 | AVG Nozzle Temp (F) | Nozzle chamber average air exit drybulb temperature (oF)
48 | AVG Noz DP (in H2O) | Nozzle plate air pressure drop average of two sensors (inH2O)
49 | Active Baro Pres (inHg) | Barometric pressure being used for air property calculations (inHg)
50 | Unit ESP (in H2O) | Indoor unit external static pressure (inH2O)
51 | OD Air AVG DB (F) | Outdoor unit air averaged drybulb temperature (oF)
52 | OD Air StDev (F) | Standard deviation of the outdoor unit air drybulb temperatures (oF)
53 | Dewtemp_DELTA(F) | Indoor unit air dewpoint temperature change (oF)
54 | CALC_Exit Dewtemp (F) | Indoor unit air exit dewpoint temperature with any zero offset included used for air property calculations (oF)
55 | Inlet Humidity Ratio (lbw/lbda) | Calculated indoor inlet air humidity ratio (lbs water vapor per lbs of dry air, lbw lbda-1)
56 | Exit Humidity Ratio (lbw/lbda) | Calculated indoor exit air humidity ratio (lbs water vapor per lbs of dry air, lbw lbda-1)
57 | Mixture Specific Vol. (ft3/lbmix) | Indoor unit moist air specific volume (cubic feet per lb of water vapor and dry air mixture, ft3 lbmix-1)
58 | Mixture Specific Heat (Btu/lbm-F) | Indoor unit moist air constant pressure specific heat (British thermal units per lb of water vapor and dry air mixture per degree Fahrenheit, Btu lbmix-1 oF-1)
59 | Mixture Density (lbm/ft3) | Indoor unit moist air density (lb of water vapor and dry air mixture per cubic foot, lbmix ft-3)
60 | Indoor Unit SCFM | Indoor unit calculated airflow rate at standard density of 0.075 lbm ft-3 (ft3 min-1)
61 | Indoor Unit CFM | Indoor unit calculated airflow rate at the current moist air density (ft3 min-1)
62 | Sensible Capacity (Btu/h) | Sensible cooling capacity (Btu h-1)
63 | Latent Capacity (Btu/h) | Latent cooling capacity (Btu h-1)
64 | TOTAL Capacity (Btu/h) | Sensible plus latent cooling capacity (Btu h-1)
65 | SHR | Ratio of sensible capacity to total capacity
66 | ODVapSV_Suph_F | Calculated outdoor unit vapor refrigerant line service valve superheat temperature (oF)
67 | ODVapSV_Tsat_F | Calculated outdoor unit vapor refrigerant line service valve saturated refrigerant temperature at current measured pressure (oF)
68 | 1702_ODLiqSV_psia | Outdoor unit liquid refrigerant line service valve pressure (psia)
69 | ODLiqSV_Tsat_F | Calculated outdoor unit liquid refrigerant line service valve saturated refrigerant temperature at current measured pressure (oF)
70 | ODLiqSV_Tsub_F | Calculated outdoor unit liquid refrigerant line service valve subcooled temperature (oF)
71 | CompSuct_Suph_F | Compressor suction refrigerant vapor superheat temperature (oF)
72 | CompSuct_Tsat_F | Compressor suction refrigerant saturation temperature at the measured suction service port pressure (oF)
73 | CompDisch_psia | Compressor discharge refrigerant pressure (psia)
74 | 1617_CompDisch_TempF | Compressor discharge refrigerant line surface temperature (oF)
75 | CompDisch_Suph_F | Compressor discharge refrigerant line superheat temperature (oF)
76 | CompDisch_Tsat_F | Compressor discharge refrigerant saturation temperature (oF)
77 | Refrig_Liq_Enthalpy_Btu/lbm | Calculated enthalpy of subcooled liquid refrigerant enterring the indoor unit before the TXV (Btu lbm-1)
78 | Refrig_Vap_Enthalpy_Btu/lbm | Calculated enthalpy of superheated vapor refrigerant exitting the indoor unit (Btu lbm-1)
79 | Refrig-Side Capacity_Btu/h | Calculated refrigerant-side cooling capacity (Btu h-1)
80 | 1724_IDLiq@TXV_psia | Liquid line refrigerant pressure before the TXV (psia)
81 | IDLiq@TXV_Tsat_F | Liquid line refrigerant saturation temperature at the measured pressure before the TXV (oF)
82 | IDLiq@TXV_Tsub_F | Liquid line refrigerant subcooled temperature before the TXV (oF)
83 | IDVap_Suph_F | Indoor vapor refrigerant superheat temperature near the indoor unit (oF)
84 | IDVap_Tsat_F | Vapor line refrigerant saturation temperature at the measured pressure near the indoor unit (oF)
85 | CoriolisLiq_ID#1_Tsub_F | Liquid refrigerant subcooled temperature at the liquid line pressure near the indoor unit (oF)
86 | CoriolisLiq_OD#2_Tsub_F | Liquid refrigerant subcooled temperature at the liquid line service valve pressure (oF)
87 | Blower_Heat_Btu/h | Calculated heat added to the indoor airstream by the indoor unit blower (Btu h-1)
88 | Adj_RefSide_Q_Btu/h | Refrigerant-side cooling capacity minus the blower heat to compare to air-side capacity (Btu h-1)
89 | COP | Instantaneous coefficient of performance is total cooling capacity divided by total input electrical power (dimensionless)
90 | SCFM/TON | Standard density air volume flow rate divided by the total cooling capacity (ft3 min-1 ton-1)
91 | NF(NO=0,Yes=1) | If this is fault-free or no-fault then value=1, else value=0
92 | EF | Indoor airflow fault level with 100 % equal to no-fault and 90 % equal to 10 % reduced airflow
93 | CF | Outdoor unit air flow face area percentage free of blockage, 100 % is no blockage, 70 % is 30 % blocked area
94 | LL | Liquid refrigerant line pressure drop fault calculated from the outdoor unit service valve and indoor unit liquid line at the TXV pressures, 100 % is normal pressure drop, 150 % is 50 % greater pressure drop
95 | UC/OC | Refrigerant undercharge or overcharge fault, 100 % is normal charge, 90 % is 10 % undercharge
96 | Long/Short (0/1) | Indicates long or short lineset length being used (0 is 50 ft total, and 1 is 25 ft)
97 | Rated_SEER | Indicated the AHRI rated Seasonal Energy Efficiency Ratio, SEER, of the system