## CSV
Template for NIST FaTIMA single zone aerosol exposure tool.
| FATE |  |  | SOURCES | (#) |  | DEPOSITED | (#) |  | FILTERED | (#) |  | Inputs | [14 empty] | Charts
| Qbal | 50 |  | Continuous | 4608.5 | 41.56% | Floor | 116.88 | 87.8% | Outdoor Air | 0 | 0%
|  | (#) |  | Burst | 6480.2 | 58.44% | Walls | 16.241 | 12.2% | Recirculation | 2459.9 | 29.26% | Zone Geometry
| Exfiltrated | 1093.9 | 9.865% | Outdoor | 0 | 0% | Ceiling | 0.0013642 | 0.001025% | Air Cleaner | 5947.3 | 70.74% |  | Zone Volume (m³) | Floor Area (m² ) | Wall Area (m²) | Ceiling Area (m²) | Other Surface Area (m²) | Surface Volume Ratio
| Filtered | 8407.2 | 75.82% |  | 11088.7 |  | Other | 0 | 0% | Envelope | 0 | 0% |  | 100 | 40 | 63.25 | 40 | 4 | 1.5
| On Surfaces | 133.13 | 1.201% |  |  |  |  | 133.1224 |  |  | 8407.2 |  | Infiltration
| Deactivated | 1378.3 | 12.43% | [10 empty] | Infiltration 1/h | Penetration Factor
| Airborne | 75.94 | 0.6849% | [10 empty] | 0.5 | 1
| TOTAL | 11088.47 | [10 empty] | Ventilation System
[14 empty] | Supply Airflow Rate (sm³/h) | Outdoor Air Intake Fraction | Return Airflow Rate (sm³/h) | Local Exhaust Airflow Rate (sm³/h)
[14 empty] | 360 | 0 | 360 | 0
System Filters
[14 empty] | Outdoor Air Filter | Recirculation Air Filter
[14 empty] | None | MERV 8
Calculated Airflows
[14 empty] | Total Outdoor Air Change Rate (1/h) | Outdoor Air Intake Rate (sm³/h) | Recirculation Airflow Rate (sm³/h)
[14 empty] | 0.5 | 0 | 360
Room Air Cleaner
[14 empty] | Maximum Airflow Rate (scfm) | Fan Flow Fraction | Filter Efficiency | CADR (scfm)
[14 empty] | 200 | 1 | 0.8 | 160
Particle Properties
[14 empty] | Name | Diameter (µm) | Density (g/cm³) | Particle Deactivation | Half-life (h) | Decay Rate (1/h)
[14 empty] | IV1 | 1 | 1 | On | 1.1 | 0.63014
Continuous Source
[14 empty] | Source | Generation Rate (#/min) | Generation Time Period (Start) | Generation Time Period (End)
[14 empty] | On | 3.2 | 0:00 | 24:00
Burst Source
[14 empty] | Source | Burst Type | Amount per Burst (#) | Generation Time Period (Start) | Generation Time Period (End) | Burst Interval (min)
[14 empty] | On | Intermittent | 45 | 0:01 | 24:00 | 10
Particle Deposition Velocities
[14 empty] | Floor (cm/s) | Wall (cm/s) | Ceiling (cm/s) | Other Surface (cm/s) | Effective Deposition Rate (1/h)
[14 empty] | 0.00371 | 0.000326 | 4.33e-08 | 0 | 0.060848
Initial Concentrations
[14 empty] | Outdoor Air (#/m³) | Zone Air (#/m³)
[14 empty] | 0 | 0
Occupant Exposure
[14 empty] | Occupancy Time Period (Start) | Occupancy Time Period (End) | Occupancy Type | Intermittent Occupancy Interval (min) | Intermittent Occupancy Duration (min)
[14 empty] | 7:00 | 17:00 | Intermittent | 60 | 10
Results
Sources
[14 empty] | Continuous (#) | Burst (#) | Outdoor (#) | Total (#)
[14 empty] | 4608.5 | 6480.2 | 0 | 11089
Airborne Concentration
[14 empty] | Average (10 h) (#/m³) | Average (24 h) (#/m³) | Maximum (24 h) (#/m³)
[14 empty] | 0.91784 | 0.91146 | 1.1629
Airborne Exposure
[14 empty] | Average (10 h) (#/m³) | Maximum (10 h) (#/m³) | Integrated Exposure (# s/m³)
[14 empty] | 0.15298 | 1.1549 | 5507.4
Surface Loading
[14 empty] | Floor (#/m²) | Wall (#/m²) | Ceiling (#/m²) | Other (#/m²) | Total (#/m²)
[14 empty] | 2.9221 | 0.25676 | 3.4104e-05 | 0 | 3.1789
Deposited
[14 empty] | Floor (#) | Walls (#) | Ceiling (#) | Other (#) | Total (#)
[14 empty] | 116.88 | 16.241 | 0.0013642 | 0 | 133.13
Filtered
[14 empty] | Outdoor Air (#) | Recirculation (#) | AirCleaner (#) | Envelope (#) | Total (#)
[14 empty] | 0 | 2459.9 | 5947.3 | 0 | 8407.2
Other
[14 empty] | Deactivated (#) | Exited Zone (#) | Remining in Zone (#)
[14 empty] | 1378.3 | 1093.9 | 75.94
[13 empty] | Airborne Concentration |  |  |  |  | Airborne Exposure |  |  |  | Surface Loading
[13 empty] | Time | Zone (#/m³) | Average (24 h) (#/m³) | Average (10 h) (#/m³) |  | Time | 'Occupant (#/m³) | Average (10 h) (#/m³) | 'Integrated Exposure (# s/m³) | Time | Total (#/m²) | Floor (#/m²) | Wall (#/m²) | Ceiling (#/m²) | Other (#/m²)
[13 empty] | 0:00 | 0 | 0.91146 | 0 |  | 0:00 | 0 | 0 | 0 | 0:00 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0:00 | 0.0078355 | 0.91146 | 0 |  | 0:00 | 0 | 0 | 0 | 0:00 | 4.7436e-06 | 4.3604e-06 | 3.8316e-07 | 5.0892e-11 | 0
[13 empty] | 0:00 | 0.01551 | 0.91146 | 0 |  | 0:00 | 0 | 0 | 0 | 0:00 | 1.4134e-05 | 1.2992e-05 | 1.1416e-06 | 1.5163e-10 | 0
[13 empty] | 0:01 | 0.023027 | 0.91146 | 0 |  | 0:01 | 0 | 0 | 0 | 0:01 | 2.8074e-05 | 2.5806e-05 | 2.2676e-06 | 3.0118e-10 | 0
[13 empty] | 0:01 | 0.030389 | 0.91146 | 0 |  | 0:01 | 0 | 0 | 0 | 0:01 | 4.6472e-05 | 4.2718e-05 | 3.7536e-06 | 4.9857e-10 | 0
[13 empty] | 0:01 | 0.47835 | 0.91146 | 0 |  | 0:01 | 0 | 0 | 0 | 0:01 | 0.00033607 | 0.00030892 | 2.7145e-05 | 3.6054e-09 | 0
[13 empty] | 0:02 | 0.47636 | 0.91146 | 0 |  | 0:02 | 0 | 0 | 0 | 0:02 | 0.00062445 | 0.00057401 | 5.0439e-05 | 6.6994e-09 | 0
[13 empty] | 0:02 | 0.47441 | 0.91146 | 0 |  | 0:02 | 0 | 0 | 0 | 0:02 | 0.00091168 | 0.00083803 | 7.3638e-05 | 9.7808e-09 | 0
[13 empty] | 0:02 | 0.4725 | 0.91146 | 0 |  | 0:02 | 0 | 0 | 0 | 0:02 | 0.0011977 | 0.001101 | 9.6744e-05 | 1.285e-08 | 0
[13 empty] | 0:02 | 0.47064 | 0.91146 | 0 |  | 0:02 | 0 | 0 | 0 | 0:02 | 0.0014826 | 0.0013629 | 0.00011976 | 1.5906e-08 | 0
[13 empty] | 0:02 | 0.4688 | 0.91146 | 0 |  | 0:02 | 0 | 0 | 0 | 0:02 | 0.0017665 | 0.0016238 | 0.00014268 | 1.8951e-08 | 0
[13 empty] | 0:03 | 0.46701 | 0.91146 | 0 |  | 0:03 | 0 | 0 | 0 | 0:03 | 0.0020492 | 0.0018837 | 0.00016552 | 2.1984e-08 | 0
[13 empty] | 0:03 | 0.46525 | 0.91146 | 0 |  | 0:03 | 0 | 0 | 0 | 0:03 | 0.0023308 | 0.0021425 | 0.00018827 | 2.5006e-08 | 0
[13 empty] | 0:03 | 0.46353 | 0.91146 | 0 |  | 0:03 | 0 | 0 | 0 | 0:03 | 0.0026115 | 0.0024005 | 0.00021094 | 2.8018e-08 | 0
[13 empty] | 0:04 | 0.46184 | 0.91146 | 0 |  | 0:04 | 0 | 0 | 0 | 0:04 | 0.0028911 | 0.0026576 | 0.00023352 | 3.1016e-08 | 0
[13 empty] | 0:04 | 0.46019 | 0.91146 | 0 |  | 0:04 | 0 | 0 | 0 | 0:04 | 0.0031697 | 0.0029137 | 0.00025602 | 3.4005e-08 | 0
[13 empty] | 0:04 | 0.45858 | 0.91146 | 0 |  | 0:04 | 0 | 0 | 0 | 0:04 | 0.0034473 | 0.0031688 | 0.00027844 | 3.6984e-08 | 0
[13 empty] | 0:04 | 0.45699 | 0.91146 | 0 |  | 0:04 | 0 | 0 | 0 | 0:04 | 0.0037241 | 0.0034232 | 0.0003008 | 3.9952e-08 | 0
[13 empty] | 0:04 | 0.45544 | 0.91146 | 0 |  | 0:04 | 0 | 0 | 0 | 0:04 | 0.0039998 | 0.0036767 | 0.00032307 | 4.2911e-08 | 0
[13 empty] | 0:05 | 0.45392 | 0.91146 | 0 |  | 0:05 | 0 | 0 | 0 | 0:05 | 0.0042745 | 0.0039292 | 0.00034526 | 4.5858e-08 | 0
[13 empty] | 0:05 | 0.45243 | 0.91146 | 0 |  | 0:05 | 0 | 0 | 0 | 0:05 | 0.0045485 | 0.0041811 | 0.00036738 | 4.8797e-08 | 0
[13 empty] | 0:05 | 0.45098 | 0.91146 | 0 |  | 0:05 | 0 | 0 | 0 | 0:05 | 0.0048215 | 0.004432 | 0.00038944 | 5.1727e-08 | 0
[13 empty] | 0:06 | 0.44955 | 0.91146 | 0 |  | 0:06 | 0 | 0 | 0 | 0:06 | 0.0050937 | 0.0046822 | 0.00041142 | 5.4647e-08 | 0
[13 empty] | 0:06 | 0.44815 | 0.91146 | 0 |  | 0:06 | 0 | 0 | 0 | 0:06 | 0.0053648 | 0.0049314 | 0.00043333 | 5.7557e-08 | 0
[13 empty] | 0:06 | 0.44678 | 0.91146 | 0 |  | 0:06 | 0 | 0 | 0 | 0:06 | 0.0056353 | 0.0051801 | 0.00045518 | 6.0459e-08 | 0
[13 empty] | 0:06 | 0.44544 | 0.91146 | 0 |  | 0:06 | 0 | 0 | 0 | 0:06 | 0.005905 | 0.005428 | 0.00047697 | 6.3352e-08 | 0
[13 empty] | 0:07 | 0.44412 | 0.91146 | 0 |  | 0:07 | 0 | 0 | 0 | 0:07 | 0.0061739 | 0.0056751 | 0.00049868 | 6.6236e-08 | 0
[13 empty] | 0:07 | 0.44284 | 0.91146 | 0 |  | 0:07 | 0 | 0 | 0 | 0:07 | 0.0064421 | 0.0059217 | 0.00052034 | 6.9112e-08 | 0
[13 empty] | 0:07 | 0.44158 | 0.91146 | 0 |  | 0:07 | 0 | 0 | 0 | 0:07 | 0.0067093 | 0.0061673 | 0.00054192 | 7.1981e-08 | 0
[13 empty] | 0:07 | 0.44034 | 0.91146 | 0 |  | 0:07 | 0 | 0 | 0 | 0:07 | 0.0069759 | 0.0064124 | 0.00056347 | 7.484e-08 | 0
[13 empty] | 0:08 | 0.43913 | 0.91146 | 0 |  | 0:08 | 0 | 0 | 0 | 0:08 | 0.0072418 | 0.0066568 | 0.00058493 | 7.7693e-08 | 0
[13 empty] | 0:08 | 0.43795 | 0.91146 | 0 |  | 0:08 | 0 | 0 | 0 | 0:08 | 0.007507 | 0.0069005 | 0.00060636 | 8.0537e-08 | 0
[13 empty] | 0:08 | 0.43679 | 0.91146 | 0 |  | 0:08 | 0 | 0 | 0 | 0:08 | 0.0077714 | 0.0071436 | 0.00062771 | 8.3373e-08 | 0
[13 empty] | 0:08 | 0.43565 | 0.91146 | 0 |  | 0:08 | 0 | 0 | 0 | 0:08 | 0.0080351 | 0.007386 | 0.00064901 | 8.6203e-08 | 0
[13 empty] | 0:08 | 0.43454 | 0.91146 | 0 |  | 0:08 | 0 | 0 | 0 | 0:08 | 0.0082981 | 0.0076278 | 0.00067027 | 8.9026e-08 | 0
[13 empty] | 0:09 | 0.43345 | 0.91146 | 0 |  | 0:09 | 0 | 0 | 0 | 0:09 | 0.0085606 | 0.007869 | 0.00069146 | 9.1841e-08 | 0
[13 empty] | 0:09 | 0.43238 | 0.91146 | 0 |  | 0:09 | 0 | 0 | 0 | 0:09 | 0.0088223 | 0.0081096 | 0.00071261 | 9.4649e-08 | 0
[13 empty] | 0:09 | 0.43133 | 0.91146 | 0 |  | 0:09 | 0 | 0 | 0 | 0:09 | 0.0090835 | 0.0083497 | 0.00073369 | 9.7451e-08 | 0
[13 empty] | 0:10 | 0.43031 | 0.91146 | 0 |  | 0:10 | 0 | 0 | 0 | 0:10 | 0.009344 | 0.0085892 | 0.00075474 | 1.0025e-07 | 0
[13 empty] | 0:10 | 0.42931 | 0.91146 | 0 |  | 0:10 | 0 | 0 | 0 | 0:10 | 0.009604 | 0.0088281 | 0.00077573 | 1.0303e-07 | 0
[13 empty] | 0:10 | 0.42832 | 0.91146 | 0 |  | 0:10 | 0 | 0 | 0 | 0:10 | 0.0098633 | 0.0090665 | 0.00079668 | 1.0582e-07 | 0
[13 empty] | 0:10 | 0.42736 | 0.91146 | 0 |  | 0:10 | 0 | 0 | 0 | 0:10 | 0.010122 | 0.0093043 | 0.00081757 | 1.0859e-07 | 0
[13 empty] | 0:10 | 0.42642 | 0.91146 | 0 |  | 0:10 | 0 | 0 | 0 | 0:10 | 0.01038 | 0.0095417 | 0.00083843 | 1.1136e-07 | 0
[13 empty] | 0:11 | 0.4255 | 0.91146 | 0 |  | 0:11 | 0 | 0 | 0 | 0:11 | 0.010638 | 0.0097783 | 0.00085923 | 1.1413e-07 | 0
[13 empty] | 0:11 | 0.42459 | 0.91146 | 0 |  | 0:11 | 0 | 0 | 0 | 0:11 | 0.010895 | 0.010015 | 0.00087999 | 1.1688e-07 | 0
[13 empty] | 0:11 | 0.86446 | 0.91146 | 0 |  | 0:11 | 0 | 0 | 0 | 0:11 | 0.011418 | 0.010496 | 0.00092227 | 1.225e-07 | 0
[13 empty] | 0:12 | 0.85454 | 0.91146 | 0 |  | 0:12 | 0 | 0 | 0 | 0:12 | 0.011935 | 0.010971 | 0.00096406 | 1.2805e-07 | 0
[13 empty] | 0:12 | 0.84482 | 0.91146 | 0 |  | 0:12 | 0 | 0 | 0 | 0:12 | 0.012447 | 0.011441 | 0.0010054 | 1.3354e-07 | 0
[13 empty] | 0:12 | 0.8353 | 0.91146 | 0 |  | 0:12 | 0 | 0 | 0 | 0:12 | 0.012953 | 0.011906 | 0.0010462 | 1.3896e-07 | 0
[13 empty] | 0:12 | 0.82598 | 0.91146 | 0 |  | 0:12 | 0 | 0 | 0 | 0:12 | 0.013453 | 0.012366 | 0.0010866 | 1.4432e-07 | 0
[13 empty] | 0:12 | 0.81685 | 0.91146 | 0 |  | 0:12 | 0 | 0 | 0 | 0:12 | 0.013947 | 0.012821 | 0.0011265 | 1.4963e-07 | 0
[13 empty] | 0:13 | 0.8079 | 0.91146 | 0 |  | 0:13 | 0 | 0 | 0 | 0:13 | 0.014436 | 0.01327 | 0.001166 | 1.5488e-07 | 0
[13 empty] | 0:13 | 0.79915 | 0.91146 | 0 |  | 0:13 | 0 | 0 | 0 | 0:13 | 0.01492 | 0.013715 | 0.0012051 | 1.6007e-07 | 0
[13 empty] | 0:13 | 0.79057 | 0.91146 | 0 |  | 0:13 | 0 | 0 | 0 | 0:13 | 0.015399 | 0.014155 | 0.0012438 | 1.652e-07 | 0
[13 empty] | 0:14 | 0.78216 | 0.91146 | 0 |  | 0:14 | 0 | 0 | 0 | 0:14 | 0.015872 | 0.01459 | 0.001282 | 1.7028e-07 | 0
[13 empty] | 0:14 | 0.77393 | 0.91146 | 0 |  | 0:14 | 0 | 0 | 0 | 0:14 | 0.016341 | 0.015021 | 0.0013199 | 1.7531e-07 | 0
[13 empty] | 0:14 | 0.76587 | 0.91146 | 0 |  | 0:14 | 0 | 0 | 0 | 0:14 | 0.016804 | 0.015447 | 0.0013573 | 1.8028e-07 | 0
[13 empty] | 0:14 | 0.75798 | 0.91146 | 0 |  | 0:14 | 0 | 0 | 0 | 0:14 | 0.017263 | 0.015869 | 0.0013944 | 1.8521e-07 | 0
[13 empty] | 0:15 | 0.75024 | 0.91146 | 0 |  | 0:15 | 0 | 0 | 0 | 0:15 | 0.017718 | 0.016286 | 0.0014311 | 1.9008e-07 | 0
[13 empty] | 0:15 | 0.74267 | 0.91146 | 0 |  | 0:15 | 0 | 0 | 0 | 0:15 | 0.018167 | 0.0167 | 0.0014674 | 1.949e-07 | 0
[13 empty] | 0:15 | 0.73525 | 0.91146 | 0 |  | 0:15 | 0 | 0 | 0 | 0:15 | 0.018612 | 0.017109 | 0.0015033 | 1.9968e-07 | 0
[13 empty] | 0:15 | 0.72798 | 0.91146 | 0 |  | 0:15 | 0 | 0 | 0 | 0:15 | 0.019053 | 0.017514 | 0.0015389 | 2.0441e-07 | 0
[13 empty] | 0:16 | 0.72086 | 0.91146 | 0 |  | 0:16 | 0 | 0 | 0 | 0:16 | 0.019489 | 0.017915 | 0.0015742 | 2.0909e-07 | 0
[13 empty] | 0:16 | 0.71389 | 0.91146 | 0 |  | 0:16 | 0 | 0 | 0 | 0:16 | 0.019922 | 0.018312 | 0.0016091 | 2.1373e-07 | 0
[13 empty] | 0:16 | 0.70706 | 0.91146 | 0 |  | 0:16 | 0 | 0 | 0 | 0:16 | 0.02035 | 0.018706 | 0.0016437 | 2.1832e-07 | 0
[13 empty] | 0:16 | 0.70037 | 0.91146 | 0 |  | 0:16 | 0 | 0 | 0 | 0:16 | 0.020774 | 0.019096 | 0.0016779 | 2.2286e-07 | 0
[13 empty] | 0:16 | 0.69383 | 0.91146 | 0 |  | 0:16 | 0 | 0 | 0 | 0:16 | 0.021195 | 0.019482 | 0.0017119 | 2.2737e-07 | 0
[13 empty] | 0:17 | 0.68741 | 0.91146 | 0 |  | 0:17 | 0 | 0 | 0 | 0:17 | 0.02161 | 0.019864 | 0.0017455 | 2.3184e-07 | 0
[13 empty] | 0:17 | 0.68112 | 0.91146 | 0 |  | 0:17 | 0 | 0 | 0 | 0:17 | 0.022022 | 0.020243 | 0.0017788 | 2.3627e-07 | 0
[13 empty] | 0:17 | 0.67497 | 0.91146 | 0 |  | 0:17 | 0 | 0 | 0 | 0:17 | 0.022431 | 0.020619 | 0.0018118 | 2.4064e-07 | 0
[13 empty] | 0:18 | 0.66894 | 0.91146 | 0 |  | 0:18 | 0 | 0 | 0 | 0:18 | 0.022836 | 0.020991 | 0.0018445 | 2.45e-07 | 0
[13 empty] | 0:18 | 0.66303 | 0.91146 | 0 |  | 0:18 | 0 | 0 | 0 | 0:18 | 0.023237 | 0.02136 | 0.0018769 | 2.4929e-07 | 0
[13 empty] | 0:18 | 0.65725 | 0.91146 | 0 |  | 0:18 | 0 | 0 | 0 | 0:18 | 0.023636 | 0.021727 | 0.0019091 | 2.5357e-07 | 0
[13 empty] | 0:18 | 0.65159 | 0.91146 | 0 |  | 0:18 | 0 | 0 | 0 | 0:18 | 0.024029 | 0.022088 | 0.001941 | 2.5779e-07 | 0
[13 empty] | 0:18 | 0.64604 | 0.91146 | 0 |  | 0:18 | 0 | 0 | 0 | 0:18 | 0.024421 | 0.022448 | 0.0019725 | 2.6199e-07 | 0
[13 empty] | 0:19 | 0.6406 | 0.91146 | 0 |  | 0:19 | 0 | 0 | 0 | 0:19 | 0.024808 | 0.022804 | 0.0020038 | 2.6616e-07 | 0
[13 empty] | 0:19 | 0.63528 | 0.91146 | 0 |  | 0:19 | 0 | 0 | 0 | 0:19 | 0.025192 | 0.023157 | 0.002035 | 2.7028e-07 | 0
[13 empty] | 0:19 | 0.63007 | 0.91146 | 0 |  | 0:19 | 0 | 0 | 0 | 0:19 | 0.025574 | 0.023508 | 0.0020657 | 2.7437e-07 | 0
[13 empty] | 0:20 | 0.62496 | 0.91146 | 0 |  | 0:20 | 0 | 0 | 0 | 0:20 | 0.025953 | 0.023856 | 0.0020963 | 2.7844e-07 | 0
[13 empty] | 0:20 | 0.61996 | 0.91146 | 0 |  | 0:20 | 0 | 0 | 0 | 0:20 | 0.026329 | 0.024202 | 0.0021266 | 2.8245e-07 | 0
[13 empty] | 0:20 | 0.61506 | 0.91146 | 0 |  | 0:20 | 0 | 0 | 0 | 0:20 | 0.026701 | 0.024544 | 0.0021566 | 2.8646e-07 | 0
[13 empty] | 0:20 | 0.61026 | 0.91146 | 0 |  | 0:20 | 0 | 0 | 0 | 0:20 | 0.02707 | 0.024884 | 0.0021866 | 2.9041e-07 | 0
[13 empty] | 0:20 | 0.60556 | 0.91146 | 0 |  | 0:20 | 0 | 0 | 0 | 0:20 | 0.027436 | 0.02522 | 0.0022162 | 2.9435e-07 | 0
[13 empty] | 0:21 | 0.60096 | 0.91146 | 0 |  | 0:21 | 0 | 0 | 0 | 0:21 | 0.0278 | 0.025554 | 0.0022454 | 2.9826e-07 | 0
[13 empty] | 0:21 | 0.59645 | 0.91146 | 0 |  | 0:21 | 0 | 0 | 0 | 0:21 | 0.028161 | 0.025886 | 0.0022746 | 3.0212e-07 | 0
[13 empty] | 0:21 | 1.0328 | 0.91146 | 0 |  | 0:21 | 0 | 0 | 0 | 0:21 | 0.028787 | 0.026461 | 0.0023253 | 3.0884e-07 | 0
[13 empty] | 0:22 | 1.0194 | 0.91146 | 0 |  | 0:22 | 0 | 0 | 0 | 0:22 | 0.029404 | 0.027028 | 0.0023751 | 3.1545e-07 | 0
[13 empty] | 0:22 | 1.0063 | 0.91146 | 0 |  | 0:22 | 0 | 0 | 0 | 0:22 | 0.030012 | 0.027588 | 0.0024242 | 3.2198e-07 | 0
[13 empty] | 0:22 | 0.99347 | 0.91146 | 0 |  | 0:22 | 0 | 0 | 0 | 0:22 | 0.030615 | 0.028142 | 0.0024729 | 3.2844e-07 | 0
[13 empty] | 0:22 | 0.9809 | 0.91146 | 0 |  | 0:22 | 0 | 0 | 0 | 0:22 | 0.031209 | 0.028688 | 0.0025208 | 3.3482e-07 | 0
[13 empty] | 0:22 | 0.96859 | 0.91146 | 0 |  | 0:22 | 0 | 0 | 0 | 0:22 | 0.031795 | 0.029227 | 0.0025682 | 3.411e-07 | 0
[13 empty] | 0:23 | 0.95653 | 0.91146 | 0 |  | 0:23 | 0 | 0 | 0 | 0:23 | 0.032375 | 0.029759 | 0.002615 | 3.4733e-07 | 0
[13 empty] | 0:23 | 0.94471 | 0.91146 | 0 |  | 0:23 | 0 | 0 | 0 | 0:23 | 0.032946 | 0.030285 | 0.0026612 | 3.5346e-07 | 0
[13 empty] | 0:23 | 0.93315 | 0.91146 | 0 |  | 0:23 | 0 | 0 | 0 | 0:23 | 0.033511 | 0.030804 | 0.0027067 | 3.5951e-07 | 0
[13 empty] | 0:24 | 0.92181 | 0.91146 | 0 |  | 0:24 | 0 | 0 | 0 | 0:24 | 0.034068 | 0.031316 | 0.0027519 | 3.6551e-07 | 0
[13 empty] | 0:24 | 0.91071 | 0.91146 | 0 |  | 0:24 | 0 | 0 | 0 | 0:24 | 0.034621 | 0.031824 | 0.0027964 | 3.7141e-07 | 0
[13 empty] | 0:24 | 0.89984 | 0.91146 | 0 |  | 0:24 | 0 | 0 | 0 | 0:24 | 0.035165 | 0.032324 | 0.0028403 | 3.7725e-07 | 0
[13 empty] | 0:24 | 0.88919 | 0.91146 | 0 |  | 0:24 | 0 | 0 | 0 | 0:24 | 0.035703 | 0.032819 | 0.0028839 | 3.8304e-07 | 0
[13 empty] | 0:24 | 0.87877 | 0.91146 | 0 |  | 0:24 | 0 | 0 | 0 | 0:24 | 0.036235 | 0.033308 | 0.0029269 | 3.8875e-07 | 0
[13 empty] | 0:25 | 0.86855 | 0.91146 | 0 |  | 0:25 | 0 | 0 | 0 | 0:25 | 0.036761 | 0.033791 | 0.0029693 | 3.9439e-07 | 0
[13 empty] | 0:25 | 0.85855 | 0.91146 | 0 |  | 0:25 | 0 | 0 | 0 | 0:25 | 0.03728 | 0.034269 | 0.0030113 | 3.9996e-07 | 0
[13 empty] | 0:25 | 0.84875 | 0.91146 | 0 |  | 0:25 | 0 | 0 | 0 | 0:25 | 0.037795 | 0.034742 | 0.0030527 | 4.0548e-07 | 0
[13 empty] | 0:26 | 0.83915 | 0.91146 | 0 |  | 0:26 | 0 | 0 | 0 | 0:26 | 0.038302 | 0.035208 | 0.0030938 | 4.1093e-07 | 0
[13 empty] | 0:26 | 0.82975 | 0.91146 | 0 |  | 0:26 | 0 | 0 | 0 | 0:26 | 0.038805 | 0.03567 | 0.0031345 | 4.1631e-07 | 0
[13 empty] | 0:26 | 0.82054 | 0.91146 | 0 |  | 0:26 | 0 | 0 | 0 | 0:26 | 0.039302 | 0.036127 | 0.0031746 | 4.2164e-07 | 0
[13 empty] | 0:26 | 0.81152 | 0.91146 | 0 |  | 0:26 | 0 | 0 | 0 | 0:26 | 0.039794 | 0.03658 | 0.0032141 | 4.2691e-07 | 0
[13 empty] | 0:26 | 0.80269 | 0.91146 | 0 |  | 0:26 | 0 | 0 | 0 | 0:26 | 0.040278 | 0.037025 | 0.0032534 | 4.3212e-07 | 0
[13 empty] | 0:27 | 0.79403 | 0.91146 | 0 |  | 0:27 | 0 | 0 | 0 | 0:27 | 0.04076 | 0.037468 | 0.0032922 | 4.3728e-07 | 0
[13 empty] | 0:27 | 0.78556 | 0.91146 | 0 |  | 0:27 | 0 | 0 | 0 | 0:27 | 0.041236 | 0.037905 | 0.0033306 | 4.4238e-07 | 0
[13 empty] | 0:27 | 0.77726 | 0.91146 | 0 |  | 0:27 | 0 | 0 | 0 | 0:27 | 0.041706 | 0.038337 | 0.0033686 | 4.4744e-07 | 0
[13 empty] | 0:27 | 0.76913 | 0.91146 | 0 |  | 0:27 | 0 | 0 | 0 | 0:27 | 0.042171 | 0.038764 | 0.0034062 | 4.5243e-07 | 0
[13 empty] | 0:28 | 0.76117 | 0.91146 | 0 |  | 0:28 | 0 | 0 | 0 | 0:28 | 0.042632 | 0.039188 | 0.0034435 | 4.5737e-07 | 0
[13 empty] | 0:28 | 0.75337 | 0.91146 | 0 |  | 0:28 | 0 | 0 | 0 | 0:28 | 0.043089 | 0.039609 | 0.0034803 | 4.6226e-07 | 0
[13 empty] | 0:28 | 0.74573 | 0.91146 | 0 |  | 0:28 | 0 | 0 | 0 | 0:28 | 0.04354 | 0.040023 | 0.0035168 | 4.6711e-07 | 0
[13 empty] | 0:28 | 0.73825 | 0.91146 | 0 |  | 0:28 | 0 | 0 | 0 | 0:28 | 0.043987 | 0.040434 | 0.0035529 | 4.7191e-07 | 0
[13 empty] | 0:29 | 0.73092 | 0.91146 | 0 |  | 0:29 | 0 | 0 | 0 | 0:29 | 0.04443 | 0.04084 | 0.0035886 | 4.7666e-07 | 0
[13 empty] | 0:29 | 0.72374 | 0.91146 | 0 |  | 0:29 | 0 | 0 | 0 | 0:29 | 0.044868 | 0.041243 | 0.0036241 | 4.8136e-07 | 0
[13 empty] | 0:29 | 0.71671 | 0.91146 | 0 |  | 0:29 | 0 | 0 | 0 | 0:29 | 0.045302 | 0.041643 | 0.0036591 | 4.86e-07 | 0
[13 empty] | 0:30 | 0.70982 | 0.91146 | 0 |  | 0:30 | 0 | 0 | 0 | 0:30 | 0.045732 | 0.042038 | 0.0036939 | 4.9062e-07 | 0
[13 empty] | 0:30 | 0.70308 | 0.91146 | 0 |  | 0:30 | 0 | 0 | 0 | 0:30 | 0.046156 | 0.042428 | 0.0037282 | 4.9519e-07 | 0
[13 empty] | 0:30 | 0.69647 | 0.91146 | 0 |  | 0:30 | 0 | 0 | 0 | 0:30 | 0.046578 | 0.042815 | 0.0037622 | 4.9971e-07 | 0
[13 empty] | 0:30 | 0.69 | 0.91146 | 0 |  | 0:30 | 0 | 0 | 0 | 0:30 | 0.046996 | 0.043199 | 0.003796 | 5.0418e-07 | 0
[13 empty] | 0:30 | 0.68366 | 0.91146 | 0 |  | 0:30 | 0 | 0 | 0 | 0:30 | 0.047411 | 0.043581 | 0.0038295 | 5.0863e-07 | 0
[13 empty] | 0:31 | 0.67746 | 0.91146 | 0 |  | 0:31 | 0 | 0 | 0 | 0:31 | 0.04782 | 0.043957 | 0.0038625 | 5.1303e-07 | 0
[13 empty] | 0:31 | 0.67138 | 0.91146 | 0 |  | 0:31 | 0 | 0 | 0 | 0:31 | 0.048228 | 0.044332 | 0.0038953 | 5.174e-07 | 0
[13 empty] | 0:31 | 1.1062 | 0.91146 | 0 |  | 0:31 | 0 | 0 | 0 | 0:31 | 0.048897 | 0.044947 | 0.0039494 | 5.2458e-07 | 0
[13 empty] | 0:32 | 1.0913 | 0.91146 | 0 |  | 0:32 | 0 | 0 | 0 | 0:32 | 0.049557 | 0.045554 | 0.0040029 | 5.3167e-07 | 0
[13 empty] | 0:32 | 1.0767 | 0.91146 | 0 |  | 0:32 | 0 | 0 | 0 | 0:32 | 0.05021 | 0.046154 | 0.0040554 | 5.3866e-07 | 0
[13 empty] | 0:32 | 1.0624 | 0.91146 | 0 |  | 0:32 | 0 | 0 | 0 | 0:32 | 0.050852 | 0.046744 | 0.0041075 | 5.4555e-07 | 0
[13 empty] | 0:32 | 1.0484 | 0.91146 | 0 |  | 0:32 | 0 | 0 | 0 | 0:32 | 0.051487 | 0.047328 | 0.0041587 | 5.5237e-07 | 0
[13 empty] | 0:32 | 1.0347 | 0.91146 | 0 |  | 0:32 | 0 | 0 | 0 | 0:32 | 0.052113 | 0.047903 | 0.0042093 | 5.5909e-07 | 0
[13 empty] | 0:33 | 1.0213 | 0.91146 | 0 |  | 0:33 | 0 | 0 | 0 | 0:33 | 0.052732 | 0.048472 | 0.0042592 | 5.6572e-07 | 0
[13 empty] | 0:33 | 1.0082 | 0.91146 | 0 |  | 0:33 | 0 | 0 | 0 | 0:33 | 0.053343 | 0.049034 | 0.0043086 | 5.7227e-07 | 0
[13 empty] | 0:33 | 0.9953 | 0.91146 | 0 |  | 0:33 | 0 | 0 | 0 | 0:33 | 0.053945 | 0.049588 | 0.0043572 | 5.7874e-07 | 0
[13 empty] | 0:34 | 0.9827 | 0.91146 | 0 |  | 0:34 | 0 | 0 | 0 | 0:34 | 0.05454 | 0.050134 | 0.0044053 | 5.8512e-07 | 0
[13 empty] | 0:34 | 0.97035 | 0.91146 | 0 |  | 0:34 | 0 | 0 | 0 | 0:34 | 0.055128 | 0.050674 | 0.0044526 | 5.9143e-07 | 0
[13 empty] | 0:34 | 0.95825 | 0.91146 | 0 |  | 0:34 | 0 | 0 | 0 | 0:34 | 0.055707 | 0.051207 | 0.0044996 | 5.9765e-07 | 0
[13 empty] | 0:34 | 0.9464 | 0.91146 | 0 |  | 0:34 | 0 | 0 | 0 | 0:34 | 0.056281 | 0.051734 | 0.0045458 | 6.0378e-07 | 0
[13 empty] | 0:34 | 0.9348 | 0.91146 | 0 |  | 0:34 | 0 | 0 | 0 | 0:34 | 0.056846 | 0.052254 | 0.0045915 | 6.0986e-07 | 0
[13 empty] | 0:35 | 0.92343 | 0.91146 | 0 |  | 0:35 | 0 | 0 | 0 | 0:35 | 0.057405 | 0.052768 | 0.0046368 | 6.1585e-07 | 0
[13 empty] | 0:35 | 0.9123 | 0.91146 | 0 |  | 0:35 | 0 | 0 | 0 | 0:35 | 0.057957 | 0.053276 | 0.0046813 | 6.2179e-07 | 0
[13 empty] | 0:35 | 0.9014 | 0.91146 | 0 |  | 0:35 | 0 | 0 | 0 | 0:35 | 0.058504 | 0.053778 | 0.0047254 | 6.2764e-07 | 0
[13 empty] | 0:36 | 0.89072 | 0.91146 | 0 |  | 0:36 | 0 | 0 | 0 | 0:36 | 0.059042 | 0.054272 | 0.0047689 | 6.3342e-07 | 0
[13 empty] | 0:36 | 0.88026 | 0.91146 | 0 |  | 0:36 | 0 | 0 | 0 | 0:36 | 0.059576 | 0.054763 | 0.0048121 | 6.3913e-07 | 0
[13 empty] | 0:36 | 0.87001 | 0.91146 | 0 |  | 0:36 | 0 | 0 | 0 | 0:36 | 0.060102 | 0.055246 | 0.0048545 | 6.4479e-07 | 0
[13 empty] | 0:36 | 0.85998 | 0.91146 | 0 |  | 0:36 | 0 | 0 | 0 | 0:36 | 0.060623 | 0.055726 | 0.0048967 | 6.5038e-07 | 0
[13 empty] | 0:36 | 0.85015 | 0.91146 | 0 |  | 0:36 | 0 | 0 | 0 | 0:36 | 0.061136 | 0.056198 | 0.0049381 | 6.559e-07 | 0
[13 empty] | 0:37 | 0.84052 | 0.91146 | 0 |  | 0:37 | 0 | 0 | 0 | 0:37 | 0.061646 | 0.056666 | 0.0049794 | 6.6137e-07 | 0
[13 empty] | 0:37 | 0.83109 | 0.91146 | 0 |  | 0:37 | 0 | 0 | 0 | 0:37 | 0.062148 | 0.057128 | 0.0050199 | 6.6675e-07 | 0
[13 empty] | 0:37 | 0.82185 | 0.91146 | 0 |  | 0:37 | 0 | 0 | 0 | 0:37 | 0.062647 | 0.057586 | 0.0050602 | 6.721e-07 | 0
[13 empty] | 0:38 | 0.81281 | 0.91146 | 0 |  | 0:38 | 0 | 0 | 0 | 0:38 | 0.063139 | 0.058039 | 0.0050999 | 6.7737e-07 | 0
[13 empty] | 0:38 | 0.80395 | 0.91146 | 0 |  | 0:38 | 0 | 0 | 0 | 0:38 | 0.063626 | 0.058486 | 0.0051392 | 6.826e-07 | 0
[13 empty] | 0:38 | 0.79527 | 0.91146 | 0 |  | 0:38 | 0 | 0 | 0 | 0:38 | 0.064107 | 0.058929 | 0.005178 | 6.8776e-07 | 0
[13 empty] | 0:38 | 0.78677 | 0.91146 | 0 |  | 0:38 | 0 | 0 | 0 | 0:38 | 0.064583 | 0.059366 | 0.0052166 | 6.9288e-07 | 0
[13 empty] | 0:38 | 0.77845 | 0.91146 | 0 |  | 0:38 | 0 | 0 | 0 | 0:38 | 0.065055 | 0.0598 | 0.0052546 | 6.9792e-07 | 0
[13 empty] | 0:39 | 0.77029 | 0.91146 | 0 |  | 0:39 | 0 | 0 | 0 | 0:39 | 0.06552 | 0.060227 | 0.0052922 | 7.0292e-07 | 0
[13 empty] | 0:39 | 0.76231 | 0.91146 | 0 |  | 0:39 | 0 | 0 | 0 | 0:39 | 0.065982 | 0.060651 | 0.0053295 | 7.0789e-07 | 0
[13 empty] | 0:39 | 0.75448 | 0.91146 | 0 |  | 0:39 | 0 | 0 | 0 | 0:39 | 0.066439 | 0.061072 | 0.0053665 | 7.1278e-07 | 0
[13 empty] | 0:40 | 0.74682 | 0.91146 | 0 |  | 0:40 | 0 | 0 | 0 | 0:40 | 0.066892 | 0.061488 | 0.005403 | 7.1763e-07 | 0
[13 empty] | 0:40 | 0.73932 | 0.91146 | 0 |  | 0:40 | 0 | 0 | 0 | 0:40 | 0.067338 | 0.061899 | 0.0054391 | 7.2244e-07 | 0
[13 empty] | 0:40 | 0.73197 | 0.91146 | 0 |  | 0:40 | 0 | 0 | 0 | 0:40 | 0.067783 | 0.062307 | 0.005475 | 7.272e-07 | 0
[13 empty] | 0:40 | 0.72476 | 0.91146 | 0 |  | 0:40 | 0 | 0 | 0 | 0:40 | 0.068221 | 0.06271 | 0.0055103 | 7.319e-07 | 0
[13 empty] | 0:40 | 0.71771 | 0.91146 | 0 |  | 0:40 | 0 | 0 | 0 | 0:40 | 0.068656 | 0.063109 | 0.0055455 | 7.3656e-07 | 0
[13 empty] | 0:41 | 0.71081 | 0.91146 | 0 |  | 0:41 | 0 | 0 | 0 | 0:41 | 0.069086 | 0.063505 | 0.0055802 | 7.4118e-07 | 0
[13 empty] | 0:41 | 0.70404 | 0.91146 | 0 |  | 0:41 | 0 | 0 | 0 | 0:41 | 0.069512 | 0.063896 | 0.0056146 | 7.4574e-07 | 0
[13 empty] | 0:41 | 1.1382 | 0.91146 | 0 |  | 0:41 | 0 | 0 | 0 | 0:41 | 0.070201 | 0.06453 | 0.0056704 | 7.5313e-07 | 0
[13 empty] | 0:42 | 1.1226 | 0.91146 | 0 |  | 0:42 | 0 | 0 | 0 | 0:42 | 0.070881 | 0.065155 | 0.0057252 | 7.6043e-07 | 0
[13 empty] | 0:42 | 1.1074 | 0.91146 | 0 |  | 0:42 | 0 | 0 | 0 | 0:42 | 0.071552 | 0.065772 | 0.0057794 | 7.6763e-07 | 0
[13 empty] | 0:42 | 1.0925 | 0.91146 | 0 |  | 0:42 | 0 | 0 | 0 | 0:42 | 0.072213 | 0.066379 | 0.0058327 | 7.7472e-07 | 0
[13 empty] | 0:42 | 1.0779 | 0.91146 | 0 |  | 0:42 | 0 | 0 | 0 | 0:42 | 0.072865 | 0.066979 | 0.0058854 | 7.8172e-07 | 0
[13 empty] | 0:43 | 1.0636 | 0.91146 | 0 |  | 0:43 | 0 | 0 | 0 | 0:43 | 0.073509 | 0.067571 | 0.0059376 | 7.8862e-07 | 0
[13 empty] | 0:43 | 1.0496 | 0.91146 | 0 |  | 0:43 | 0 | 0 | 0 | 0:43 | 0.074145 | 0.068155 | 0.0059887 | 7.9544e-07 | 0
[13 empty] | 0:43 | 1.0358 | 0.91146 | 0 |  | 0:43 | 0 | 0 | 0 | 0:43 | 0.074772 | 0.068732 | 0.0060395 | 8.0218e-07 | 0
[13 empty] | 0:43 | 1.0224 | 0.91146 | 0 |  | 0:43 | 0 | 0 | 0 | 0:43 | 0.075389 | 0.069299 | 0.0060894 | 8.0881e-07 | 0
[13 empty] | 0:44 | 1.0092 | 0.91146 | 0 |  | 0:44 | 0 | 0 | 0 | 0:44 | 0.076002 | 0.069863 | 0.0061389 | 8.1538e-07 | 0
[13 empty] | 0:44 | 0.99634 | 0.91146 | 0 |  | 0:44 | 0 | 0 | 0 | 0:44 | 0.076605 | 0.070417 | 0.0061876 | 8.2183e-07 | 0
[13 empty] | 0:44 | 0.98372 | 0.91146 | 0 |  | 0:44 | 0 | 0 | 0 | 0:44 | 0.077201 | 0.070965 | 0.0062357 | 8.2823e-07 | 0
[13 empty] | 0:44 | 0.97134 | 0.91146 | 0 |  | 0:44 | 0 | 0 | 0 | 0:44 | 0.077789 | 0.071505 | 0.0062831 | 8.3453e-07 | 0
[13 empty] | 0:44 | 0.95923 | 0.91146 | 0 |  | 0:44 | 0 | 0 | 0 | 0:44 | 0.078369 | 0.072038 | 0.00633 | 8.4076e-07 | 0
[13 empty] | 0:45 | 0.94736 | 0.91146 | 0 |  | 0:45 | 0 | 0 | 0 | 0:45 | 0.078942 | 0.072565 | 0.0063764 | 8.4693e-07 | 0
[13 empty] | 0:45 | 0.93574 | 0.91146 | 0 |  | 0:45 | 0 | 0 | 0 | 0:45 | 0.079509 | 0.073086 | 0.0064221 | 8.53e-07 | 0
[13 empty] | 0:45 | 0.92435 | 0.91146 | 0 |  | 0:45 | 0 | 0 | 0 | 0:45 | 0.080068 | 0.0736 | 0.0064674 | 8.59e-07 | 0
[13 empty] | 0:46 | 0.9132 | 0.91146 | 0 |  | 0:46 | 0 | 0 | 0 | 0:46 | 0.080621 | 0.074108 | 0.006512 | 8.6494e-07 | 0
[13 empty] | 0:46 | 0.90228 | 0.91146 | 0 |  | 0:46 | 0 | 0 | 0 | 0:46 | 0.081168 | 0.074611 | 0.0065562 | 8.708e-07 | 0
[13 empty] | 0:46 | 0.89158 | 0.91146 | 0 |  | 0:46 | 0 | 0 | 0 | 0:46 | 0.081708 | 0.075107 | 0.0065997 | 8.7659e-07 | 0
[13 empty] | 0:46 | 0.8811 | 0.91146 | 0 |  | 0:46 | 0 | 0 | 0 | 0:46 | 0.082242 | 0.075598 | 0.0066427 | 8.823e-07 | 0
[13 empty] | 0:47 | 0.87084 | 0.91146 | 0 |  | 0:47 | 0 | 0 | 0 | 0:47 | 0.082767 | 0.076081 | 0.0066853 | 8.8797e-07 | 0
[13 empty] | 0:47 | 0.86079 | 0.91146 | 0 |  | 0:47 | 0 | 0 | 0 | 0:47 | 0.083289 | 0.076561 | 0.0067275 | 8.9355e-07 | 0
[13 empty] | 0:47 | 0.85094 | 0.91146 | 0 |  | 0:47 | 0 | 0 | 0 | 0:47 | 0.083804 | 0.077034 | 0.0067691 | 8.9909e-07 | 0
[13 empty] | 0:47 | 0.8413 | 0.91146 | 0 |  | 0:47 | 0 | 0 | 0 | 0:47 | 0.084313 | 0.077502 | 0.0068102 | 9.0455e-07 | 0
[13 empty] | 0:48 | 0.83185 | 0.91146 | 0 |  | 0:48 | 0 | 0 | 0 | 0:48 | 0.084818 | 0.077966 | 0.0068509 | 9.0995e-07 | 0
[13 empty] | 0:48 | 0.8226 | 0.91146 | 0 |  | 0:48 | 0 | 0 | 0 | 0:48 | 0.085315 | 0.078423 | 0.0068912 | 9.153e-07 | 0
[13 empty] | 0:48 | 0.81354 | 0.91146 | 0 |  | 0:48 | 0 | 0 | 0 | 0:48 | 0.085807 | 0.078875 | 0.0069309 | 9.2057e-07 | 0
[13 empty] | 0:48 | 0.80467 | 0.91146 | 0 |  | 0:48 | 0 | 0 | 0 | 0:48 | 0.086295 | 0.079324 | 0.0069702 | 9.258e-07 | 0
[13 empty] | 0:48 | 0.79597 | 0.91146 | 0 |  | 0:48 | 0 | 0 | 0 | 0:48 | 0.086777 | 0.079767 | 0.0070092 | 9.3098e-07 | 0
[13 empty] | 0:49 | 0.78746 | 0.91146 | 0 |  | 0:49 | 0 | 0 | 0 | 0:49 | 0.087253 | 0.080205 | 0.0070476 | 9.3608e-07 | 0
[13 empty] | 0:49 | 0.77912 | 0.91146 | 0 |  | 0:49 | 0 | 0 | 0 | 0:49 | 0.087725 | 0.080638 | 0.0070858 | 9.4114e-07 | 0
[13 empty] | 0:49 | 0.77095 | 0.91146 | 0 |  | 0:49 | 0 | 0 | 0 | 0:49 | 0.088192 | 0.081068 | 0.0071234 | 9.4614e-07 | 0
[13 empty] | 0:49 | 0.76295 | 0.91146 | 0 |  | 0:49 | 0 | 0 | 0 | 0:49 | 0.088654 | 0.081492 | 0.0071608 | 9.5111e-07 | 0
[13 empty] | 0:50 | 0.75511 | 0.91146 | 0 |  | 0:50 | 0 | 0 | 0 | 0:50 | 0.089111 | 0.081912 | 0.0071977 | 9.5602e-07 | 0
[13 empty] | 0:50 | 0.74744 | 0.91146 | 0 |  | 0:50 | 0 | 0 | 0 | 0:50 | 0.089563 | 0.082328 | 0.0072342 | 9.6087e-07 | 0
[13 empty] | 0:50 | 0.73992 | 0.91146 | 0 |  | 0:50 | 0 | 0 | 0 | 0:50 | 0.090012 | 0.082741 | 0.0072705 | 9.6568e-07 | 0
[13 empty] | 0:50 | 0.73256 | 0.91146 | 0 |  | 0:50 | 0 | 0 | 0 | 0:50 | 0.090455 | 0.083148 | 0.0073062 | 9.7044e-07 | 0
[13 empty] | 0:51 | 0.72535 | 0.91146 | 0 |  | 0:51 | 0 | 0 | 0 | 0:51 | 0.090893 | 0.083551 | 0.0073417 | 9.7514e-07 | 0
[13 empty] | 0:51 | 0.71828 | 0.91146 | 0 |  | 0:51 | 0 | 0 | 0 | 0:51 | 0.091329 | 0.083952 | 0.0073768 | 9.7982e-07 | 0
[13 empty] | 0:51 | 1.1521 | 0.91146 | 0 |  | 0:51 | 0 | 0 | 0 | 0:51 | 0.092026 | 0.084591 | 0.0074332 | 9.8728e-07 | 0
[13 empty] | 0:52 | 1.1363 | 0.91146 | 0 |  | 0:52 | 0 | 0 | 0 | 0:52 | 0.092715 | 0.085226 | 0.0074887 | 9.9467e-07 | 0
[13 empty] | 0:52 | 1.1208 | 0.91146 | 0 |  | 0:52 | 0 | 0 | 0 | 0:52 | 0.093393 | 0.085848 | 0.0075436 | 1.002e-06 | 0
[13 empty] | 0:52 | 1.1056 | 0.91146 | 0 |  | 0:52 | 0 | 0 | 0 | 0:52 | 0.094062 | 0.086463 | 0.0075976 | 1.0091e-06 | 0
[13 empty] | 0:52 | 1.0907 | 0.91146 | 0 |  | 0:52 | 0 | 0 | 0 | 0:52 | 0.094722 | 0.08707 | 0.0076509 | 1.0162e-06 | 0
[13 empty] | 0:52 | 1.0762 | 0.91146 | 0 |  | 0:52 | 0 | 0 | 0 | 0:52 | 0.095375 | 0.08767 | 0.0077036 | 1.0232e-06 | 0
[13 empty] | 0:53 | 1.0619 | 0.91146 | 0 |  | 0:53 | 0 | 0 | 0 | 0:53 | 0.096017 | 0.08826 | 0.0077556 | 1.0301e-06 | 0
[13 empty] | 0:53 | 1.0479 | 0.91146 | 0 |  | 0:53 | 0 | 0 | 0 | 0:53 | 0.096651 | 0.088843 | 0.0078067 | 1.0369e-06 | 0
[13 empty] | 0:53 | 1.0342 | 0.91146 | 0 |  | 0:53 | 0 | 0 | 0 | 0:53 | 0.097278 | 0.08942 | 0.0078574 | 1.0436e-06 | 0
[13 empty] | 0:54 | 1.0208 | 0.91146 | 0 |  | 0:54 | 0 | 0 | 0 | 0:54 | 0.097895 | 0.089987 | 0.0079072 | 1.0503e-06 | 0
[13 empty] | 0:54 | 1.0077 | 0.91146 | 0 |  | 0:54 | 0 | 0 | 0 | 0:54 | 0.098506 | 0.090548 | 0.0079565 | 1.0568e-06 | 0
[13 empty] | 0:54 | 0.99482 | 0.91146 | 0 |  | 0:54 | 0 | 0 | 0 | 0:54 | 0.099108 | 0.091102 | 0.0080052 | 1.0633e-06 | 0
[13 empty] | 0:54 | 0.98222 | 0.91146 | 0 |  | 0:54 | 0 | 0 | 0 | 0:54 | 0.099703 | 0.091648 | 0.0080531 | 1.0696e-06 | 0
[13 empty] | 0:54 | 0.96988 | 0.91146 | 0 |  | 0:54 | 0 | 0 | 0 | 0:54 | 0.10029 | 0.092189 | 0.0081007 | 1.0759e-06 | 0
[13 empty] | 0:55 | 0.95779 | 0.91146 | 0 |  | 0:55 | 0 | 0 | 0 | 0:55 | 0.10087 | 0.092722 | 0.0081475 | 1.0822e-06 | 0
[13 empty] | 0:55 | 0.94595 | 0.91146 | 0 |  | 0:55 | 0 | 0 | 0 | 0:55 | 0.10144 | 0.093247 | 0.0081937 | 1.0883e-06 | 0
[13 empty] | 0:55 | 0.93436 | 0.91146 | 0 |  | 0:55 | 0 | 0 | 0 | 0:55 | 0.10201 | 0.093766 | 0.0082393 | 1.0944e-06 | 0
[13 empty] | 0:56 | 0.923 | 0.91146 | 0 |  | 0:56 | 0 | 0 | 0 | 0:56 | 0.10257 | 0.09428 | 0.0082846 | 1.1004e-06 | 0
[13 empty] | 0:56 | 0.91188 | 0.91146 | 0 |  | 0:56 | 0 | 0 | 0 | 0:56 | 0.10312 | 0.094788 | 0.0083291 | 1.1063e-06 | 0
[13 empty] | 0:56 | 0.90098 | 0.91146 | 0 |  | 0:56 | 0 | 0 | 0 | 0:56 | 0.10366 | 0.095291 | 0.0083732 | 1.1121e-06 | 0
[13 empty] | 0:56 | 0.89031 | 0.91146 | 0 |  | 0:56 | 0 | 0 | 0 | 0:56 | 0.1042 | 0.095785 | 0.0084167 | 1.1179e-06 | 0
[13 empty] | 0:56 | 0.87986 | 0.91146 | 0 |  | 0:56 | 0 | 0 | 0 | 0:56 | 0.10473 | 0.096274 | 0.0084597 | 1.1236e-06 | 0
[13 empty] | 0:57 | 0.86962 | 0.91146 | 0 |  | 0:57 | 0 | 0 | 0 | 0:57 | 0.10526 | 0.096759 | 0.0085023 | 1.1293e-06 | 0
[13 empty] | 0:57 | 0.8596 | 0.91146 | 0 |  | 0:57 | 0 | 0 | 0 | 0:57 | 0.10578 | 0.097237 | 0.0085443 | 1.1349e-06 | 0
[13 empty] | 0:57 | 0.84977 | 0.91146 | 0 |  | 0:57 | 0 | 0 | 0 | 0:57 | 0.1063 | 0.09771 | 0.0085858 | 1.1404e-06 | 0
[13 empty] | 0:58 | 0.84015 | 0.91146 | 0 |  | 0:58 | 0 | 0 | 0 | 0:58 | 0.10681 | 0.098178 | 0.008627 | 1.1458e-06 | 0
[13 empty] | 0:58 | 0.83073 | 0.91146 | 0 |  | 0:58 | 0 | 0 | 0 | 0:58 | 0.10731 | 0.09864 | 0.0086675 | 1.1512e-06 | 0
[13 empty] | 0:58 | 0.8215 | 0.91146 | 0 |  | 0:58 | 0 | 0 | 0 | 0:58 | 0.10781 | 0.099097 | 0.0087078 | 1.1566e-06 | 0
[13 empty] | 0:58 | 0.81247 | 0.91146 | 0 |  | 0:58 | 0 | 0 | 0 | 0:58 | 0.1083 | 0.09955 | 0.0087475 | 1.1619e-06 | 0
[13 empty] | 0:58 | 0.80361 | 0.91146 | 0 |  | 0:58 | 0 | 0 | 0 | 0:58 | 0.10878 | 0.099996 | 0.0087867 | 1.1671e-06 | 0
[13 empty] | 0:59 | 0.79494 | 0.91146 | 0 |  | 0:59 | 0 | 0 | 0 | 0:59 | 0.10927 | 0.10044 | 0.0088257 | 1.1722e-06 | 0
[13 empty] | 0:59 | 0.78645 | 0.91146 | 0 |  | 0:59 | 0 | 0 | 0 | 0:59 | 0.10974 | 0.10088 | 0.008864 | 1.1774e-06 | 0
[13 empty] | 0:59 | 0.77813 | 0.91146 | 0 |  | 0:59 | 0 | 0 | 0 | 0:59 | 0.11021 | 0.10131 | 0.008902 | 1.1824e-06 | 0
[13 empty] | 1:00 | 0.76998 | 0.91146 | 0 |  | 1:00 | 0 | 0 | 0 | 1:00 | 0.11068 | 0.10174 | 0.0089399 | 1.1874e-06 | 0
[13 empty] | 1:00 | 0.762 | 0.91146 | 0 |  | 1:00 | 0 | 0 | 0 | 1:00 | 0.11114 | 0.10216 | 0.0089771 | 1.1923e-06 | 0
[13 empty] | 1:00 | 0.75419 | 0.91146 | 0 |  | 1:00 | 0 | 0 | 0 | 1:00 | 0.1116 | 0.10258 | 0.009014 | 1.1973e-06 | 0
[13 empty] | 1:00 | 0.74653 | 0.91146 | 0 |  | 1:00 | 0 | 0 | 0 | 1:00 | 0.11205 | 0.103 | 0.0090504 | 1.2021e-06 | 0
[13 empty] | 1:00 | 0.73903 | 0.91146 | 0 |  | 1:00 | 0 | 0 | 0 | 1:00 | 0.1125 | 0.10341 | 0.0090865 | 1.2069e-06 | 0
[13 empty] | 1:01 | 0.73169 | 0.91146 | 0 |  | 1:01 | 0 | 0 | 0 | 1:01 | 0.11294 | 0.10382 | 0.0091224 | 1.2117e-06 | 0
[13 empty] | 1:01 | 0.72449 | 0.91146 | 0 |  | 1:01 | 0 | 0 | 0 | 1:01 | 0.11338 | 0.10422 | 0.0091578 | 1.2164e-06 | 0
[13 empty] | 1:01 | 1.1582 | 0.91146 | 0 |  | 1:01 | 0 | 0 | 0 | 1:01 | 0.11408 | 0.10486 | 0.0092145 | 1.2239e-06 | 0
[13 empty] | 1:01 | 1.1422 | 0.91146 | 0 |  | 1:01 | 0 | 0 | 0 | 1:01 | 0.11477 | 0.1055 | 0.0092703 | 1.2313e-06 | 0
[13 empty] | 1:02 | 1.1266 | 0.91146 | 0 |  | 1:02 | 0 | 0 | 0 | 1:02 | 0.11545 | 0.10613 | 0.0093253 | 1.2386e-06 | 0
[13 empty] | 1:02 | 1.1113 | 0.91146 | 0 |  | 1:02 | 0 | 0 | 0 | 1:02 | 0.11612 | 0.10674 | 0.0093797 | 1.2458e-06 | 0
[13 empty] | 1:02 | 1.0963 | 0.91146 | 0 |  | 1:02 | 0 | 0 | 0 | 1:02 | 0.11679 | 0.10736 | 0.0094334 | 1.2529e-06 | 0
[13 empty] | 1:03 | 1.0816 | 0.91146 | 0 |  | 1:03 | 0 | 0 | 0 | 1:03 | 0.11744 | 0.10796 | 0.0094863 | 1.26e-06 | 0
[13 empty] | 1:03 | 1.0673 | 0.91146 | 0 |  | 1:03 | 0 | 0 | 0 | 1:03 | 0.11809 | 0.10855 | 0.0095384 | 1.2669e-06 | 0
[13 empty] | 1:03 | 1.0532 | 0.91146 | 0 |  | 1:03 | 0 | 0 | 0 | 1:03 | 0.11873 | 0.10914 | 0.00959 | 1.2737e-06 | 0
[13 empty] | 1:03 | 1.0394 | 0.91146 | 0 |  | 1:03 | 0 | 0 | 0 | 1:03 | 0.11936 | 0.10972 | 0.0096408 | 1.2805e-06 | 0
[13 empty] | 1:04 | 1.0259 | 0.91146 | 0 |  | 1:04 | 0 | 0 | 0 | 1:04 | 0.11998 | 0.11029 | 0.0096908 | 1.2872e-06 | 0
[13 empty] | 1:04 | 1.0126 | 0.91146 | 0 |  | 1:04 | 0 | 0 | 0 | 1:04 | 0.12059 | 0.11085 | 0.0097405 | 1.2937e-06 | 0
[13 empty] | 1:04 | 0.99966 | 0.91146 | 0 |  | 1:04 | 0 | 0 | 0 | 1:04 | 0.1212 | 0.11141 | 0.0097894 | 1.3002e-06 | 0
[13 empty] | 1:04 | 0.98696 | 0.91146 | 0 |  | 1:04 | 0 | 0 | 0 | 1:04 | 0.12179 | 0.11195 | 0.0098375 | 1.3066e-06 | 0
[13 empty] | 1:04 | 0.97452 | 0.91146 | 0 |  | 1:04 | 0 | 0 | 0 | 1:04 | 0.12238 | 0.1125 | 0.0098852 | 1.313e-06 | 0
[13 empty] | 1:05 | 0.96234 | 0.91146 | 0 |  | 1:05 | 0 | 0 | 0 | 1:05 | 0.12297 | 0.11303 | 0.0099322 | 1.3192e-06 | 0
[13 empty] | 1:05 | 0.95041 | 0.91146 | 0 |  | 1:05 | 0 | 0 | 0 | 1:05 | 0.12354 | 0.11356 | 0.0099788 | 1.3254e-06 | 0
[13 empty] | 1:05 | 0.93872 | 0.91146 | 0 |  | 1:05 | 0 | 0 | 0 | 1:05 | 0.12411 | 0.11408 | 0.010025 | 1.3315e-06 | 0
[13 empty] | 1:06 | 0.92727 | 0.91146 | 0 |  | 1:06 | 0 | 0 | 0 | 1:06 | 0.12467 | 0.1146 | 0.01007 | 1.3375e-06 | 0
[13 empty] | 1:06 | 0.91606 | 0.91146 | 0 |  | 1:06 | 0 | 0 | 0 | 1:06 | 0.12523 | 0.11511 | 0.010115 | 1.3435e-06 | 0
[13 empty] | 1:06 | 0.90508 | 0.91146 | 0 |  | 1:06 | 0 | 0 | 0 | 1:06 | 0.12577 | 0.11561 | 0.010159 | 1.3494e-06 | 0
[13 empty] | 1:06 | 0.89433 | 0.91146 | 0 |  | 1:06 | 0 | 0 | 0 | 1:06 | 0.12632 | 0.11611 | 0.010203 | 1.3552e-06 | 0
[13 empty] | 1:06 | 0.88379 | 0.91146 | 0 |  | 1:06 | 0 | 0 | 0 | 1:06 | 0.12685 | 0.1166 | 0.010246 | 1.3609e-06 | 0
[13 empty] | 1:07 | 0.87347 | 0.91146 | 0 |  | 1:07 | 0 | 0 | 0 | 1:07 | 0.12738 | 0.11709 | 0.010289 | 1.3666e-06 | 0
[13 empty] | 1:07 | 0.86337 | 0.91146 | 0 |  | 1:07 | 0 | 0 | 0 | 1:07 | 0.1279 | 0.11757 | 0.010331 | 1.3722e-06 | 0
[13 empty] | 1:07 | 0.85347 | 0.91146 | 0 |  | 1:07 | 0 | 0 | 0 | 1:07 | 0.12842 | 0.11804 | 0.010373 | 1.3777e-06 | 0
[13 empty] | 1:08 | 0.84377 | 0.91146 | 0 |  | 1:08 | 0 | 0 | 0 | 1:08 | 0.12893 | 0.11851 | 0.010414 | 1.3832e-06 | 0
[13 empty] | 1:08 | 0.83428 | 0.91146 | 0 |  | 1:08 | 0 | 0 | 0 | 1:08 | 0.12943 | 0.11898 | 0.010455 | 1.3886e-06 | 0
[13 empty] | 1:08 | 0.82498 | 0.91146 | 0 |  | 1:08 | 0 | 0 | 0 | 1:08 | 0.12993 | 0.11944 | 0.010495 | 1.394e-06 | 0
[13 empty] | 1:08 | 0.81587 | 0.91146 | 0 |  | 1:08 | 0 | 0 | 0 | 1:08 | 0.13043 | 0.11989 | 0.010535 | 1.3993e-06 | 0
[13 empty] | 1:08 | 0.80694 | 0.91146 | 0 |  | 1:08 | 0 | 0 | 0 | 1:08 | 0.13092 | 0.12034 | 0.010574 | 1.4045e-06 | 0
[13 empty] | 1:09 | 0.7982 | 0.91146 | 0 |  | 1:09 | 0 | 0 | 0 | 1:09 | 0.1314 | 0.12079 | 0.010613 | 1.4097e-06 | 0
[13 empty] | 1:09 | 0.78964 | 0.91146 | 0 |  | 1:09 | 0 | 0 | 0 | 1:09 | 0.13188 | 0.12122 | 0.010652 | 1.4148e-06 | 0
[13 empty] | 1:09 | 0.78126 | 0.91146 | 0 |  | 1:09 | 0 | 0 | 0 | 1:09 | 0.13235 | 0.12166 | 0.01069 | 1.4199e-06 | 0
[13 empty] | 1:10 | 0.77305 | 0.91146 | 0 |  | 1:10 | 0 | 0 | 0 | 1:10 | 0.13282 | 0.12209 | 0.010728 | 1.4249e-06 | 0
[13 empty] | 1:10 | 0.76501 | 0.91146 | 0 |  | 1:10 | 0 | 0 | 0 | 1:10 | 0.13328 | 0.12252 | 0.010765 | 1.4299e-06 | 0
[13 empty] | 1:10 | 0.75713 | 0.91146 | 0 |  | 1:10 | 0 | 0 | 0 | 1:10 | 0.13374 | 0.12294 | 0.010803 | 1.4348e-06 | 0
[13 empty] | 1:10 | 0.74941 | 0.91146 | 0 |  | 1:10 | 0 | 0 | 0 | 1:10 | 0.13419 | 0.12335 | 0.010839 | 1.4397e-06 | 0
[13 empty] | 1:10 | 0.74185 | 0.91146 | 0 |  | 1:10 | 0 | 0 | 0 | 1:10 | 0.13464 | 0.12377 | 0.010876 | 1.4445e-06 | 0
[13 empty] | 1:11 | 0.73445 | 0.91146 | 0 |  | 1:11 | 0 | 0 | 0 | 1:11 | 0.13509 | 0.12418 | 0.010911 | 1.4493e-06 | 0
[13 empty] | 1:11 | 0.7272 | 0.91146 | 0 |  | 1:11 | 0 | 0 | 0 | 1:11 | 0.13553 | 0.12458 | 0.010947 | 1.454e-06 | 0
[13 empty] | 1:11 | 1.1609 | 0.91146 | 0 |  | 1:11 | 0 | 0 | 0 | 1:11 | 0.13623 | 0.12523 | 0.011004 | 1.4615e-06 | 0
[13 empty] | 1:12 | 1.1448 | 0.91146 | 0 |  | 1:12 | 0 | 0 | 0 | 1:12 | 0.13692 | 0.12586 | 0.01106 | 1.469e-06 | 0
[13 empty] | 1:12 | 1.1292 | 0.91146 | 0 |  | 1:12 | 0 | 0 | 0 | 1:12 | 0.13761 | 0.12649 | 0.011115 | 1.4763e-06 | 0
[13 empty] | 1:12 | 1.1138 | 0.91146 | 0 |  | 1:12 | 0 | 0 | 0 | 1:12 | 0.13828 | 0.12711 | 0.011169 | 1.4835e-06 | 0
[13 empty] | 1:12 | 1.0988 | 0.91146 | 0 |  | 1:12 | 0 | 0 | 0 | 1:12 | 0.13895 | 0.12772 | 0.011223 | 1.4907e-06 | 0
[13 empty] | 1:12 | 1.084 | 0.91146 | 0 |  | 1:12 | 0 | 0 | 0 | 1:12 | 0.1396 | 0.12833 | 0.011276 | 1.4977e-06 | 0
[13 empty] | 1:13 | 1.0696 | 0.91146 | 0 |  | 1:13 | 0 | 0 | 0 | 1:13 | 0.14025 | 0.12892 | 0.011328 | 1.5047e-06 | 0
[13 empty] | 1:13 | 1.0555 | 0.91146 | 0 |  | 1:13 | 0 | 0 | 0 | 1:13 | 0.14089 | 0.12951 | 0.01138 | 1.5115e-06 | 0
[13 empty] | 1:13 | 1.0416 | 0.91146 | 0 |  | 1:13 | 0 | 0 | 0 | 1:13 | 0.14152 | 0.13009 | 0.011431 | 1.5183e-06 | 0
[13 empty] | 1:14 | 1.0281 | 0.91146 | 0 |  | 1:14 | 0 | 0 | 0 | 1:14 | 0.14214 | 0.13066 | 0.011481 | 1.5249e-06 | 0
[13 empty] | 1:14 | 1.0148 | 0.91146 | 0 |  | 1:14 | 0 | 0 | 0 | 1:14 | 0.14276 | 0.13122 | 0.011531 | 1.5315e-06 | 0
[13 empty] | 1:14 | 1.0018 | 0.91146 | 0 |  | 1:14 | 0 | 0 | 0 | 1:14 | 0.14336 | 0.13178 | 0.01158 | 1.538e-06 | 0
[13 empty] | 1:14 | 0.98902 | 0.91146 | 0 |  | 1:14 | 0 | 0 | 0 | 1:14 | 0.14396 | 0.13233 | 0.011628 | 1.5445e-06 | 0
[13 empty] | 1:14 | 0.97655 | 0.91146 | 0 |  | 1:14 | 0 | 0 | 0 | 1:14 | 0.14455 | 0.13288 | 0.011676 | 1.5508e-06 | 0
[13 empty] | 1:15 | 0.96432 | 0.91146 | 0 |  | 1:15 | 0 | 0 | 0 | 1:15 | 0.14514 | 0.13341 | 0.011723 | 1.5571e-06 | 0
[13 empty] | 1:15 | 0.95235 | 0.91146 | 0 |  | 1:15 | 0 | 0 | 0 | 1:15 | 0.14571 | 0.13394 | 0.01177 | 1.5633e-06 | 0
[13 empty] | 1:15 | 0.94062 | 0.91146 | 0 |  | 1:15 | 0 | 0 | 0 | 1:15 | 0.14628 | 0.13447 | 0.011816 | 1.5694e-06 | 0
[13 empty] | 1:16 | 0.92914 | 0.91146 | 0 |  | 1:16 | 0 | 0 | 0 | 1:16 | 0.14685 | 0.13498 | 0.011861 | 1.5754e-06 | 0
[13 empty] | 1:16 | 0.91789 | 0.91146 | 0 |  | 1:16 | 0 | 0 | 0 | 1:16 | 0.1474 | 0.13549 | 0.011906 | 1.5814e-06 | 0
[13 empty] | 1:16 | 0.90687 | 0.91146 | 0 |  | 1:16 | 0 | 0 | 0 | 1:16 | 0.14795 | 0.136 | 0.01195 | 1.5873e-06 | 0
[13 empty] | 1:16 | 0.89608 | 0.91146 | 0 |  | 1:16 | 0 | 0 | 0 | 1:16 | 0.14849 | 0.1365 | 0.011994 | 1.5931e-06 | 0
[13 empty] | 1:16 | 0.88551 | 0.91146 | 0 |  | 1:16 | 0 | 0 | 0 | 1:16 | 0.14903 | 0.13699 | 0.012037 | 1.5988e-06 | 0
[13 empty] | 1:17 | 0.87515 | 0.91146 | 0 |  | 1:17 | 0 | 0 | 0 | 1:17 | 0.14956 | 0.13748 | 0.01208 | 1.6045e-06 | 0
[13 empty] | 1:17 | 0.86501 | 0.91146 | 0 |  | 1:17 | 0 | 0 | 0 | 1:17 | 0.15008 | 0.13796 | 0.012122 | 1.6101e-06 | 0
[13 empty] | 1:17 | 0.85508 | 0.91146 | 0 |  | 1:17 | 0 | 0 | 0 | 1:17 | 0.1506 | 0.13843 | 0.012164 | 1.6157e-06 | 0
[13 empty] | 1:18 | 0.84535 | 0.91146 | 0 |  | 1:18 | 0 | 0 | 0 | 1:18 | 0.15111 | 0.1389 | 0.012206 | 1.6212e-06 | 0
[13 empty] | 1:18 | 0.83582 | 0.91146 | 0 |  | 1:18 | 0 | 0 | 0 | 1:18 | 0.15162 | 0.13937 | 0.012247 | 1.6266e-06 | 0
[13 empty] | 1:18 | 0.82649 | 0.91146 | 0 |  | 1:18 | 0 | 0 | 0 | 1:18 | 0.15212 | 0.13983 | 0.012287 | 1.632e-06 | 0
[13 empty] | 1:18 | 0.81735 | 0.91146 | 0 |  | 1:18 | 0 | 0 | 0 | 1:18 | 0.15261 | 0.14028 | 0.012327 | 1.6373e-06 | 0
[13 empty] | 1:18 | 0.8084 | 0.91146 | 0 |  | 1:18 | 0 | 0 | 0 | 1:18 | 0.1531 | 0.14073 | 0.012367 | 1.6425e-06 | 0
[13 empty] | 1:19 | 0.79963 | 0.91146 | 0 |  | 1:19 | 0 | 0 | 0 | 1:19 | 0.15359 | 0.14118 | 0.012405 | 1.6477e-06 | 0
[13 empty] | 1:19 | 0.79104 | 0.91146 | 0 |  | 1:19 | 0 | 0 | 0 | 1:19 | 0.15407 | 0.14162 | 0.012444 | 1.6529e-06 | 0
[13 empty] | 1:19 | 0.78262 | 0.91146 | 0 |  | 1:19 | 0 | 0 | 0 | 1:19 | 0.15454 | 0.14206 | 0.012482 | 1.6579e-06 | 0
[13 empty] | 1:20 | 0.77438 | 0.91146 | 0 |  | 1:20 | 0 | 0 | 0 | 1:20 | 0.15501 | 0.14249 | 0.01252 | 1.663e-06 | 0
[13 empty] | 1:20 | 0.76631 | 0.91146 | 0 |  | 1:20 | 0 | 0 | 0 | 1:20 | 0.15547 | 0.14291 | 0.012558 | 1.668e-06 | 0
[13 empty] | 1:20 | 0.75841 | 0.91146 | 0 |  | 1:20 | 0 | 0 | 0 | 1:20 | 0.15593 | 0.14333 | 0.012595 | 1.6729e-06 | 0
[13 empty] | 1:20 | 0.75067 | 0.91146 | 0 |  | 1:20 | 0 | 0 | 0 | 1:20 | 0.15639 | 0.14375 | 0.012632 | 1.6778e-06 | 0
[13 empty] | 1:20 | 0.74308 | 0.91146 | 0 |  | 1:20 | 0 | 0 | 0 | 1:20 | 0.15684 | 0.14417 | 0.012668 | 1.6826e-06 | 0
[13 empty] | 1:21 | 0.73565 | 0.91146 | 0 |  | 1:21 | 0 | 0 | 0 | 1:21 | 0.15728 | 0.14458 | 0.012704 | 1.6874e-06 | 0
[13 empty] | 1:21 | 0.72838 | 0.91146 | 0 |  | 1:21 | 0 | 0 | 0 | 1:21 | 0.15772 | 0.14498 | 0.01274 | 1.6921e-06 | 0
[13 empty] | 1:21 | 1.162 | 0.91146 | 0 |  | 1:21 | 0 | 0 | 0 | 1:21 | 0.15842 | 0.14563 | 0.012796 | 1.6996e-06 | 0
[13 empty] | 1:22 | 1.146 | 0.91146 | 0 |  | 1:22 | 0 | 0 | 0 | 1:22 | 0.15912 | 0.14626 | 0.012852 | 1.7071e-06 | 0
[13 empty] | 1:22 | 1.1303 | 0.91146 | 0 |  | 1:22 | 0 | 0 | 0 | 1:22 | 0.1598 | 0.14689 | 0.012908 | 1.7144e-06 | 0
[13 empty] | 1:22 | 1.1149 | 0.91146 | 0 |  | 1:22 | 0 | 0 | 0 | 1:22 | 0.16048 | 0.14751 | 0.012962 | 1.7217e-06 | 0
[13 empty] | 1:22 | 1.0998 | 0.91146 | 0 |  | 1:22 | 0 | 0 | 0 | 1:22 | 0.16114 | 0.14813 | 0.013016 | 1.7288e-06 | 0
[13 empty] | 1:22 | 1.0851 | 0.91146 | 0 |  | 1:22 | 0 | 0 | 0 | 1:22 | 0.1618 | 0.14873 | 0.013069 | 1.7359e-06 | 0
[13 empty] | 1:23 | 1.0706 | 0.91146 | 0 |  | 1:23 | 0 | 0 | 0 | 1:23 | 0.16245 | 0.14933 | 0.013121 | 1.7428e-06 | 0
[13 empty] | 1:23 | 1.0565 | 0.91146 | 0 |  | 1:23 | 0 | 0 | 0 | 1:23 | 0.16309 | 0.14991 | 0.013173 | 1.7497e-06 | 0
[13 empty] | 1:23 | 1.0426 | 0.91146 | 0 |  | 1:23 | 0 | 0 | 0 | 1:23 | 0.16372 | 0.1505 | 0.013224 | 1.7564e-06 | 0
[13 empty] | 1:24 | 1.029 | 0.91146 | 0 |  | 1:24 | 0 | 0 | 0 | 1:24 | 0.16434 | 0.15107 | 0.013274 | 1.7631e-06 | 0
[13 empty] | 1:24 | 1.0157 | 0.91146 | 0 |  | 1:24 | 0 | 0 | 0 | 1:24 | 0.16496 | 0.15163 | 0.013324 | 1.7697e-06 | 0
[13 empty] | 1:24 | 1.0027 | 0.91146 | 0 |  | 1:24 | 0 | 0 | 0 | 1:24 | 0.16557 | 0.15219 | 0.013373 | 1.7762e-06 | 0
[13 empty] | 1:24 | 0.98993 | 0.91146 | 0 |  | 1:24 | 0 | 0 | 0 | 1:24 | 0.16616 | 0.15274 | 0.013422 | 1.7827e-06 | 0
[13 empty] | 1:24 | 0.97743 | 0.91146 | 0 |  | 1:24 | 0 | 0 | 0 | 1:24 | 0.16676 | 0.15329 | 0.013469 | 1.789e-06 | 0
[13 empty] | 1:25 | 0.96519 | 0.91146 | 0 |  | 1:25 | 0 | 0 | 0 | 1:25 | 0.16734 | 0.15382 | 0.013516 | 1.7953e-06 | 0
[13 empty] | 1:25 | 0.9532 | 0.91146 | 0 |  | 1:25 | 0 | 0 | 0 | 1:25 | 0.16792 | 0.15435 | 0.013563 | 1.8015e-06 | 0
[13 empty] | 1:25 | 0.94145 | 0.91146 | 0 |  | 1:25 | 0 | 0 | 0 | 1:25 | 0.16849 | 0.15488 | 0.013609 | 1.8076e-06 | 0
[13 empty] | 1:26 | 0.92995 | 0.91146 | 0 |  | 1:26 | 0 | 0 | 0 | 1:26 | 0.16905 | 0.15539 | 0.013655 | 1.8136e-06 | 0
[13 empty] | 1:26 | 0.91868 | 0.91146 | 0 |  | 1:26 | 0 | 0 | 0 | 1:26 | 0.16961 | 0.15591 | 0.013699 | 1.8196e-06 | 0
[13 empty] | 1:26 | 0.90765 | 0.91146 | 0 |  | 1:26 | 0 | 0 | 0 | 1:26 | 0.17016 | 0.15641 | 0.013744 | 1.8255e-06 | 0
[13 empty] | 1:26 | 0.89684 | 0.91146 | 0 |  | 1:26 | 0 | 0 | 0 | 1:26 | 0.1707 | 0.15691 | 0.013788 | 1.8313e-06 | 0
[13 empty] | 1:26 | 0.88625 | 0.91146 | 0 |  | 1:26 | 0 | 0 | 0 | 1:26 | 0.17124 | 0.1574 | 0.013831 | 1.8371e-06 | 0
[13 empty] | 1:27 | 0.87589 | 0.91146 | 0 |  | 1:27 | 0 | 0 | 0 | 1:27 | 0.17177 | 0.15789 | 0.013874 | 1.8428e-06 | 0
[13 empty] | 1:27 | 0.86573 | 0.91146 | 0 |  | 1:27 | 0 | 0 | 0 | 1:27 | 0.17229 | 0.15837 | 0.013916 | 1.8484e-06 | 0
[13 empty] | 1:27 | 0.85578 | 0.91146 | 0 |  | 1:27 | 0 | 0 | 0 | 1:27 | 0.17281 | 0.15885 | 0.013958 | 1.8539e-06 | 0
[13 empty] | 1:28 | 0.84604 | 0.91146 | 0 |  | 1:28 | 0 | 0 | 0 | 1:28 | 0.17332 | 0.15932 | 0.013999 | 1.8594e-06 | 0
[13 empty] | 1:28 | 0.8365 | 0.91146 | 0 |  | 1:28 | 0 | 0 | 0 | 1:28 | 0.17383 | 0.15978 | 0.01404 | 1.8649e-06 | 0
[13 empty] | 1:28 | 0.82715 | 0.91146 | 0 |  | 1:28 | 0 | 0 | 0 | 1:28 | 0.17433 | 0.16024 | 0.014081 | 1.8702e-06 | 0
[13 empty] | 1:28 | 0.818 | 0.91146 | 0 |  | 1:28 | 0 | 0 | 0 | 1:28 | 0.17482 | 0.1607 | 0.014121 | 1.8756e-06 | 0
[13 empty] | 1:28 | 0.80903 | 0.91146 | 0 |  | 1:28 | 0 | 0 | 0 | 1:28 | 0.17531 | 0.16115 | 0.01416 | 1.8808e-06 | 0
[13 empty] | 1:29 | 0.80025 | 0.91146 | 0 |  | 1:29 | 0 | 0 | 0 | 1:29 | 0.1758 | 0.1616 | 0.014199 | 1.886e-06 | 0
[13 empty] | 1:29 | 0.79164 | 0.91146 | 0 |  | 1:29 | 0 | 0 | 0 | 1:29 | 0.17628 | 0.16204 | 0.014238 | 1.8911e-06 | 0
[13 empty] | 1:29 | 0.78322 | 0.91146 | 0 |  | 1:29 | 0 | 0 | 0 | 1:29 | 0.17675 | 0.16247 | 0.014277 | 1.8962e-06 | 0
[13 empty] | 1:30 | 0.77497 | 0.91146 | 0 |  | 1:30 | 0 | 0 | 0 | 1:30 | 0.17722 | 0.1629 | 0.014314 | 1.9013e-06 | 0
[13 empty] | 1:30 | 0.76688 | 0.91146 | 0 |  | 1:30 | 0 | 0 | 0 | 1:30 | 0.17768 | 0.16333 | 0.014352 | 1.9062e-06 | 0
[13 empty] | 1:30 | 0.75897 | 0.91146 | 0 |  | 1:30 | 0 | 0 | 0 | 1:30 | 0.17814 | 0.16375 | 0.014389 | 1.9112e-06 | 0
[13 empty] | 1:30 | 0.75121 | 0.91146 | 0 |  | 1:30 | 0 | 0 | 0 | 1:30 | 0.1786 | 0.16417 | 0.014426 | 1.916e-06 | 0
[13 empty] | 1:30 | 0.74362 | 0.91146 | 0 |  | 1:30 | 0 | 0 | 0 | 1:30 | 0.17905 | 0.16458 | 0.014462 | 1.9209e-06 | 0
[13 empty] | 1:31 | 0.73618 | 0.91146 | 0 |  | 1:31 | 0 | 0 | 0 | 1:31 | 0.17949 | 0.16499 | 0.014498 | 1.9257e-06 | 0
[13 empty] | 1:31 | 0.72889 | 0.91146 | 0 |  | 1:31 | 0 | 0 | 0 | 1:31 | 0.17994 | 0.1654 | 0.014534 | 1.9305e-06 | 0
[13 empty] | 1:31 | 1.1625 | 0.91146 | 0 |  | 1:31 | 0 | 0 | 0 | 1:31 | 0.18064 | 0.16605 | 0.014591 | 1.9379e-06 | 0
[13 empty] | 1:32 | 1.1465 | 0.91146 | 0 |  | 1:32 | 0 | 0 | 0 | 1:32 | 0.18133 | 0.16668 | 0.014647 | 1.9454e-06 | 0
[13 empty] | 1:32 | 1.1308 | 0.91146 | 0 |  | 1:32 | 0 | 0 | 0 | 1:32 | 0.18202 | 0.16731 | 0.014702 | 1.9528e-06 | 0
[13 empty] | 1:32 | 1.1154 | 0.91146 | 0 |  | 1:32 | 0 | 0 | 0 | 1:32 | 0.18269 | 0.16793 | 0.014757 | 1.9599e-06 | 0
[13 empty] | 1:32 | 1.1003 | 0.91146 | 0 |  | 1:32 | 0 | 0 | 0 | 1:32 | 0.18336 | 0.16855 | 0.01481 | 1.9672e-06 | 0
[13 empty] | 1:32 | 1.0855 | 0.91146 | 0 |  | 1:32 | 0 | 0 | 0 | 1:32 | 0.18402 | 0.16915 | 0.014863 | 1.9742e-06 | 0
[13 empty] | 1:33 | 1.0711 | 0.91146 | 0 |  | 1:33 | 0 | 0 | 0 | 1:33 | 0.18466 | 0.16975 | 0.014916 | 1.9811e-06 | 0
[13 empty] | 1:33 | 1.0569 | 0.91146 | 0 |  | 1:33 | 0 | 0 | 0 | 1:33 | 0.1853 | 0.17033 | 0.014967 | 1.988e-06 | 0
[13 empty] | 1:33 | 1.043 | 0.91146 | 0 |  | 1:33 | 0 | 0 | 0 | 1:33 | 0.18594 | 0.17092 | 0.015018 | 1.9948e-06 | 0
[13 empty] | 1:34 | 1.0294 | 0.91146 | 0 |  | 1:34 | 0 | 0 | 0 | 1:34 | 0.18656 | 0.17149 | 0.015069 | 2.0015e-06 | 0
[13 empty] | 1:34 | 1.0161 | 0.91146 | 0 |  | 1:34 | 0 | 0 | 0 | 1:34 | 0.18717 | 0.17205 | 0.015118 | 2.008e-06 | 0
[13 empty] | 1:34 | 1.0031 | 0.91146 | 0 |  | 1:34 | 0 | 0 | 0 | 1:34 | 0.18778 | 0.17261 | 0.015168 | 2.0145e-06 | 0
[13 empty] | 1:34 | 0.99032 | 0.91146 | 0 |  | 1:34 | 0 | 0 | 0 | 1:34 | 0.18838 | 0.17316 | 0.015216 | 2.021e-06 | 0
[13 empty] | 1:34 | 0.97781 | 0.91146 | 0 |  | 1:34 | 0 | 0 | 0 | 1:34 | 0.18897 | 0.17371 | 0.015264 | 2.0273e-06 | 0
[13 empty] | 1:35 | 0.96556 | 0.91146 | 0 |  | 1:35 | 0 | 0 | 0 | 1:35 | 0.18956 | 0.17424 | 0.015311 | 2.0336e-06 | 0
[13 empty] | 1:35 | 0.95357 | 0.91146 | 0 |  | 1:35 | 0 | 0 | 0 | 1:35 | 0.19013 | 0.17478 | 0.015358 | 2.0399e-06 | 0
[13 empty] | 1:35 | 0.94181 | 0.91146 | 0 |  | 1:35 | 0 | 0 | 0 | 1:35 | 0.19071 | 0.1753 | 0.015404 | 2.046e-06 | 0
[13 empty] | 1:36 | 0.9303 | 0.91146 | 0 |  | 1:36 | 0 | 0 | 0 | 1:36 | 0.19127 | 0.17582 | 0.015449 | 2.052e-06 | 0
[13 empty] | 1:36 | 0.91903 | 0.91146 | 0 |  | 1:36 | 0 | 0 | 0 | 1:36 | 0.19182 | 0.17633 | 0.015494 | 2.0579e-06 | 0
[13 empty] | 1:36 | 0.90799 | 0.91146 | 0 |  | 1:36 | 0 | 0 | 0 | 1:36 | 0.19237 | 0.17683 | 0.015538 | 2.0638e-06 | 0
[13 empty] | 1:36 | 0.89717 | 0.91146 | 0 |  | 1:36 | 0 | 0 | 0 | 1:36 | 0.19292 | 0.17733 | 0.015582 | 2.0697e-06 | 0
[13 empty] | 1:36 | 0.88658 | 0.91146 | 0 |  | 1:36 | 0 | 0 | 0 | 1:36 | 0.19345 | 0.17783 | 0.015626 | 2.0754e-06 | 0
[13 empty] | 1:37 | 0.87621 | 0.91146 | 0 |  | 1:37 | 0 | 0 | 0 | 1:37 | 0.19398 | 0.17831 | 0.015669 | 2.0812e-06 | 0
[13 empty] | 1:37 | 0.86604 | 0.91146 | 0 |  | 1:37 | 0 | 0 | 0 | 1:37 | 0.19451 | 0.1788 | 0.015711 | 2.0867e-06 | 0
[13 empty] | 1:37 | 0.85609 | 0.91146 | 0 |  | 1:37 | 0 | 0 | 0 | 1:37 | 0.19503 | 0.17927 | 0.015753 | 2.0923e-06 | 0
[13 empty] | 1:38 | 0.84634 | 0.91146 | 0 |  | 1:38 | 0 | 0 | 0 | 1:38 | 0.19554 | 0.17974 | 0.015794 | 2.0978e-06 | 0
[13 empty] | 1:38 | 0.83679 | 0.91146 | 0 |  | 1:38 | 0 | 0 | 0 | 1:38 | 0.19605 | 0.18021 | 0.015835 | 2.1033e-06 | 0
[13 empty] | 1:38 | 0.82744 | 0.91146 | 0 |  | 1:38 | 0 | 0 | 0 | 1:38 | 0.19655 | 0.18067 | 0.015876 | 2.1087e-06 | 0
[13 empty] | 1:38 | 0.81828 | 0.91146 | 0 |  | 1:38 | 0 | 0 | 0 | 1:38 | 0.19704 | 0.18113 | 0.015916 | 2.114e-06 | 0
[13 empty] | 1:38 | 0.8093 | 0.91146 | 0 |  | 1:38 | 0 | 0 | 0 | 1:38 | 0.19753 | 0.18158 | 0.015955 | 2.1192e-06 | 0
[13 empty] | 1:39 | 0.80052 | 0.91146 | 0 |  | 1:39 | 0 | 0 | 0 | 1:39 | 0.19802 | 0.18202 | 0.015994 | 2.1243e-06 | 0
[13 empty] | 1:39 | 0.79191 | 0.91146 | 0 |  | 1:39 | 0 | 0 | 0 | 1:39 | 0.1985 | 0.18246 | 0.016033 | 2.1295e-06 | 0
[13 empty] | 1:39 | 0.78348 | 0.91146 | 0 |  | 1:39 | 0 | 0 | 0 | 1:39 | 0.19897 | 0.1829 | 0.016071 | 2.1346e-06 | 0
[13 empty] | 1:39 | 0.77522 | 0.91146 | 0 |  | 1:39 | 0 | 0 | 0 | 1:39 | 0.19944 | 0.18333 | 0.016109 | 2.1396e-06 | 0
[13 empty] | 1:40 | 0.76713 | 0.91146 | 0 |  | 1:40 | 0 | 0 | 0 | 1:40 | 0.1999 | 0.18376 | 0.016147 | 2.1446e-06 | 0
[13 empty] | 1:40 | 0.75921 | 0.91146 | 0 |  | 1:40 | 0 | 0 | 0 | 1:40 | 0.20037 | 0.18418 | 0.016184 | 2.1495e-06 | 0
[13 empty] | 1:40 | 0.75145 | 0.91146 | 0 |  | 1:40 | 0 | 0 | 0 | 1:40 | 0.20082 | 0.1846 | 0.016221 | 2.1545e-06 | 0
[13 empty] | 1:40 | 0.74385 | 0.91146 | 0 |  | 1:40 | 0 | 0 | 0 | 1:40 | 0.20127 | 0.18501 | 0.016257 | 2.1593e-06 | 0
[13 empty] | 1:41 | 0.73641 | 0.91146 | 0 |  | 1:41 | 0 | 0 | 0 | 1:41 | 0.20172 | 0.18542 | 0.016293 | 2.1641e-06 | 0
[13 empty] | 1:41 | 0.72912 | 0.91146 | 0 |  | 1:41 | 0 | 0 | 0 | 1:41 | 0.20216 | 0.18583 | 0.016329 | 2.1688e-06 | 0
[13 empty] | 1:41 | 1.1627 | 0.91146 | 0 |  | 1:41 | 0 | 0 | 0 | 1:41 | 0.20286 | 0.18647 | 0.016385 | 2.1763e-06 | 0
[13 empty] | 1:42 | 1.1467 | 0.91146 | 0 |  | 1:42 | 0 | 0 | 0 | 1:42 | 0.20355 | 0.18711 | 0.016442 | 2.1837e-06 | 0
[13 empty] | 1:42 | 1.131 | 0.91146 | 0 |  | 1:42 | 0 | 0 | 0 | 1:42 | 0.20424 | 0.18774 | 0.016497 | 2.1912e-06 | 0
[13 empty] | 1:42 | 1.1156 | 0.91146 | 0 |  | 1:42 | 0 | 0 | 0 | 1:42 | 0.20492 | 0.18836 | 0.016551 | 2.1984e-06 | 0
[13 empty] | 1:42 | 1.1005 | 0.91146 | 0 |  | 1:42 | 0 | 0 | 0 | 1:42 | 0.20558 | 0.18897 | 0.016605 | 2.2055e-06 | 0
[13 empty] | 1:43 | 1.0857 | 0.91146 | 0 |  | 1:43 | 0 | 0 | 0 | 1:43 | 0.20624 | 0.18958 | 0.016658 | 2.2126e-06 | 0
[13 empty] | 1:43 | 1.0713 | 0.91146 | 0 |  | 1:43 | 0 | 0 | 0 | 1:43 | 0.20689 | 0.19017 | 0.016711 | 2.2196e-06 | 0
[13 empty] | 1:43 | 1.0571 | 0.91146 | 0 |  | 1:43 | 0 | 0 | 0 | 1:43 | 0.20753 | 0.19076 | 0.016762 | 2.2265e-06 | 0
[13 empty] | 1:43 | 1.0432 | 0.91146 | 0 |  | 1:43 | 0 | 0 | 0 | 1:43 | 0.20816 | 0.19135 | 0.016813 | 2.2332e-06 | 0
[13 empty] | 1:44 | 1.0296 | 0.91146 | 0 |  | 1:44 | 0 | 0 | 0 | 1:44 | 0.20879 | 0.19192 | 0.016864 | 2.2399e-06 | 0
[13 empty] | 1:44 | 1.0163 | 0.91146 | 0 |  | 1:44 | 0 | 0 | 0 | 1:44 | 0.20939 | 0.19248 | 0.016914 | 2.2466e-06 | 0
[13 empty] | 1:44 | 1.0033 | 0.91146 | 0 |  | 1:44 | 0 | 0 | 0 | 1:44 | 0.21001 | 0.19305 | 0.016963 | 2.2531e-06 | 0
[13 empty] | 1:44 | 0.99049 | 0.91146 | 0 |  | 1:44 | 0 | 0 | 0 | 1:44 | 0.2106 | 0.19358 | 0.017011 | 2.2594e-06 | 0
[13 empty] | 1:45 | 0.97798 | 0.91146 | 0 |  | 1:45 | 0 | 0 | 0 | 1:45 | 0.2112 | 0.19414 | 0.017059 | 2.2659e-06 | 0
[13 empty] | 1:45 | 0.96573 | 0.91146 | 0 |  | 1:45 | 0 | 0 | 0 | 1:45 | 0.21178 | 0.19467 | 0.017106 | 2.272e-06 | 0
[13 empty] | 1:45 | 0.95373 | 0.91146 | 0 |  | 1:45 | 0 | 0 | 0 | 1:45 | 0.21236 | 0.19521 | 0.017153 | 2.2783e-06 | 0
[13 empty] | 1:45 | 0.94197 | 0.91146 | 0 |  | 1:45 | 0 | 0 | 0 | 1:45 | 0.21292 | 0.19572 | 0.017199 | 2.2844e-06 | 0
[13 empty] | 1:46 | 0.93046 | 0.91146 | 0 |  | 1:46 | 0 | 0 | 0 | 1:46 | 0.21348 | 0.19624 | 0.017244 | 2.2905e-06 | 0
[13 empty] | 1:46 | 0.91918 | 0.91146 | 0 |  | 1:46 | 0 | 0 | 0 | 1:46 | 0.21405 | 0.19675 | 0.017289 | 2.2964e-06 | 0
[13 empty] | 1:46 | 0.90814 | 0.91146 | 0 |  | 1:46 | 0 | 0 | 0 | 1:46 | 0.21461 | 0.19727 | 0.017334 | 2.3023e-06 | 0
[13 empty] | 1:46 | 0.89732 | 0.91146 | 0 |  | 1:46 | 0 | 0 | 0 | 1:46 | 0.21515 | 0.19777 | 0.017377 | 2.3081e-06 | 0
[13 empty] | 1:46 | 0.88672 | 0.91146 | 0 |  | 1:46 | 0 | 0 | 0 | 1:46 | 0.21569 | 0.19826 | 0.017421 | 2.3138e-06 | 0
[13 empty] | 1:47 | 0.87634 | 0.91146 | 0 |  | 1:47 | 0 | 0 | 0 | 1:47 | 0.21621 | 0.19874 | 0.017464 | 2.3195e-06 | 0
[13 empty] | 1:47 | 0.86618 | 0.91146 | 0 |  | 1:47 | 0 | 0 | 0 | 1:47 | 0.21673 | 0.19922 | 0.017506 | 2.3253e-06 | 0
[13 empty] | 1:47 | 0.85622 | 0.91146 | 0 |  | 1:47 | 0 | 0 | 0 | 1:47 | 0.21725 | 0.19969 | 0.017548 | 2.3308e-06 | 0
[13 empty] | 1:48 | 0.84647 | 0.91146 | 0 |  | 1:48 | 0 | 0 | 0 | 1:48 | 0.21776 | 0.20017 | 0.017589 | 2.3363e-06 | 0
[13 empty] | 1:48 | 0.83692 | 0.91146 | 0 |  | 1:48 | 0 | 0 | 0 | 1:48 | 0.21826 | 0.20063 | 0.01763 | 2.3417e-06 | 0
[13 empty] | 1:48 | 0.82756 | 0.91146 | 0 |  | 1:48 | 0 | 0 | 0 | 1:48 | 0.21878 | 0.20111 | 0.017671 | 2.347e-06 | 0
[13 empty] | 1:48 | 0.8184 | 0.91146 | 0 |  | 1:48 | 0 | 0 | 0 | 1:48 | 0.21926 | 0.20155 | 0.017711 | 2.3524e-06 | 0
[13 empty] | 1:48 | 0.80943 | 0.91146 | 0 |  | 1:48 | 0 | 0 | 0 | 1:48 | 0.21976 | 0.20201 | 0.01775 | 2.3577e-06 | 0
[13 empty] | 1:49 | 0.80064 | 0.91146 | 0 |  | 1:49 | 0 | 0 | 0 | 1:49 | 0.22024 | 0.20245 | 0.017789 | 2.3629e-06 | 0
[13 empty] | 1:49 | 0.79202 | 0.91146 | 0 |  | 1:49 | 0 | 0 | 0 | 1:49 | 0.22071 | 0.20288 | 0.017828 | 2.368e-06 | 0
[13 empty] | 1:49 | 0.78359 | 0.91146 | 0 |  | 1:49 | 0 | 0 | 0 | 1:49 | 0.22119 | 0.20332 | 0.017867 | 2.373e-06 | 0
[13 empty] | 1:49 | 0.77533 | 0.91146 | 0 |  | 1:49 | 0 | 0 | 0 | 1:49 | 0.22167 | 0.20376 | 0.017904 | 2.3782e-06 | 0
[13 empty] | 1:50 | 0.76724 | 0.91146 | 0 |  | 1:50 | 0 | 0 | 0 | 1:50 | 0.22213 | 0.20418 | 0.017942 | 2.3831e-06 | 0
[13 empty] | 1:50 | 0.75932 | 0.91146 | 0 |  | 1:50 | 0 | 0 | 0 | 1:50 | 0.22258 | 0.2046 | 0.017979 | 2.3881e-06 | 0
[13 empty] | 1:50 | 0.75156 | 0.91146 | 0 |  | 1:50 | 0 | 0 | 0 | 1:50 | 0.22304 | 0.20502 | 0.018016 | 2.3929e-06 | 0
[13 empty] | 1:50 | 0.74396 | 0.91146 | 0 |  | 1:50 | 0 | 0 | 0 | 1:50 | 0.2235 | 0.20544 | 0.018052 | 2.3976e-06 | 0
[13 empty] | 1:51 | 0.73651 | 0.91146 | 0 |  | 1:51 | 0 | 0 | 0 | 1:51 | 0.22394 | 0.20584 | 0.018088 | 2.4026e-06 | 0
[13 empty] | 1:51 | 0.72922 | 0.91146 | 0 |  | 1:51 | 0 | 0 | 0 | 1:51 | 0.22439 | 0.20626 | 0.018124 | 2.4072e-06 | 0
[13 empty] | 1:51 | 1.1628 | 0.91146 | 0 |  | 1:51 | 0 | 0 | 0 | 1:51 | 0.22508 | 0.2069 | 0.018181 | 2.4148e-06 | 0
[13 empty] | 1:52 | 1.1468 | 0.91146 | 0 |  | 1:52 | 0 | 0 | 0 | 1:52 | 0.22578 | 0.20754 | 0.018237 | 2.4223e-06 | 0
[13 empty] | 1:52 | 1.1311 | 0.91146 | 0 |  | 1:52 | 0 | 0 | 0 | 1:52 | 0.22647 | 0.20817 | 0.018292 | 2.4295e-06 | 0
[13 empty] | 1:52 | 1.1157 | 0.91146 | 0 |  | 1:52 | 0 | 0 | 0 | 1:52 | 0.22713 | 0.20879 | 0.018347 | 2.4368e-06 | 0
[13 empty] | 1:52 | 1.1006 | 0.91146 | 0 |  | 1:52 | 0 | 0 | 0 | 1:52 | 0.2278 | 0.2094 | 0.018401 | 2.444e-06 | 0
[13 empty] | 1:52 | 1.0858 | 0.91146 | 0 |  | 1:52 | 0 | 0 | 0 | 1:52 | 0.22846 | 0.21001 | 0.018454 | 2.4511e-06 | 0
[13 empty] | 1:53 | 1.0713 | 0.91146 | 0 |  | 1:53 | 0 | 0 | 0 | 1:53 | 0.22911 | 0.2106 | 0.018506 | 2.458e-06 | 0
[13 empty] | 1:53 | 1.0572 | 0.91146 | 0 |  | 1:53 | 0 | 0 | 0 | 1:53 | 0.22975 | 0.21119 | 0.018558 | 2.4649e-06 | 0
[13 empty] | 1:53 | 1.0433 | 0.91146 | 0 |  | 1:53 | 0 | 0 | 0 | 1:53 | 0.23038 | 0.21177 | 0.018609 | 2.4715e-06 | 0
[13 empty] | 1:54 | 1.0297 | 0.91146 | 0 |  | 1:54 | 0 | 0 | 0 | 1:54 | 0.231 | 0.21234 | 0.018659 | 2.4784e-06 | 0
[13 empty] | 1:54 | 1.0164 | 0.91146 | 0 |  | 1:54 | 0 | 0 | 0 | 1:54 | 0.23162 | 0.21291 | 0.018709 | 2.4849e-06 | 0
[13 empty] | 1:54 | 1.0033 | 0.91146 | 0 |  | 1:54 | 0 | 0 | 0 | 1:54 | 0.23223 | 0.21346 | 0.018758 | 2.4914e-06 | 0
[13 empty] | 1:54 | 0.99056 | 0.91146 | 0 |  | 1:54 | 0 | 0 | 0 | 1:54 | 0.23283 | 0.21402 | 0.018806 | 2.4979e-06 | 0
[13 empty] | 1:54 | 0.97805 | 0.91146 | 0 |  | 1:54 | 0 | 0 | 0 | 1:54 | 0.23343 | 0.21457 | 0.018854 | 2.5042e-06 | 0
[13 empty] | 1:55 | 0.9658 | 0.91146 | 0 |  | 1:55 | 0 | 0 | 0 | 1:55 | 0.23401 | 0.21511 | 0.018901 | 2.5105e-06 | 0
[13 empty] | 1:55 | 0.9538 | 0.91146 | 0 |  | 1:55 | 0 | 0 | 0 | 1:55 | 0.23459 | 0.21564 | 0.018948 | 2.5166e-06 | 0
[13 empty] | 1:55 | 0.94204 | 0.91146 | 0 |  | 1:55 | 0 | 0 | 0 | 1:55 | 0.23515 | 0.21616 | 0.018994 | 2.5227e-06 | 0
[13 empty] | 1:56 | 0.93053 | 0.91146 | 0 |  | 1:56 | 0 | 0 | 0 | 1:56 | 0.23572 | 0.21667 | 0.01904 | 2.5288e-06 | 0
[13 empty] | 1:56 | 0.91925 | 0.91146 | 0 |  | 1:56 | 0 | 0 | 0 | 1:56 | 0.23628 | 0.21719 | 0.019084 | 2.5348e-06 | 0
[13 empty] | 1:56 | 0.9082 | 0.91146 | 0 |  | 1:56 | 0 | 0 | 0 | 1:56 | 0.23682 | 0.21769 | 0.019129 | 2.5407e-06 | 0
[13 empty] | 1:56 | 0.89738 | 0.91146 | 0 |  | 1:56 | 0 | 0 | 0 | 1:56 | 0.23738 | 0.2182 | 0.019173 | 2.5466e-06 | 0
[13 empty] | 1:56 | 0.88678 | 0.91146 | 0 |  | 1:56 | 0 | 0 | 0 | 1:56 | 0.2379 | 0.21868 | 0.019217 | 2.5523e-06 | 0
[13 empty] | 1:57 | 0.87641 | 0.91146 | 0 |  | 1:57 | 0 | 0 | 0 | 1:57 | 0.23844 | 0.21918 | 0.019259 | 2.5581e-06 | 0
[13 empty] | 1:57 | 0.86624 | 0.91146 | 0 |  | 1:57 | 0 | 0 | 0 | 1:57 | 0.23896 | 0.21965 | 0.019301 | 2.5636e-06 | 0
[13 empty] | 1:57 | 0.85628 | 0.91146 | 0 |  | 1:57 | 0 | 0 | 0 | 1:57 | 0.23948 | 0.22013 | 0.019343 | 2.5691e-06 | 0
[13 empty] | 1:58 | 0.84653 | 0.91146 | 0 |  | 1:58 | 0 | 0 | 0 | 1:58 | 0.24 | 0.22061 | 0.019385 | 2.5747e-06 | 0
[13 empty] | 1:58 | 0.83697 | 0.91146 | 0 |  | 1:58 | 0 | 0 | 0 | 1:58 | 0.24049 | 0.22107 | 0.019425 | 2.5802e-06 | 0
[13 empty] | 1:58 | 0.82762 | 0.91146 | 0 |  | 1:58 | 0 | 0 | 0 | 1:58 | 0.24099 | 0.22152 | 0.019465 | 2.5856e-06 | 0
[13 empty] | 1:58 | 0.81845 | 0.91146 | 0 |  | 1:58 | 0 | 0 | 0 | 1:58 | 0.24149 | 0.22198 | 0.019505 | 2.5909e-06 | 0
[13 empty] | 1:58 | 0.80948 | 0.91146 | 0 |  | 1:58 | 0 | 0 | 0 | 1:58 | 0.24199 | 0.22244 | 0.019545 | 2.5961e-06 | 0
[13 empty] | 1:59 | 0.80069 | 0.91146 | 0 |  | 1:59 | 0 | 0 | 0 | 1:59 | 0.24247 | 0.22288 | 0.019586 | 2.6012e-06 | 0
[13 empty] | 1:59 | 0.79208 | 0.91146 | 0 |  | 1:59 | 0 | 0 | 0 | 1:59 | 0.24295 | 0.22332 | 0.019624 | 2.6064e-06 | 0
[13 empty] | 1:59 | 0.78364 | 0.91146 | 0 |  | 1:59 | 0 | 0 | 0 | 1:59 | 0.24342 | 0.22376 | 0.019662 | 2.6115e-06 | 0
[13 empty] | 2:00 | 0.77538 | 0.91146 | 0 |  | 2:00 | 0 | 0 | 0 | 2:00 | 0.2439 | 0.2242 | 0.0197 | 2.6165e-06 | 0
[13 empty] | 2:00 | 0.76729 | 0.91146 | 0 |  | 2:00 | 0 | 0 | 0 | 2:00 | 0.24436 | 0.22462 | 0.019736 | 2.6215e-06 | 0
[13 empty] | 2:00 | 0.75936 | 0.91146 | 0 |  | 2:00 | 0 | 0 | 0 | 2:00 | 0.24482 | 0.22504 | 0.019775 | 2.6264e-06 | 0
[13 empty] | 2:00 | 0.7516 | 0.91146 | 0 |  | 2:00 | 0 | 0 | 0 | 2:00 | 0.24527 | 0.22546 | 0.019811 | 2.6314e-06 | 0
[13 empty] | 2:00 | 0.744 | 0.91146 | 0 |  | 2:00 | 0 | 0 | 0 | 2:00 | 0.24573 | 0.22588 | 0.019847 | 2.6362e-06 | 0
[13 empty] | 2:01 | 0.73655 | 0.91146 | 0 |  | 2:01 | 0 | 0 | 0 | 2:01 | 0.24617 | 0.22628 | 0.019884 | 2.641e-06 | 0
[13 empty] | 2:01 | 0.72926 | 0.91146 | 0 |  | 2:01 | 0 | 0 | 0 | 2:01 | 0.2466 | 0.22668 | 0.01992 | 2.6457e-06 | 0
[13 empty] | 2:01 | 1.1629 | 0.91146 | 0 |  | 2:01 | 0 | 0 | 0 | 2:01 | 0.24731 | 0.22733 | 0.019975 | 2.6532e-06 | 0
[13 empty] | 2:01 | 1.1468 | 0.91146 | 0 |  | 2:01 | 0 | 0 | 0 | 2:01 | 0.24802 | 0.22798 | 0.020033 | 2.6606e-06 | 0
[13 empty] | 2:02 | 1.1311 | 0.91146 | 0 |  | 2:02 | 0 | 0 | 0 | 2:02 | 0.2487 | 0.22861 | 0.020088 | 2.6681e-06 | 0
[13 empty] | 2:02 | 1.1157 | 0.91146 | 0 |  | 2:02 | 0 | 0 | 0 | 2:02 | 0.24937 | 0.22922 | 0.020141 | 2.6753e-06 | 0
[13 empty] | 2:02 | 1.1006 | 0.91146 | 0 |  | 2:02 | 0 | 0 | 0 | 2:02 | 0.25003 | 0.22983 | 0.020195 | 2.6824e-06 | 0
[13 empty] | 2:02 | 1.0858 | 0.91146 | 0 |  | 2:02 | 0 | 0 | 0 | 2:02 | 0.25069 | 0.23044 | 0.020248 | 2.6895e-06 | 0
[13 empty] | 2:03 | 1.0714 | 0.91146 | 0 |  | 2:03 | 0 | 0 | 0 | 2:03 | 0.25134 | 0.23104 | 0.020302 | 2.6965e-06 | 0
[13 empty] | 2:03 | 1.0572 | 0.91146 | 0 |  | 2:03 | 0 | 0 | 0 | 2:03 | 0.25198 | 0.23163 | 0.020353 | 2.7034e-06 | 0
[13 empty] | 2:03 | 1.0433 | 0.91146 | 0 |  | 2:03 | 0 | 0 | 0 | 2:03 | 0.25261 | 0.2322 | 0.020405 | 2.7101e-06 | 0
[13 empty] | 2:03 | 1.0297 | 0.91146 | 0 |  | 2:03 | 0 | 0 | 0 | 2:03 | 0.25323 | 0.23277 | 0.020455 | 2.7168e-06 | 0
[13 empty] | 2:04 | 1.0164 | 0.91146 | 0 |  | 2:04 | 0 | 0 | 0 | 2:04 | 0.25385 | 0.23335 | 0.020504 | 2.7235e-06 | 0
[13 empty] | 2:04 | 1.0034 | 0.91146 | 0 |  | 2:04 | 0 | 0 | 0 | 2:04 | 0.25446 | 0.2339 | 0.020554 | 2.73e-06 | 0
[13 empty] | 2:04 | 0.9906 | 0.91146 | 0 |  | 2:04 | 0 | 0 | 0 | 2:04 | 0.25506 | 0.23445 | 0.020602 | 2.7363e-06 | 0
[13 empty] | 2:05 | 0.97808 | 0.91146 | 0 |  | 2:05 | 0 | 0 | 0 | 2:05 | 0.25564 | 0.23499 | 0.020649 | 2.7427e-06 | 0
[13 empty] | 2:05 | 0.96583 | 0.91146 | 0 |  | 2:05 | 0 | 0 | 0 | 2:05 | 0.25624 | 0.23554 | 0.020697 | 2.7491e-06 | 0
[13 empty] | 2:05 | 0.95383 | 0.91146 | 0 |  | 2:05 | 0 | 0 | 0 | 2:05 | 0.2568 | 0.23606 | 0.020743 | 2.7552e-06 | 0
[13 empty] | 2:05 | 0.94207 | 0.91146 | 0 |  | 2:05 | 0 | 0 | 0 | 2:05 | 0.25738 | 0.23659 | 0.020789 | 2.7613e-06 | 0
[13 empty] | 2:06 | 0.93055 | 0.91146 | 0 |  | 2:06 | 0 | 0 | 0 | 2:06 | 0.25795 | 0.23711 | 0.020835 | 2.7674e-06 | 0
[13 empty] | 2:06 | 0.91928 | 0.91146 | 0 |  | 2:06 | 0 | 0 | 0 | 2:06 | 0.25851 | 0.23762 | 0.02088 | 2.7733e-06 | 0
[13 empty] | 2:06 | 0.90823 | 0.91146 | 0 |  | 2:06 | 0 | 0 | 0 | 2:06 | 0.25905 | 0.23812 | 0.020924 | 2.7792e-06 | 0
[13 empty] | 2:06 | 0.89741 | 0.91146 | 0 |  | 2:06 | 0 | 0 | 0 | 2:06 | 0.25959 | 0.23862 | 0.020968 | 2.785e-06 | 0
[13 empty] | 2:07 | 0.88681 | 0.91146 | 0 |  | 2:07 | 0 | 0 | 0 | 2:07 | 0.26013 | 0.23911 | 0.021012 | 2.7909e-06 | 0
[13 empty] | 2:07 | 0.87643 | 0.91146 | 0 |  | 2:07 | 0 | 0 | 0 | 2:07 | 0.26067 | 0.23961 | 0.021054 | 2.7964e-06 | 0
[13 empty] | 2:07 | 0.86626 | 0.91146 | 0 |  | 2:07 | 0 | 0 | 0 | 2:07 | 0.26119 | 0.24009 | 0.021096 | 2.8021e-06 | 0
[13 empty] | 2:07 | 0.85631 | 0.91146 | 0 |  | 2:07 | 0 | 0 | 0 | 2:07 | 0.26171 | 0.24057 | 0.021138 | 2.8077e-06 | 0
[13 empty] | 2:08 | 0.84655 | 0.91146 | 0 |  | 2:08 | 0 | 0 | 0 | 2:08 | 0.26223 | 0.24104 | 0.02118 | 2.8132e-06 | 0
[13 empty] | 2:08 | 0.837 | 0.91146 | 0 |  | 2:08 | 0 | 0 | 0 | 2:08 | 0.26272 | 0.2415 | 0.02122 | 2.8186e-06 | 0
[13 empty] | 2:08 | 0.82764 | 0.91146 | 0 |  | 2:08 | 0 | 0 | 0 | 2:08 | 0.26322 | 0.24196 | 0.021261 | 2.8239e-06 | 0
[13 empty] | 2:08 | 0.81848 | 0.91146 | 0 |  | 2:08 | 0 | 0 | 0 | 2:08 | 0.26372 | 0.24242 | 0.021301 | 2.8293e-06 | 0
[13 empty] | 2:08 | 0.8095 | 0.91146 | 0 |  | 2:08 | 0 | 0 | 0 | 2:08 | 0.26422 | 0.24288 | 0.021341 | 2.8346e-06 | 0
[13 empty] | 2:09 | 0.80071 | 0.91146 | 0 |  | 2:09 | 0 | 0 | 0 | 2:09 | 0.2647 | 0.24332 | 0.021381 | 2.8398e-06 | 0
[13 empty] | 2:09 | 0.7921 | 0.91146 | 0 |  | 2:09 | 0 | 0 | 0 | 2:09 | 0.26518 | 0.24376 | 0.021419 | 2.8449e-06 | 0
[13 empty] | 2:09 | 0.78366 | 0.91146 | 0 |  | 2:09 | 0 | 0 | 0 | 2:09 | 0.26565 | 0.24419 | 0.021457 | 2.8499e-06 | 0
[13 empty] | 2:10 | 0.7754 | 0.91146 | 0 |  | 2:10 | 0 | 0 | 0 | 2:10 | 0.26611 | 0.24461 | 0.021495 | 2.855e-06 | 0
[13 empty] | 2:10 | 0.76731 | 0.91146 | 0 |  | 2:10 | 0 | 0 | 0 | 2:10 | 0.26659 | 0.24505 | 0.021532 | 2.86e-06 | 0
[13 empty] | 2:10 | 0.75938 | 0.91146 | 0 |  | 2:10 | 0 | 0 | 0 | 2:10 | 0.26705 | 0.24547 | 0.02157 | 2.865e-06 | 0
[13 empty] | 2:10 | 0.75162 | 0.91146 | 0 |  | 2:10 | 0 | 0 | 0 | 2:10 | 0.2675 | 0.24589 | 0.021606 | 2.8698e-06 | 0
[13 empty] | 2:10 | 0.74402 | 0.91146 | 0 |  | 2:10 | 0 | 0 | 0 | 2:10 | 0.26794 | 0.2463 | 0.021643 | 2.8747e-06 | 0
[13 empty] | 2:11 | 0.73657 | 0.91146 | 0 |  | 2:11 | 0 | 0 | 0 | 2:11 | 0.2684 | 0.24672 | 0.021679 | 2.8795e-06 | 0
[13 empty] | 2:11 | 0.72928 | 0.91146 | 0 |  | 2:11 | 0 | 0 | 0 | 2:11 | 0.26883 | 0.24712 | 0.021715 | 2.8841e-06 | 0
[13 empty] | 2:11 | 1.1629 | 0.91146 | 0 |  | 2:11 | 0 | 0 | 0 | 2:11 | 0.26954 | 0.24777 | 0.02177 | 2.8917e-06 | 0
[13 empty] | 2:12 | 1.1468 | 0.91146 | 0 |  | 2:12 | 0 | 0 | 0 | 2:12 | 0.27023 | 0.2484 | 0.021828 | 2.8992e-06 | 0
[13 empty] | 2:12 | 1.1311 | 0.91146 | 0 |  | 2:12 | 0 | 0 | 0 | 2:12 | 0.27091 | 0.24903 | 0.021883 | 2.9064e-06 | 0
[13 empty] | 2:12 | 1.1157 | 0.91146 | 0 |  | 2:12 | 0 | 0 | 0 | 2:12 | 0.2716 | 0.24966 | 0.021937 | 2.9137e-06 | 0
[13 empty] | 2:12 | 1.1006 | 0.91146 | 0 |  | 2:12 | 0 | 0 | 0 | 2:12 | 0.27226 | 0.25027 | 0.021992 | 2.9209e-06 | 0
[13 empty] | 2:12 | 1.0859 | 0.91146 | 0 |  | 2:12 | 0 | 0 | 0 | 2:12 | 0.27293 | 0.25088 | 0.022044 | 2.928e-06 | 0
[13 empty] | 2:13 | 1.0714 | 0.91146 | 0 |  | 2:13 | 0 | 0 | 0 | 2:13 | 0.27357 | 0.25147 | 0.022097 | 2.9349e-06 | 0
[13 empty] | 2:13 | 1.0572 | 0.91146 | 0 |  | 2:13 | 0 | 0 | 0 | 2:13 | 0.27421 | 0.25206 | 0.022149 | 2.9418e-06 | 0
[13 empty] | 2:13 | 1.0433 | 0.91146 | 0 |  | 2:13 | 0 | 0 | 0 | 2:13 | 0.27484 | 0.25264 | 0.0222 | 2.9486e-06 | 0
[13 empty] | 2:14 | 1.0297 | 0.91146 | 0 |  | 2:14 | 0 | 0 | 0 | 2:14 | 0.27546 | 0.25321 | 0.02225 | 2.9553e-06 | 0
[13 empty] | 2:14 | 1.0164 | 0.91146 | 0 |  | 2:14 | 0 | 0 | 0 | 2:14 | 0.27608 | 0.25378 | 0.0223 | 2.9618e-06 | 0
[13 empty] | 2:14 | 1.0034 | 0.91146 | 0 |  | 2:14 | 0 | 0 | 0 | 2:14 | 0.27669 | 0.25434 | 0.022349 | 2.9683e-06 | 0
[13 empty] | 2:14 | 0.99061 | 0.91146 | 0 |  | 2:14 | 0 | 0 | 0 | 2:14 | 0.27729 | 0.25489 | 0.022397 | 2.9748e-06 | 0
[13 empty] | 2:14 | 0.9781 | 0.91146 | 0 |  | 2:14 | 0 | 0 | 0 | 2:14 | 0.27787 | 0.25542 | 0.022445 | 2.9811e-06 | 0
[13 empty] | 2:15 | 0.96584 | 0.91146 | 0 |  | 2:15 | 0 | 0 | 0 | 2:15 | 0.27845 | 0.25596 | 0.022492 | 2.9874e-06 | 0
[13 empty] | 2:15 | 0.95384 | 0.91146 | 0 |  | 2:15 | 0 | 0 | 0 | 2:15 | 0.27904 | 0.25649 | 0.022538 | 2.9937e-06 | 0
[13 empty] | 2:15 | 0.94208 | 0.91146 | 0 |  | 2:15 | 0 | 0 | 0 | 2:15 | 0.27962 | 0.25703 | 0.022584 | 2.9998e-06 | 0
[13 empty] | 2:16 | 0.93057 | 0.91146 | 0 |  | 2:16 | 0 | 0 | 0 | 2:16 | 0.28018 | 0.25754 | 0.02263 | 3.0057e-06 | 0
[13 empty] | 2:16 | 0.91929 | 0.91146 | 0 |  | 2:16 | 0 | 0 | 0 | 2:16 | 0.28074 | 0.25806 | 0.022676 | 3.0118e-06 | 0
[13 empty] | 2:16 | 0.90824 | 0.91146 | 0 |  | 2:16 | 0 | 0 | 0 | 2:16 | 0.28128 | 0.25856 | 0.02272 | 3.0176e-06 | 0
[13 empty] | 2:16 | 0.89742 | 0.91146 | 0 |  | 2:16 | 0 | 0 | 0 | 2:16 | 0.28182 | 0.25905 | 0.022764 | 3.0235e-06 | 0
[13 empty] | 2:16 | 0.88682 | 0.91146 | 0 |  | 2:16 | 0 | 0 | 0 | 2:16 | 0.28236 | 0.25955 | 0.022808 | 3.0292e-06 | 0
[13 empty] | 2:17 | 0.87644 | 0.91146 | 0 |  | 2:17 | 0 | 0 | 0 | 2:17 | 0.2829 | 0.26005 | 0.02285 | 3.035e-06 | 0
[13 empty] | 2:17 | 0.86628 | 0.91146 | 0 |  | 2:17 | 0 | 0 | 0 | 2:17 | 0.28342 | 0.26052 | 0.022892 | 3.0405e-06 | 0
[13 empty] | 2:17 | 0.85632 | 0.91146 | 0 |  | 2:17 | 0 | 0 | 0 | 2:17 | 0.28394 | 0.261 | 0.022934 | 3.0462e-06 | 0
[13 empty] | 2:18 | 0.84656 | 0.91146 | 0 |  | 2:18 | 0 | 0 | 0 | 2:18 | 0.28444 | 0.26146 | 0.022976 | 3.0516e-06 | 0
[13 empty] | 2:18 | 0.83701 | 0.91146 | 0 |  | 2:18 | 0 | 0 | 0 | 2:18 | 0.28496 | 0.26194 | 0.023016 | 3.0571e-06 | 0
[13 empty] | 2:18 | 0.82765 | 0.91146 | 0 |  | 2:18 | 0 | 0 | 0 | 2:18 | 0.28545 | 0.2624 | 0.023056 | 3.0625e-06 | 0
[13 empty] | 2:18 | 0.81849 | 0.91146 | 0 |  | 2:18 | 0 | 0 | 0 | 2:18 | 0.28595 | 0.26285 | 0.023096 | 3.0678e-06 | 0
[13 empty] | 2:18 | 0.80951 | 0.91146 | 0 |  | 2:18 | 0 | 0 | 0 | 2:18 | 0.28643 | 0.26329 | 0.023136 | 3.073e-06 | 0
[13 empty] | 2:19 | 0.80072 | 0.91146 | 0 |  | 2:19 | 0 | 0 | 0 | 2:19 | 0.28693 | 0.26375 | 0.023176 | 3.0783e-06 | 0
[13 empty] | 2:19 | 0.79211 | 0.91146 | 0 |  | 2:19 | 0 | 0 | 0 | 2:19 | 0.28741 | 0.26419 | 0.023214 | 3.0833e-06 | 0
[13 empty] | 2:19 | 0.78367 | 0.91146 | 0 |  | 2:19 | 0 | 0 | 0 | 2:19 | 0.28789 | 0.26463 | 0.023253 | 3.0884e-06 | 0
[13 empty] | 2:20 | 0.77541 | 0.91146 | 0 |  | 2:20 | 0 | 0 | 0 | 2:20 | 0.28834 | 0.26505 | 0.023291 | 3.0934e-06 | 0
[13 empty] | 2:20 | 0.76732 | 0.91146 | 0 |  | 2:20 | 0 | 0 | 0 | 2:20 | 0.28882 | 0.26549 | 0.023329 | 3.0986e-06 | 0
[13 empty] | 2:20 | 0.75939 | 0.91146 | 0 |  | 2:20 | 0 | 0 | 0 | 2:20 | 0.28928 | 0.26591 | 0.023365 | 3.1033e-06 | 0
[13 empty] | 2:20 | 0.75163 | 0.91146 | 0 |  | 2:20 | 0 | 0 | 0 | 2:20 | 0.28973 | 0.26633 | 0.023402 | 3.1083e-06 | 0
[13 empty] | 2:20 | 0.74403 | 0.91146 | 0 |  | 2:20 | 0 | 0 | 0 | 2:20 | 0.29017 | 0.26673 | 0.023438 | 3.1131e-06 | 0
[13 empty] | 2:21 | 0.73658 | 0.91146 | 0 |  | 2:21 | 0 | 0 | 0 | 2:21 | 0.29063 | 0.26715 | 0.023474 | 3.1178e-06 | 0
[13 empty] | 2:21 | 0.72929 | 0.91146 | 0 |  | 2:21 | 0 | 0 | 0 | 2:21 | 0.29107 | 0.26755 | 0.02351 | 3.1226e-06 | 0
[13 empty] | 2:21 | 1.1629 | 0.91146 | 0 |  | 2:21 | 0 | 0 | 0 | 2:21 | 0.29177 | 0.2682 | 0.023568 | 3.1303e-06 | 0
[13 empty] | 2:22 | 1.1468 | 0.91146 | 0 |  | 2:22 | 0 | 0 | 0 | 2:22 | 0.29246 | 0.26883 | 0.023623 | 3.1377e-06 | 0
[13 empty] | 2:22 | 1.1311 | 0.91146 | 0 |  | 2:22 | 0 | 0 | 0 | 2:22 | 0.29314 | 0.26946 | 0.023678 | 3.145e-06 | 0
[13 empty] | 2:22 | 1.1157 | 0.91146 | 0 |  | 2:22 | 0 | 0 | 0 | 2:22 | 0.29383 | 0.27009 | 0.023732 | 3.1522e-06 | 0
[13 empty] | 2:22 | 1.1006 | 0.91146 | 0 |  | 2:22 | 0 | 0 | 0 | 2:22 | 0.29449 | 0.2707 | 0.023787 | 3.1593e-06 | 0
[13 empty] | 2:22 | 1.0859 | 0.91146 | 0 |  | 2:22 | 0 | 0 | 0 | 2:22 | 0.29514 | 0.2713 | 0.023839 | 3.1664e-06 | 0
[13 empty] | 2:23 | 1.0714 | 0.91146 | 0 |  | 2:23 | 0 | 0 | 0 | 2:23 | 0.2958 | 0.27191 | 0.023892 | 3.1734e-06 | 0
[13 empty] | 2:23 | 1.0572 | 0.91146 | 0 |  | 2:23 | 0 | 0 | 0 | 2:23 | 0.29643 | 0.27248 | 0.023944 | 3.1803e-06 | 0
[13 empty] | 2:23 | 1.0433 | 0.91146 | 0 |  | 2:23 | 0 | 0 | 0 | 2:23 | 0.29707 | 0.27307 | 0.023995 | 3.187e-06 | 0
[13 empty] | 2:24 | 1.0298 | 0.91146 | 0 |  | 2:24 | 0 | 0 | 0 | 2:24 | 0.29769 | 0.27364 | 0.024045 | 3.1937e-06 | 0
[13 empty] | 2:24 | 1.0164 | 0.91146 | 0 |  | 2:24 | 0 | 0 | 0 | 2:24 | 0.29832 | 0.27422 | 0.024095 | 3.2004e-06 | 0
[13 empty] | 2:24 | 1.0034 | 0.91146 | 0 |  | 2:24 | 0 | 0 | 0 | 2:24 | 0.29892 | 0.27477 | 0.024144 | 3.2068e-06 | 0
[13 empty] | 2:24 | 0.99062 | 0.91146 | 0 |  | 2:24 | 0 | 0 | 0 | 2:24 | 0.29952 | 0.27533 | 0.024192 | 3.2133e-06 | 0
[13 empty] | 2:24 | 0.97811 | 0.91146 | 0 |  | 2:24 | 0 | 0 | 0 | 2:24 | 0.3001 | 0.27586 | 0.02424 | 3.2196e-06 | 0
[13 empty] | 2:25 | 0.96585 | 0.91146 | 0 |  | 2:25 | 0 | 0 | 0 | 2:25 | 0.30069 | 0.27639 | 0.024288 | 3.2259e-06 | 0
[13 empty] | 2:25 | 0.95385 | 0.91146 | 0 |  | 2:25 | 0 | 0 | 0 | 2:25 | 0.30127 | 0.27693 | 0.024334 | 3.2321e-06 | 0
[13 empty] | 2:25 | 0.94209 | 0.91146 | 0 |  | 2:25 | 0 | 0 | 0 | 2:25 | 0.30183 | 0.27745 | 0.024379 | 3.2382e-06 | 0
[13 empty] | 2:25 | 0.93057 | 0.91146 | 0 |  | 2:25 | 0 | 0 | 0 | 2:25 | 0.30241 | 0.27798 | 0.024425 | 3.2443e-06 | 0
[13 empty] | 2:26 | 0.91929 | 0.91146 | 0 |  | 2:26 | 0 | 0 | 0 | 2:26 | 0.30295 | 0.27848 | 0.024471 | 3.2502e-06 | 0
[13 empty] | 2:26 | 0.90825 | 0.91146 | 0 |  | 2:26 | 0 | 0 | 0 | 2:26 | 0.30351 | 0.27899 | 0.024515 | 3.2561e-06 | 0
[13 empty] | 2:26 | 0.89743 | 0.91146 | 0 |  | 2:26 | 0 | 0 | 0 | 2:26 | 0.30405 | 0.27949 | 0.024559 | 3.262e-06 | 0
[13 empty] | 2:26 | 0.88683 | 0.91146 | 0 |  | 2:26 | 0 | 0 | 0 | 2:26 | 0.30459 | 0.27999 | 0.024603 | 3.2678e-06 | 0
[13 empty] | 2:27 | 0.87645 | 0.91146 | 0 |  | 2:27 | 0 | 0 | 0 | 2:27 | 0.30511 | 0.28046 | 0.024645 | 3.2735e-06 | 0
[13 empty] | 2:27 | 0.86628 | 0.91146 | 0 |  | 2:27 | 0 | 0 | 0 | 2:27 | 0.30565 | 0.28096 | 0.024687 | 3.279e-06 | 0
[13 empty] | 2:27 | 0.85632 | 0.91146 | 0 |  | 2:27 | 0 | 0 | 0 | 2:27 | 0.30617 | 0.28144 | 0.024729 | 3.2846e-06 | 0
[13 empty] | 2:28 | 0.84657 | 0.91146 | 0 |  | 2:28 | 0 | 0 | 0 | 2:28 | 0.30667 | 0.2819 | 0.024771 | 3.2901e-06 | 0
[13 empty] | 2:28 | 0.83701 | 0.91146 | 0 |  | 2:28 | 0 | 0 | 0 | 2:28 | 0.30719 | 0.28237 | 0.024811 | 3.2955e-06 | 0
[13 empty] | 2:28 | 0.82766 | 0.91146 | 0 |  | 2:28 | 0 | 0 | 0 | 2:28 | 0.30769 | 0.28283 | 0.024853 | 3.301e-06 | 0
[13 empty] | 2:28 | 0.81849 | 0.91146 | 0 |  | 2:28 | 0 | 0 | 0 | 2:28 | 0.30819 | 0.28329 | 0.024893 | 3.3062e-06 | 0
[13 empty] | 2:28 | 0.80951 | 0.91146 | 0 |  | 2:28 | 0 | 0 | 0 | 2:28 | 0.30866 | 0.28373 | 0.024931 | 3.3115e-06 | 0
[13 empty] | 2:29 | 0.80072 | 0.91146 | 0 |  | 2:29 | 0 | 0 | 0 | 2:29 | 0.30916 | 0.28419 | 0.024971 | 3.3167e-06 | 0
[13 empty] | 2:29 | 0.79211 | 0.91146 | 0 |  | 2:29 | 0 | 0 | 0 | 2:29 | 0.30964 | 0.28463 | 0.02501 | 3.3218e-06 | 0
[13 empty] | 2:29 | 0.78368 | 0.91146 | 0 |  | 2:29 | 0 | 0 | 0 | 2:29 | 0.3101 | 0.28505 | 0.025048 | 3.327e-06 | 0
[13 empty] | 2:30 | 0.77541 | 0.91146 | 0 |  | 2:30 | 0 | 0 | 0 | 2:30 | 0.31058 | 0.28549 | 0.025086 | 3.3319e-06 | 0
[13 empty] | 2:30 | 0.76732 | 0.91146 | 0 |  | 2:30 | 0 | 0 | 0 | 2:30 | 0.31103 | 0.28591 | 0.025124 | 3.3369e-06 | 0
[13 empty] | 2:30 | 0.7594 | 0.91146 | 0 |  | 2:30 | 0 | 0 | 0 | 2:30 | 0.31151 | 0.28635 | 0.02516 | 3.3419e-06 | 0
[13 empty] | 2:30 | 0.75163 | 0.91146 | 0 |  | 2:30 | 0 | 0 | 0 | 2:30 | 0.31195 | 0.28675 | 0.025197 | 3.3468e-06 | 0
[13 empty] | 2:30 | 0.74403 | 0.91146 | 0 |  | 2:30 | 0 | 0 | 0 | 2:30 | 0.3124 | 0.28717 | 0.025233 | 3.3516e-06 | 0
[13 empty] | 2:31 | 0.73658 | 0.91146 | 0 |  | 2:31 | 0 | 0 | 0 | 2:31 | 0.31286 | 0.28759 | 0.025269 | 3.3564e-06 | 0
[13 empty] | 2:31 | 0.72929 | 0.91146 | 0 |  | 2:31 | 0 | 0 | 0 | 2:31 | 0.3133 | 0.28799 | 0.025306 | 3.3612e-06 | 0
[13 empty] | 2:31 | 1.1629 | 0.91146 | 0 |  | 2:31 | 0 | 0 | 0 | 2:31 | 0.314 | 0.28864 | 0.025363 | 3.3686e-06 | 0
[13 empty] | 2:32 | 1.1468 | 0.91146 | 0 |  | 2:32 | 0 | 0 | 0 | 2:32 | 0.31469 | 0.28927 | 0.025418 | 3.3761e-06 | 0
[13 empty] | 2:32 | 1.1311 | 0.91146 | 0 |  | 2:32 | 0 | 0 | 0 | 2:32 | 0.31537 | 0.2899 | 0.025474 | 3.3835e-06 | 0
[13 empty] | 2:32 | 1.1157 | 0.91146 | 0 |  | 2:32 | 0 | 0 | 0 | 2:32 | 0.31606 | 0.29053 | 0.025529 | 3.3908e-06 | 0
[13 empty] | 2:32 | 1.1006 | 0.91146 | 0 |  | 2:32 | 0 | 0 | 0 | 2:32 | 0.31672 | 0.29114 | 0.025583 | 3.3978e-06 | 0
[13 empty] | 2:32 | 1.0859 | 0.91146 | 0 |  | 2:32 | 0 | 0 | 0 | 2:32 | 0.31737 | 0.29173 | 0.025634 | 3.4049e-06 | 0
[13 empty] | 2:33 | 1.0714 | 0.91146 | 0 |  | 2:33 | 0 | 0 | 0 | 2:33 | 0.31803 | 0.29234 | 0.025688 | 3.4118e-06 | 0
[13 empty] | 2:33 | 1.0572 | 0.91146 | 0 |  | 2:33 | 0 | 0 | 0 | 2:33 | 0.31866 | 0.29292 | 0.025739 | 3.4186e-06 | 0
[13 empty] | 2:33 | 1.0434 | 0.91146 | 0 |  | 2:33 | 0 | 0 | 0 | 2:33 | 0.3193 | 0.29351 | 0.025791 | 3.4255e-06 | 0
[13 empty] | 2:34 | 1.0298 | 0.91146 | 0 |  | 2:34 | 0 | 0 | 0 | 2:34 | 0.31992 | 0.29408 | 0.02584 | 3.4322e-06 | 0
[13 empty] | 2:34 | 1.0164 | 0.91146 | 0 |  | 2:34 | 0 | 0 | 0 | 2:34 | 0.32053 | 0.29463 | 0.02589 | 3.4387e-06 | 0
[13 empty] | 2:34 | 1.0034 | 0.91146 | 0 |  | 2:34 | 0 | 0 | 0 | 2:34 | 0.32115 | 0.29521 | 0.02594 | 3.4454e-06 | 0
[13 empty] | 2:34 | 0.99062 | 0.91146 | 0 |  | 2:34 | 0 | 0 | 0 | 2:34 | 0.32173 | 0.29574 | 0.025987 | 3.4517e-06 | 0
[13 empty] | 2:34 | 0.97811 | 0.91146 | 0 |  | 2:34 | 0 | 0 | 0 | 2:34 | 0.32233 | 0.2963 | 0.026035 | 3.4582e-06 | 0
[13 empty] | 2:35 | 0.96585 | 0.91146 | 0 |  | 2:35 | 0 | 0 | 0 | 2:35 | 0.32292 | 0.29683 | 0.026083 | 3.4643e-06 | 0
[13 empty] | 2:35 | 0.95385 | 0.91146 | 0 |  | 2:35 | 0 | 0 | 0 | 2:35 | 0.3235 | 0.29737 | 0.026129 | 3.4706e-06 | 0
[13 empty] | 2:35 | 0.94209 | 0.91146 | 0 |  | 2:35 | 0 | 0 | 0 | 2:35 | 0.32406 | 0.29788 | 0.026175 | 3.4767e-06 | 0
[13 empty] | 2:36 | 0.93058 | 0.91146 | 0 |  | 2:36 | 0 | 0 | 0 | 2:36 | 0.32462 | 0.2984 | 0.02622 | 3.4828e-06 | 0
[13 empty] | 2:36 | 0.9193 | 0.91146 | 0 |  | 2:36 | 0 | 0 | 0 | 2:36 | 0.32518 | 0.29891 | 0.026266 | 3.4887e-06 | 0
[13 empty] | 2:36 | 0.90825 | 0.91146 | 0 |  | 2:36 | 0 | 0 | 0 | 2:36 | 0.32574 | 0.29943 | 0.02631 | 3.4947e-06 | 0
[13 empty] | 2:36 | 0.89743 | 0.91146 | 0 |  | 2:36 | 0 | 0 | 0 | 2:36 | 0.32628 | 0.29992 | 0.026354 | 3.5004e-06 | 0
[13 empty] | 2:36 | 0.88683 | 0.91146 | 0 |  | 2:36 | 0 | 0 | 0 | 2:36 | 0.32682 | 0.30042 | 0.026398 | 3.5061e-06 | 0
[13 empty] | 2:37 | 0.87645 | 0.91146 | 0 |  | 2:37 | 0 | 0 | 0 | 2:37 | 0.32734 | 0.3009 | 0.02644 | 3.5118e-06 | 0
[13 empty] | 2:37 | 0.86628 | 0.91146 | 0 |  | 2:37 | 0 | 0 | 0 | 2:37 | 0.32786 | 0.30138 | 0.026482 | 3.5176e-06 | 0
[13 empty] | 2:37 | 0.85632 | 0.91146 | 0 |  | 2:37 | 0 | 0 | 0 | 2:37 | 0.32838 | 0.30185 | 0.026524 | 3.5231e-06 | 0
[13 empty] | 2:38 | 0.84657 | 0.91146 | 0 |  | 2:38 | 0 | 0 | 0 | 2:38 | 0.3289 | 0.30233 | 0.026566 | 3.5287e-06 | 0
[13 empty] | 2:38 | 0.83702 | 0.91146 | 0 |  | 2:38 | 0 | 0 | 0 | 2:38 | 0.3294 | 0.30279 | 0.026606 | 3.534e-06 | 0
[13 empty] | 2:38 | 0.82766 | 0.91146 | 0 |  | 2:38 | 0 | 0 | 0 | 2:38 | 0.32992 | 0.30327 | 0.026648 | 3.5394e-06 | 0
[13 empty] | 2:38 | 0.8185 | 0.91146 | 0 |  | 2:38 | 0 | 0 | 0 | 2:38 | 0.3304 | 0.30371 | 0.026688 | 3.5447e-06 | 0
[13 empty] | 2:38 | 0.80952 | 0.91146 | 0 |  | 2:38 | 0 | 0 | 0 | 2:38 | 0.33089 | 0.30416 | 0.026727 | 3.55e-06 | 0
[13 empty] | 2:39 | 0.80073 | 0.91146 | 0 |  | 2:39 | 0 | 0 | 0 | 2:39 | 0.33137 | 0.3046 | 0.026767 | 3.5552e-06 | 0
[13 empty] | 2:39 | 0.79211 | 0.91146 | 0 |  | 2:39 | 0 | 0 | 0 | 2:39 | 0.33185 | 0.30504 | 0.026805 | 3.5604e-06 | 0
[13 empty] | 2:39 | 0.78368 | 0.91146 | 0 |  | 2:39 | 0 | 0 | 0 | 2:39 | 0.33233 | 0.30548 | 0.026843 | 3.5653e-06 | 0
[13 empty] | 2:40 | 0.77542 | 0.91146 | 0 |  | 2:40 | 0 | 0 | 0 | 2:40 | 0.33281 | 0.30592 | 0.026881 | 3.5705e-06 | 0
[13 empty] | 2:40 | 0.76732 | 0.91146 | 0 |  | 2:40 | 0 | 0 | 0 | 2:40 | 0.33326 | 0.30634 | 0.026919 | 3.5754e-06 | 0
[13 empty] | 2:40 | 0.7594 | 0.91146 | 0 |  | 2:40 | 0 | 0 | 0 | 2:40 | 0.33372 | 0.30676 | 0.026956 | 3.5804e-06 | 0
[13 empty] | 2:40 | 0.75163 | 0.91146 | 0 |  | 2:40 | 0 | 0 | 0 | 2:40 | 0.33418 | 0.30718 | 0.026992 | 3.5852e-06 | 0
[13 empty] | 2:40 | 0.74403 | 0.91146 | 0 |  | 2:40 | 0 | 0 | 0 | 2:40 | 0.33463 | 0.3076 | 0.027028 | 3.5902e-06 | 0
[13 empty] | 2:41 | 0.73658 | 0.91146 | 0 |  | 2:41 | 0 | 0 | 0 | 2:41 | 0.33507 | 0.308 | 0.027065 | 3.5949e-06 | 0
[13 empty] | 2:41 | 0.72929 | 0.91146 | 0 |  | 2:41 | 0 | 0 | 0 | 2:41 | 0.33553 | 0.30842 | 0.027101 | 3.5995e-06 | 0
[13 empty] | 2:41 | 1.1629 | 0.91146 | 0 |  | 2:41 | 0 | 0 | 0 | 2:41 | 0.33623 | 0.30907 | 0.027158 | 3.6072e-06 | 0
[13 empty] | 2:42 | 1.1468 | 0.91146 | 0 |  | 2:42 | 0 | 0 | 0 | 2:42 | 0.33692 | 0.3097 | 0.027214 | 3.6146e-06 | 0
[13 empty] | 2:42 | 1.1311 | 0.91146 | 0 |  | 2:42 | 0 | 0 | 0 | 2:42 | 0.33761 | 0.31033 | 0.027269 | 3.6219e-06 | 0
[13 empty] | 2:42 | 1.1157 | 0.91146 | 0 |  | 2:42 | 0 | 0 | 0 | 2:42 | 0.33827 | 0.31094 | 0.027324 | 3.6291e-06 | 0
[13 empty] | 2:42 | 1.1006 | 0.91146 | 0 |  | 2:42 | 0 | 0 | 0 | 2:42 | 0.33894 | 0.31156 | 0.027378 | 3.6364e-06 | 0
[13 empty] | 2:42 | 1.0859 | 0.91146 | 0 |  | 2:42 | 0 | 0 | 0 | 2:42 | 0.3396 | 0.31217 | 0.027431 | 3.6434e-06 | 0
[13 empty] | 2:43 | 1.0714 | 0.91146 | 0 |  | 2:43 | 0 | 0 | 0 | 2:43 | 0.34025 | 0.31276 | 0.027483 | 3.6503e-06 | 0
[13 empty] | 2:43 | 1.0572 | 0.91146 | 0 |  | 2:43 | 0 | 0 | 0 | 2:43 | 0.34089 | 0.31335 | 0.027534 | 3.6572e-06 | 0
[13 empty] | 2:43 | 1.0434 | 0.91146 | 0 |  | 2:43 | 0 | 0 | 0 | 2:43 | 0.34153 | 0.31394 | 0.027586 | 3.6641e-06 | 0
[13 empty] | 2:44 | 1.0298 | 0.91146 | 0 |  | 2:44 | 0 | 0 | 0 | 2:44 | 0.34215 | 0.31452 | 0.027636 | 3.6707e-06 | 0
[13 empty] | 2:44 | 1.0164 | 0.91146 | 0 |  | 2:44 | 0 | 0 | 0 | 2:44 | 0.34276 | 0.31507 | 0.027685 | 3.6772e-06 | 0
[13 empty] | 2:44 | 1.0034 | 0.91146 | 0 |  | 2:44 | 0 | 0 | 0 | 2:44 | 0.34336 | 0.31562 | 0.027735 | 3.6837e-06 | 0
[13 empty] | 2:44 | 0.99062 | 0.91146 | 0 |  | 2:44 | 0 | 0 | 0 | 2:44 | 0.34396 | 0.31618 | 0.027783 | 3.6902e-06 | 0
[13 empty] | 2:44 | 0.97811 | 0.91146 | 0 |  | 2:44 | 0 | 0 | 0 | 2:44 | 0.34457 | 0.31673 | 0.02783 | 3.6965e-06 | 0
[13 empty] | 2:45 | 0.96585 | 0.91146 | 0 |  | 2:45 | 0 | 0 | 0 | 2:45 | 0.34515 | 0.31727 | 0.027878 | 3.7028e-06 | 0
[13 empty] | 2:45 | 0.95385 | 0.91146 | 0 |  | 2:45 | 0 | 0 | 0 | 2:45 | 0.34573 | 0.3178 | 0.027924 | 3.7089e-06 | 0
[13 empty] | 2:45 | 0.94209 | 0.91146 | 0 |  | 2:45 | 0 | 0 | 0 | 2:45 | 0.34629 | 0.31832 | 0.027972 | 3.7152e-06 | 0
[13 empty] | 2:46 | 0.93058 | 0.91146 | 0 |  | 2:46 | 0 | 0 | 0 | 2:46 | 0.34685 | 0.31883 | 0.028016 | 3.7212e-06 | 0
[13 empty] | 2:46 | 0.9193 | 0.91146 | 0 |  | 2:46 | 0 | 0 | 0 | 2:46 | 0.34741 | 0.31935 | 0.028062 | 3.7271e-06 | 0
[13 empty] | 2:46 | 0.90825 | 0.91146 | 0 |  | 2:46 | 0 | 0 | 0 | 2:46 | 0.34797 | 0.31986 | 0.028105 | 3.733e-06 | 0
[13 empty] | 2:46 | 0.89743 | 0.91146 | 0 |  | 2:46 | 0 | 0 | 0 | 2:46 | 0.34851 | 0.32036 | 0.028149 | 3.7389e-06 | 0
[13 empty] | 2:46 | 0.88683 | 0.91146 | 0 |  | 2:46 | 0 | 0 | 0 | 2:46 | 0.34905 | 0.32086 | 0.028193 | 3.7447e-06 | 0
[13 empty] | 2:47 | 0.87645 | 0.91146 | 0 |  | 2:47 | 0 | 0 | 0 | 2:47 | 0.34957 | 0.32133 | 0.028235 | 3.7504e-06 | 0
[13 empty] | 2:47 | 0.86628 | 0.91146 | 0 |  | 2:47 | 0 | 0 | 0 | 2:47 | 0.35009 | 0.32181 | 0.028277 | 3.7559e-06 | 0
[13 empty] | 2:47 | 0.85633 | 0.91146 | 0 |  | 2:47 | 0 | 0 | 0 | 2:47 | 0.35061 | 0.32229 | 0.028319 | 3.7615e-06 | 0
[13 empty] | 2:47 | 0.84657 | 0.91146 | 0 |  | 2:47 | 0 | 0 | 0 | 2:47 | 0.35113 | 0.32277 | 0.028361 | 3.767e-06 | 0
[13 empty] | 2:48 | 0.83702 | 0.91146 | 0 |  | 2:48 | 0 | 0 | 0 | 2:48 | 0.35163 | 0.32322 | 0.028403 | 3.7725e-06 | 0
[13 empty] | 2:48 | 0.82766 | 0.91146 | 0 |  | 2:48 | 0 | 0 | 0 | 2:48 | 0.35213 | 0.32368 | 0.028444 | 3.7779e-06 | 0
[13 empty] | 2:48 | 0.8185 | 0.91146 | 0 |  | 2:48 | 0 | 0 | 0 | 2:48 | 0.35263 | 0.32414 | 0.028484 | 3.7832e-06 | 0
[13 empty] | 2:49 | 0.80952 | 0.91146 | 0 |  | 2:49 | 0 | 0 | 0 | 2:49 | 0.35313 | 0.3246 | 0.028522 | 3.7884e-06 | 0
[13 empty] | 2:49 | 0.80073 | 0.91146 | 0 |  | 2:49 | 0 | 0 | 0 | 2:49 | 0.3536 | 0.32504 | 0.028562 | 3.7936e-06 | 0
[13 empty] | 2:49 | 0.79211 | 0.91146 | 0 |  | 2:49 | 0 | 0 | 0 | 2:49 | 0.35408 | 0.32548 | 0.0286 | 3.7987e-06 | 0
[13 empty] | 2:49 | 0.78368 | 0.91146 | 0 |  | 2:49 | 0 | 0 | 0 | 2:49 | 0.35456 | 0.32592 | 0.028638 | 3.8039e-06 | 0
[13 empty] | 2:50 | 0.77542 | 0.91146 | 0 |  | 2:50 | 0 | 0 | 0 | 2:50 | 0.35504 | 0.32636 | 0.028677 | 3.8088e-06 | 0
[13 empty] | 2:50 | 0.76733 | 0.91146 | 0 |  | 2:50 | 0 | 0 | 0 | 2:50 | 0.3555 | 0.32678 | 0.028715 | 3.8138e-06 | 0
[13 empty] | 2:50 | 0.7594 | 0.91146 | 0 |  | 2:50 | 0 | 0 | 0 | 2:50 | 0.35595 | 0.3272 | 0.028751 | 3.8188e-06 | 0
[13 empty] | 2:50 | 0.75164 | 0.91146 | 0 |  | 2:50 | 0 | 0 | 0 | 2:50 | 0.35641 | 0.32762 | 0.028787 | 3.8237e-06 | 0
[13 empty] | 2:50 | 0.74403 | 0.91146 | 0 |  | 2:50 | 0 | 0 | 0 | 2:50 | 0.35686 | 0.32804 | 0.028824 | 3.8285e-06 | 0
[13 empty] | 2:51 | 0.73658 | 0.91146 | 0 |  | 2:51 | 0 | 0 | 0 | 2:51 | 0.3573 | 0.32844 | 0.02886 | 3.8333e-06 | 0
[13 empty] | 2:51 | 0.72929 | 0.91146 | 0 |  | 2:51 | 0 | 0 | 0 | 2:51 | 0.35774 | 0.32884 | 0.028896 | 3.8381e-06 | 0
[13 empty] | 2:51 | 1.1629 | 0.91146 | 0 |  | 2:51 | 0 | 0 | 0 | 2:51 | 0.35845 | 0.32949 | 0.028953 | 3.8457e-06 | 0
[13 empty] | 2:52 | 1.1468 | 0.91146 | 0 |  | 2:52 | 0 | 0 | 0 | 2:52 | 0.35915 | 0.33014 | 0.029009 | 3.8531e-06 | 0
[13 empty] | 2:52 | 1.1311 | 0.91146 | 0 |  | 2:52 | 0 | 0 | 0 | 2:52 | 0.35984 | 0.33077 | 0.029064 | 3.8604e-06 | 0
[13 empty] | 2:52 | 1.1157 | 0.91146 | 0 |  | 2:52 | 0 | 0 | 0 | 2:52 | 0.3605 | 0.33138 | 0.02912 | 3.8677e-06 | 0
[13 empty] | 2:52 | 1.1006 | 0.91146 | 0 |  | 2:52 | 0 | 0 | 0 | 2:52 | 0.36117 | 0.33199 | 0.029173 | 3.8747e-06 | 0
[13 empty] | 2:52 | 1.0859 | 0.91146 | 0 |  | 2:52 | 0 | 0 | 0 | 2:52 | 0.36183 | 0.3326 | 0.029227 | 3.8818e-06 | 0
[13 empty] | 2:53 | 1.0714 | 0.91146 | 0 |  | 2:53 | 0 | 0 | 0 | 2:53 | 0.36248 | 0.33319 | 0.029278 | 3.8889e-06 | 0
[13 empty] | 2:53 | 1.0572 | 0.91146 | 0 |  | 2:53 | 0 | 0 | 0 | 2:53 | 0.36312 | 0.33379 | 0.02933 | 3.8957e-06 | 0
[13 empty] | 2:53 | 1.0434 | 0.91146 | 0 |  | 2:53 | 0 | 0 | 0 | 2:53 | 0.36374 | 0.33436 | 0.029381 | 3.9024e-06 | 0
[13 empty] | 2:54 | 1.0298 | 0.91146 | 0 |  | 2:54 | 0 | 0 | 0 | 2:54 | 0.36437 | 0.33493 | 0.029431 | 3.9091e-06 | 0
[13 empty] | 2:54 | 1.0164 | 0.91146 | 0 |  | 2:54 | 0 | 0 | 0 | 2:54 | 0.36499 | 0.3355 | 0.029481 | 3.9158e-06 | 0
[13 empty] | 2:54 | 1.0034 | 0.91146 | 0 |  | 2:54 | 0 | 0 | 0 | 2:54 | 0.36559 | 0.33606 | 0.02953 | 3.9223e-06 | 0
[13 empty] | 2:54 | 0.99062 | 0.91146 | 0 |  | 2:54 | 0 | 0 | 0 | 2:54 | 0.36619 | 0.33661 | 0.029578 | 3.9288e-06 | 0
[13 empty] | 2:54 | 0.97811 | 0.91146 | 0 |  | 2:54 | 0 | 0 | 0 | 2:54 | 0.3668 | 0.33717 | 0.029626 | 3.9351e-06 | 0
[13 empty] | 2:55 | 0.96585 | 0.91146 | 0 |  | 2:55 | 0 | 0 | 0 | 2:55 | 0.36738 | 0.3377 | 0.029673 | 3.9414e-06 | 0
[13 empty] | 2:55 | 0.95385 | 0.91146 | 0 |  | 2:55 | 0 | 0 | 0 | 2:55 | 0.36796 | 0.33824 | 0.029721 | 3.9475e-06 | 0
[13 empty] | 2:55 | 0.94209 | 0.91146 | 0 |  | 2:55 | 0 | 0 | 0 | 2:55 | 0.36852 | 0.33875 | 0.029767 | 3.9536e-06 | 0
[13 empty] | 2:56 | 0.93058 | 0.91146 | 0 |  | 2:56 | 0 | 0 | 0 | 2:56 | 0.36908 | 0.33927 | 0.029811 | 3.9597e-06 | 0
[13 empty] | 2:56 | 0.9193 | 0.91146 | 0 |  | 2:56 | 0 | 0 | 0 | 2:56 | 0.36964 | 0.33978 | 0.029857 | 3.9656e-06 | 0
[13 empty] | 2:56 | 0.90825 | 0.91146 | 0 |  | 2:56 | 0 | 0 | 0 | 2:56 | 0.37018 | 0.34028 | 0.029901 | 3.9716e-06 | 0
[13 empty] | 2:56 | 0.89743 | 0.91146 | 0 |  | 2:56 | 0 | 0 | 0 | 2:56 | 0.37074 | 0.3408 | 0.029945 | 3.9773e-06 | 0
[13 empty] | 2:56 | 0.88683 | 0.91146 | 0 |  | 2:56 | 0 | 0 | 0 | 2:56 | 0.37127 | 0.34127 | 0.029989 | 3.9832e-06 | 0
[13 empty] | 2:57 | 0.87645 | 0.91146 | 0 |  | 2:57 | 0 | 0 | 0 | 2:57 | 0.3718 | 0.34177 | 0.030031 | 3.9887e-06 | 0
[13 empty] | 2:57 | 0.86628 | 0.91146 | 0 |  | 2:57 | 0 | 0 | 0 | 2:57 | 0.37233 | 0.34225 | 0.030075 | 3.9945e-06 | 0
[13 empty] | 2:57 | 0.85633 | 0.91146 | 0 |  | 2:57 | 0 | 0 | 0 | 2:57 | 0.37284 | 0.34272 | 0.030115 | 4e-06 | 0
[13 empty] | 2:58 | 0.84657 | 0.91146 | 0 |  | 2:58 | 0 | 0 | 0 | 2:58 | 0.37336 | 0.3432 | 0.030157 | 4.0055e-06 | 0
[13 empty] | 2:58 | 0.83702 | 0.91146 | 0 |  | 2:58 | 0 | 0 | 0 | 2:58 | 0.37386 | 0.34366 | 0.030199 | 4.0109e-06 | 0
[13 empty] | 2:58 | 0.82766 | 0.91146 | 0 |  | 2:58 | 0 | 0 | 0 | 2:58 | 0.37436 | 0.34412 | 0.030239 | 4.0162e-06 | 0
[13 empty] | 2:58 | 0.8185 | 0.91146 | 0 |  | 2:58 | 0 | 0 | 0 | 2:58 | 0.37486 | 0.34458 | 0.030279 | 4.0216e-06 | 0
[13 empty] | 2:58 | 0.80952 | 0.91146 | 0 |  | 2:58 | 0 | 0 | 0 | 2:58 | 0.37536 | 0.34504 | 0.030317 | 4.0269e-06 | 0
[13 empty] | 2:59 | 0.80073 | 0.91146 | 0 |  | 2:59 | 0 | 0 | 0 | 2:59 | 0.37584 | 0.34547 | 0.030357 | 4.0321e-06 | 0
[13 empty] | 2:59 | 0.79211 | 0.91146 | 0 |  | 2:59 | 0 | 0 | 0 | 2:59 | 0.37631 | 0.34591 | 0.030395 | 4.0373e-06 | 0
[13 empty] | 2:59 | 0.78368 | 0.91146 | 0 |  | 2:59 | 0 | 0 | 0 | 2:59 | 0.37679 | 0.34635 | 0.030434 | 4.0424e-06 | 0
[13 empty] | 3:00 | 0.77542 | 0.91146 | 0 |  | 3:00 | 0 | 0 | 0 | 3:00 | 0.37727 | 0.34679 | 0.030472 | 4.0474e-06 | 0
[13 empty] | 3:00 | 0.76733 | 0.91146 | 0 |  | 3:00 | 0 | 0 | 0 | 3:00 | 0.37773 | 0.34721 | 0.03051 | 4.0523e-06 | 0
[13 empty] | 3:00 | 0.7594 | 0.91146 | 0 |  | 3:00 | 0 | 0 | 0 | 3:00 | 0.37818 | 0.34763 | 0.030546 | 4.0573e-06 | 0
[13 empty] | 3:00 | 0.75164 | 0.91146 | 0 |  | 3:00 | 0 | 0 | 0 | 3:00 | 0.37864 | 0.34805 | 0.030583 | 4.0621e-06 | 0
[13 empty] | 3:00 | 0.74403 | 0.91146 | 0 |  | 3:00 | 0 | 0 | 0 | 3:00 | 0.3791 | 0.34847 | 0.030621 | 4.067e-06 | 0
[13 empty] | 3:01 | 0.73658 | 0.91146 | 0 |  | 3:01 | 0 | 0 | 0 | 3:01 | 0.37953 | 0.34887 | 0.030655 | 4.0718e-06 | 0
[13 empty] | 3:01 | 0.72929 | 0.91146 | 0 |  | 3:01 | 0 | 0 | 0 | 3:01 | 0.37997 | 0.34928 | 0.030691 | 4.0766e-06 | 0
[13 empty] | 3:01 | 1.1629 | 0.91146 | 0 |  | 3:01 | 0 | 0 | 0 | 3:01 | 0.38068 | 0.34992 | 0.030749 | 4.084e-06 | 0
[13 empty] | 3:02 | 1.1468 | 0.91146 | 0 |  | 3:02 | 0 | 0 | 0 | 3:02 | 0.38138 | 0.35057 | 0.030804 | 4.0915e-06 | 0
[13 empty] | 3:02 | 1.1311 | 0.91146 | 0 |  | 3:02 | 0 | 0 | 0 | 3:02 | 0.38207 | 0.3512 | 0.03086 | 4.0989e-06 | 0
[13 empty] | 3:02 | 1.1157 | 0.91146 | 0 |  | 3:02 | 0 | 0 | 0 | 3:02 | 0.38273 | 0.35182 | 0.030915 | 4.1062e-06 | 0
[13 empty] | 3:02 | 1.1006 | 0.91146 | 0 |  | 3:02 | 0 | 0 | 0 | 3:02 | 0.3834 | 0.35243 | 0.030968 | 4.1133e-06 | 0
[13 empty] | 3:02 | 1.0859 | 0.91146 | 0 |  | 3:02 | 0 | 0 | 0 | 3:02 | 0.38406 | 0.35304 | 0.031022 | 4.1203e-06 | 0
[13 empty] | 3:03 | 1.0714 | 0.91146 | 0 |  | 3:03 | 0 | 0 | 0 | 3:03 | 0.38471 | 0.35363 | 0.031073 | 4.1272e-06 | 0
[13 empty] | 3:03 | 1.0572 | 0.91146 | 0 |  | 3:03 | 0 | 0 | 0 | 3:03 | 0.38535 | 0.35422 | 0.031125 | 4.1341e-06 | 0
[13 empty] | 3:03 | 1.0434 | 0.91146 | 0 |  | 3:03 | 0 | 0 | 0 | 3:03 | 0.38598 | 0.35479 | 0.031177 | 4.141e-06 | 0
[13 empty] | 3:04 | 1.0298 | 0.91146 | 0 |  | 3:04 | 0 | 0 | 0 | 3:04 | 0.3866 | 0.35537 | 0.031226 | 4.1476e-06 | 0
[13 empty] | 3:04 | 1.0164 | 0.91146 | 0 |  | 3:04 | 0 | 0 | 0 | 3:04 | 0.38722 | 0.35594 | 0.031276 | 4.1541e-06 | 0
[13 empty] | 3:04 | 1.0034 | 0.91146 | 0 |  | 3:04 | 0 | 0 | 0 | 3:04 | 0.38782 | 0.35649 | 0.031326 | 4.1608e-06 | 0
[13 empty] | 3:04 | 0.99062 | 0.91146 | 0 |  | 3:04 | 0 | 0 | 0 | 3:04 | 0.38843 | 0.35705 | 0.031373 | 4.1671e-06 | 0
[13 empty] | 3:05 | 0.97811 | 0.91146 | 0 |  | 3:05 | 0 | 0 | 0 | 3:05 | 0.38901 | 0.35758 | 0.031421 | 4.1734e-06 | 0
[13 empty] | 3:05 | 0.96585 | 0.91146 | 0 |  | 3:05 | 0 | 0 | 0 | 3:05 | 0.38961 | 0.35814 | 0.031469 | 4.1797e-06 | 0
[13 empty] | 3:05 | 0.95385 | 0.91146 | 0 |  | 3:05 | 0 | 0 | 0 | 3:05 | 0.39017 | 0.35865 | 0.031516 | 4.186e-06 | 0
[13 empty] | 3:05 | 0.94209 | 0.91146 | 0 |  | 3:05 | 0 | 0 | 0 | 3:05 | 0.39075 | 0.35919 | 0.031562 | 4.1921e-06 | 0
[13 empty] | 3:06 | 0.93058 | 0.91146 | 0 |  | 3:06 | 0 | 0 | 0 | 3:06 | 0.39132 | 0.3597 | 0.031608 | 4.1981e-06 | 0
[13 empty] | 3:06 | 0.9193 | 0.91146 | 0 |  | 3:06 | 0 | 0 | 0 | 3:06 | 0.39187 | 0.36022 | 0.031652 | 4.2042e-06 | 0
[13 empty] | 3:06 | 0.90825 | 0.91146 | 0 |  | 3:06 | 0 | 0 | 0 | 3:06 | 0.39242 | 0.36072 | 0.031696 | 4.2101e-06 | 0
[13 empty] | 3:06 | 0.89743 | 0.91146 | 0 |  | 3:06 | 0 | 0 | 0 | 3:06 | 0.39296 | 0.36121 | 0.03174 | 4.2158e-06 | 0
[13 empty] | 3:07 | 0.88683 | 0.91146 | 0 |  | 3:07 | 0 | 0 | 0 | 3:07 | 0.3935 | 0.36171 | 0.031784 | 4.2216e-06 | 0
[13 empty] | 3:07 | 0.87645 | 0.91146 | 0 |  | 3:07 | 0 | 0 | 0 | 3:07 | 0.39403 | 0.3622 | 0.031826 | 4.2273e-06 | 0
[13 empty] | 3:07 | 0.86628 | 0.91146 | 0 |  | 3:07 | 0 | 0 | 0 | 3:07 | 0.39456 | 0.36268 | 0.03187 | 4.233e-06 | 0
[13 empty] | 3:07 | 0.85633 | 0.91146 | 0 |  | 3:07 | 0 | 0 | 0 | 3:07 | 0.39508 | 0.36316 | 0.031912 | 4.2386e-06 | 0
[13 empty] | 3:08 | 0.84657 | 0.91146 | 0 |  | 3:08 | 0 | 0 | 0 | 3:08 | 0.39559 | 0.36364 | 0.031952 | 4.2439e-06 | 0
[13 empty] | 3:08 | 0.83702 | 0.91146 | 0 |  | 3:08 | 0 | 0 | 0 | 3:08 | 0.39609 | 0.3641 | 0.031994 | 4.2494e-06 | 0
[13 empty] | 3:08 | 0.82766 | 0.91146 | 0 |  | 3:08 | 0 | 0 | 0 | 3:08 | 0.39659 | 0.36455 | 0.032034 | 4.2548e-06 | 0
[13 empty] | 3:08 | 0.8185 | 0.91146 | 0 |  | 3:08 | 0 | 0 | 0 | 3:08 | 0.39709 | 0.36501 | 0.032074 | 4.2601e-06 | 0
[13 empty] | 3:08 | 0.80952 | 0.91146 | 0 |  | 3:08 | 0 | 0 | 0 | 3:08 | 0.39759 | 0.36547 | 0.032114 | 4.2653e-06 | 0
[13 empty] | 3:09 | 0.80073 | 0.91146 | 0 |  | 3:09 | 0 | 0 | 0 | 3:09 | 0.39807 | 0.36591 | 0.032152 | 4.2706e-06 | 0
[13 empty] | 3:09 | 0.79211 | 0.91146 | 0 |  | 3:09 | 0 | 0 | 0 | 3:09 | 0.39854 | 0.36635 | 0.032191 | 4.2758e-06 | 0
[13 empty] | 3:09 | 0.78368 | 0.91146 | 0 |  | 3:09 | 0 | 0 | 0 | 3:09 | 0.39902 | 0.36679 | 0.032229 | 4.2808e-06 | 0
[13 empty] | 3:10 | 0.77542 | 0.91146 | 0 |  | 3:10 | 0 | 0 | 0 | 3:10 | 0.39948 | 0.36721 | 0.032267 | 4.2859e-06 | 0
[13 empty] | 3:10 | 0.76733 | 0.91146 | 0 |  | 3:10 | 0 | 0 | 0 | 3:10 | 0.39996 | 0.36765 | 0.032305 | 4.2909e-06 | 0
[13 empty] | 3:10 | 0.7594 | 0.91146 | 0 |  | 3:10 | 0 | 0 | 0 | 3:10 | 0.40041 | 0.36807 | 0.032342 | 4.2958e-06 | 0
[13 empty] | 3:10 | 0.75164 | 0.91146 | 0 |  | 3:10 | 0 | 0 | 0 | 3:10 | 0.40087 | 0.36849 | 0.03238 | 4.3006e-06 | 0
[13 empty] | 3:10 | 0.74403 | 0.91146 | 0 |  | 3:10 | 0 | 0 | 0 | 3:10 | 0.40131 | 0.36889 | 0.032416 | 4.3054e-06 | 0
[13 empty] | 3:11 | 0.73658 | 0.91146 | 0 |  | 3:11 | 0 | 0 | 0 | 3:11 | 0.40176 | 0.36931 | 0.03245 | 4.3102e-06 | 0
[13 empty] | 3:11 | 0.72929 | 0.91146 | 0 |  | 3:11 | 0 | 0 | 0 | 3:11 | 0.4022 | 0.36971 | 0.032487 | 4.3149e-06 | 0
[13 empty] | 3:11 | 1.1629 | 0.91146 | 0 |  | 3:11 | 0 | 0 | 0 | 3:11 | 0.40291 | 0.37036 | 0.032544 | 4.3226e-06 | 0
[13 empty] | 3:12 | 1.1468 | 0.91146 | 0 |  | 3:12 | 0 | 0 | 0 | 3:12 | 0.40359 | 0.37099 | 0.032599 | 4.33e-06 | 0
[13 empty] | 3:12 | 1.1311 | 0.91146 | 0 |  | 3:12 | 0 | 0 | 0 | 3:12 | 0.40428 | 0.37162 | 0.032655 | 4.3373e-06 | 0
[13 empty] | 3:12 | 1.1157 | 0.91146 | 0 |  | 3:12 | 0 | 0 | 0 | 3:12 | 0.40497 | 0.37225 | 0.03271 | 4.3445e-06 | 0
[13 empty] | 3:12 | 1.1006 | 0.91146 | 0 |  | 3:12 | 0 | 0 | 0 | 3:12 | 0.40563 | 0.37286 | 0.032764 | 4.3518e-06 | 0
[13 empty] | 3:12 | 1.0859 | 0.91146 | 0 |  | 3:12 | 0 | 0 | 0 | 3:12 | 0.40629 | 0.37347 | 0.032817 | 4.3589e-06 | 0
[13 empty] | 3:13 | 1.0714 | 0.91146 | 0 |  | 3:13 | 0 | 0 | 0 | 3:13 | 0.40694 | 0.37407 | 0.032869 | 4.3657e-06 | 0
[13 empty] | 3:13 | 1.0572 | 0.91146 | 0 |  | 3:13 | 0 | 0 | 0 | 3:13 | 0.40758 | 0.37466 | 0.03292 | 4.3726e-06 | 0
[13 empty] | 3:13 | 1.0434 | 0.91146 | 0 |  | 3:13 | 0 | 0 | 0 | 3:13 | 0.40821 | 0.37523 | 0.032972 | 4.3793e-06 | 0
[13 empty] | 3:14 | 1.0298 | 0.91146 | 0 |  | 3:14 | 0 | 0 | 0 | 3:14 | 0.40883 | 0.3758 | 0.033021 | 4.386e-06 | 0
[13 empty] | 3:14 | 1.0164 | 0.91146 | 0 |  | 3:14 | 0 | 0 | 0 | 3:14 | 0.40945 | 0.37638 | 0.033071 | 4.3927e-06 | 0
[13 empty] | 3:14 | 1.0034 | 0.91146 | 0 |  | 3:14 | 0 | 0 | 0 | 3:14 | 0.41006 | 0.37693 | 0.033121 | 4.3992e-06 | 0
[13 empty] | 3:14 | 0.99062 | 0.91146 | 0 |  | 3:14 | 0 | 0 | 0 | 3:14 | 0.41066 | 0.37748 | 0.033169 | 4.4057e-06 | 0
[13 empty] | 3:14 | 0.97811 | 0.91146 | 0 |  | 3:14 | 0 | 0 | 0 | 3:14 | 0.41124 | 0.37802 | 0.033218 | 4.412e-06 | 0
[13 empty] | 3:15 | 0.96585 | 0.91146 | 0 |  | 3:15 | 0 | 0 | 0 | 3:15 | 0.41182 | 0.37855 | 0.033264 | 4.4183e-06 | 0
[13 empty] | 3:15 | 0.95385 | 0.91146 | 0 |  | 3:15 | 0 | 0 | 0 | 3:15 | 0.4124 | 0.37909 | 0.033312 | 4.4244e-06 | 0
[13 empty] | 3:15 | 0.94209 | 0.91146 | 0 |  | 3:15 | 0 | 0 | 0 | 3:15 | 0.41298 | 0.37962 | 0.033358 | 4.4305e-06 | 0
[13 empty] | 3:15 | 0.93058 | 0.91146 | 0 |  | 3:15 | 0 | 0 | 0 | 3:15 | 0.41355 | 0.38014 | 0.033403 | 4.4366e-06 | 0
[13 empty] | 3:16 | 0.9193 | 0.91146 | 0 |  | 3:16 | 0 | 0 | 0 | 3:16 | 0.41411 | 0.38065 | 0.033447 | 4.4425e-06 | 0
[13 empty] | 3:16 | 0.90825 | 0.91146 | 0 |  | 3:16 | 0 | 0 | 0 | 3:16 | 0.41465 | 0.38115 | 0.033491 | 4.4484e-06 | 0
[13 empty] | 3:16 | 0.89743 | 0.91146 | 0 |  | 3:16 | 0 | 0 | 0 | 3:16 | 0.41519 | 0.38165 | 0.033535 | 4.4544e-06 | 0
[13 empty] | 3:16 | 0.88683 | 0.91146 | 0 |  | 3:16 | 0 | 0 | 0 | 3:16 | 0.41573 | 0.38214 | 0.033579 | 4.4601e-06 | 0
[13 empty] | 3:17 | 0.87645 | 0.91146 | 0 |  | 3:17 | 0 | 0 | 0 | 3:17 | 0.41627 | 0.38264 | 0.033623 | 4.4658e-06 | 0
[13 empty] | 3:17 | 0.86628 | 0.91146 | 0 |  | 3:17 | 0 | 0 | 0 | 3:17 | 0.41679 | 0.38312 | 0.033665 | 4.4714e-06 | 0
[13 empty] | 3:17 | 0.85633 | 0.91146 | 0 |  | 3:17 | 0 | 0 | 0 | 3:17 | 0.41731 | 0.3836 | 0.033707 | 4.4769e-06 | 0
[13 empty] | 3:17 | 0.84657 | 0.91146 | 0 |  | 3:17 | 0 | 0 | 0 | 3:17 | 0.41781 | 0.38405 | 0.033747 | 4.4824e-06 | 0
[13 empty] | 3:18 | 0.83702 | 0.91146 | 0 |  | 3:18 | 0 | 0 | 0 | 3:18 | 0.41832 | 0.38453 | 0.033789 | 4.488e-06 | 0
[13 empty] | 3:18 | 0.82766 | 0.91146 | 0 |  | 3:18 | 0 | 0 | 0 | 3:18 | 0.41882 | 0.38499 | 0.033829 | 4.4933e-06 | 0
[13 empty] | 3:18 | 0.8185 | 0.91146 | 0 |  | 3:18 | 0 | 0 | 0 | 3:18 | 0.41932 | 0.38545 | 0.033869 | 4.4987e-06 | 0
[13 empty] | 3:18 | 0.80952 | 0.91146 | 0 |  | 3:18 | 0 | 0 | 0 | 3:18 | 0.4198 | 0.38589 | 0.03391 | 4.5038e-06 | 0
[13 empty] | 3:19 | 0.80073 | 0.91146 | 0 |  | 3:19 | 0 | 0 | 0 | 3:19 | 0.4203 | 0.38635 | 0.033948 | 4.509e-06 | 0
[13 empty] | 3:19 | 0.79211 | 0.91146 | 0 |  | 3:19 | 0 | 0 | 0 | 3:19 | 0.42078 | 0.38678 | 0.033986 | 4.5141e-06 | 0
[13 empty] | 3:19 | 0.78368 | 0.91146 | 0 |  | 3:19 | 0 | 0 | 0 | 3:19 | 0.42125 | 0.38722 | 0.034024 | 4.5193e-06 | 0
[13 empty] | 3:20 | 0.77542 | 0.91146 | 0 |  | 3:20 | 0 | 0 | 0 | 3:20 | 0.42171 | 0.38764 | 0.034062 | 4.5243e-06 | 0
[13 empty] | 3:20 | 0.76733 | 0.91146 | 0 |  | 3:20 | 0 | 0 | 0 | 3:20 | 0.42219 | 0.38808 | 0.034101 | 4.5292e-06 | 0
[13 empty] | 3:20 | 0.7594 | 0.91146 | 0 |  | 3:20 | 0 | 0 | 0 | 3:20 | 0.42264 | 0.3885 | 0.034137 | 4.5342e-06 | 0
[13 empty] | 3:20 | 0.75164 | 0.91146 | 0 |  | 3:20 | 0 | 0 | 0 | 3:20 | 0.4231 | 0.38892 | 0.034175 | 4.5392e-06 | 0
[13 empty] | 3:20 | 0.74403 | 0.91146 | 0 |  | 3:20 | 0 | 0 | 0 | 3:20 | 0.42354 | 0.38932 | 0.034211 | 4.5439e-06 | 0
[13 empty] | 3:21 | 0.73658 | 0.91146 | 0 |  | 3:21 | 0 | 0 | 0 | 3:21 | 0.424 | 0.38974 | 0.034248 | 4.5487e-06 | 0
[13 empty] | 3:21 | 0.72929 | 0.91146 | 0 |  | 3:21 | 0 | 0 | 0 | 3:21 | 0.42443 | 0.39015 | 0.034282 | 4.5535e-06 | 0
[13 empty] | 3:21 | 1.1629 | 0.91146 | 0 |  | 3:21 | 0 | 0 | 0 | 3:21 | 0.42514 | 0.3908 | 0.034339 | 4.5609e-06 | 0
[13 empty] | 3:22 | 1.1468 | 0.91146 | 0 |  | 3:22 | 0 | 0 | 0 | 3:22 | 0.42582 | 0.39143 | 0.034395 | 4.5684e-06 | 0
[13 empty] | 3:22 | 1.1311 | 0.91146 | 0 |  | 3:22 | 0 | 0 | 0 | 3:22 | 0.42651 | 0.39206 | 0.03445 | 4.5758e-06 | 0
[13 empty] | 3:22 | 1.1157 | 0.91146 | 0 |  | 3:22 | 0 | 0 | 0 | 3:22 | 0.4272 | 0.39269 | 0.034505 | 4.5831e-06 | 0
[13 empty] | 3:22 | 1.1006 | 0.91146 | 0 |  | 3:22 | 0 | 0 | 0 | 3:22 | 0.42786 | 0.3933 | 0.034559 | 4.5902e-06 | 0
[13 empty] | 3:22 | 1.0859 | 0.91146 | 0 |  | 3:22 | 0 | 0 | 0 | 3:22 | 0.42853 | 0.39391 | 0.034612 | 4.5972e-06 | 0
[13 empty] | 3:23 | 1.0714 | 0.91146 | 0 |  | 3:23 | 0 | 0 | 0 | 3:23 | 0.42917 | 0.3945 | 0.034664 | 4.6043e-06 | 0
[13 empty] | 3:23 | 1.0572 | 0.91146 | 0 |  | 3:23 | 0 | 0 | 0 | 3:23 | 0.42981 | 0.39509 | 0.034716 | 4.6112e-06 | 0
[13 empty] | 3:23 | 1.0434 | 0.91146 | 0 |  | 3:23 | 0 | 0 | 0 | 3:23 | 0.43044 | 0.39567 | 0.034767 | 4.6178e-06 | 0
[13 empty] | 3:24 | 1.0298 | 0.91146 | 0 |  | 3:24 | 0 | 0 | 0 | 3:24 | 0.43106 | 0.39624 | 0.034817 | 4.6245e-06 | 0
[13 empty] | 3:24 | 1.0164 | 0.91146 | 0 |  | 3:24 | 0 | 0 | 0 | 3:24 | 0.43168 | 0.39681 | 0.034866 | 4.6312e-06 | 0
[13 empty] | 3:24 | 1.0034 | 0.91146 | 0 |  | 3:24 | 0 | 0 | 0 | 3:24 | 0.43229 | 0.39737 | 0.034916 | 4.6377e-06 | 0
[13 empty] | 3:24 | 0.99062 | 0.91146 | 0 |  | 3:24 | 0 | 0 | 0 | 3:24 | 0.43289 | 0.39792 | 0.034966 | 4.644e-06 | 0
[13 empty] | 3:24 | 0.97811 | 0.91146 | 0 |  | 3:24 | 0 | 0 | 0 | 3:24 | 0.43347 | 0.39845 | 0.035013 | 4.6505e-06 | 0
[13 empty] | 3:25 | 0.96585 | 0.91146 | 0 |  | 3:25 | 0 | 0 | 0 | 3:25 | 0.43405 | 0.39899 | 0.035059 | 4.6568e-06 | 0
[13 empty] | 3:25 | 0.95385 | 0.91146 | 0 |  | 3:25 | 0 | 0 | 0 | 3:25 | 0.43464 | 0.39952 | 0.035107 | 4.6629e-06 | 0
[13 empty] | 3:25 | 0.94209 | 0.91146 | 0 |  | 3:25 | 0 | 0 | 0 | 3:25 | 0.43522 | 0.40006 | 0.035153 | 4.669e-06 | 0
[13 empty] | 3:26 | 0.93058 | 0.91146 | 0 |  | 3:26 | 0 | 0 | 0 | 3:26 | 0.43578 | 0.40057 | 0.035199 | 4.6751e-06 | 0
[13 empty] | 3:26 | 0.9193 | 0.91146 | 0 |  | 3:26 | 0 | 0 | 0 | 3:26 | 0.43632 | 0.40107 | 0.035243 | 4.6811e-06 | 0
[13 empty] | 3:26 | 0.90825 | 0.91146 | 0 |  | 3:26 | 0 | 0 | 0 | 3:26 | 0.43688 | 0.40159 | 0.035287 | 4.687e-06 | 0
[13 empty] | 3:26 | 0.89743 | 0.91146 | 0 |  | 3:26 | 0 | 0 | 0 | 3:26 | 0.43742 | 0.40208 | 0.03533 | 4.6927e-06 | 0
[13 empty] | 3:26 | 0.88683 | 0.91146 | 0 |  | 3:26 | 0 | 0 | 0 | 3:26 | 0.43796 | 0.40258 | 0.035374 | 4.6986e-06 | 0
[13 empty] | 3:27 | 0.87645 | 0.91146 | 0 |  | 3:27 | 0 | 0 | 0 | 3:27 | 0.43848 | 0.40306 | 0.035418 | 4.7042e-06 | 0
[13 empty] | 3:27 | 0.86628 | 0.91146 | 0 |  | 3:27 | 0 | 0 | 0 | 3:27 | 0.43902 | 0.40355 | 0.03546 | 4.7099e-06 | 0
[13 empty] | 3:27 | 0.85633 | 0.91146 | 0 |  | 3:27 | 0 | 0 | 0 | 3:27 | 0.43954 | 0.40403 | 0.035502 | 4.7154e-06 | 0
[13 empty] | 3:28 | 0.84657 | 0.91146 | 0 |  | 3:28 | 0 | 0 | 0 | 3:28 | 0.44004 | 0.40449 | 0.035542 | 4.721e-06 | 0
[13 empty] | 3:28 | 0.83702 | 0.91146 | 0 |  | 3:28 | 0 | 0 | 0 | 3:28 | 0.44056 | 0.40497 | 0.035584 | 4.7263e-06 | 0
[13 empty] | 3:28 | 0.82766 | 0.91146 | 0 |  | 3:28 | 0 | 0 | 0 | 3:28 | 0.44105 | 0.40542 | 0.035625 | 4.7317e-06 | 0
[13 empty] | 3:28 | 0.8185 | 0.91146 | 0 |  | 3:28 | 0 | 0 | 0 | 3:28 | 0.44155 | 0.40588 | 0.035665 | 4.737e-06 | 0
[13 empty] | 3:29 | 0.80952 | 0.91146 | 0 |  | 3:29 | 0 | 0 | 0 | 3:29 | 0.44203 | 0.40632 | 0.035705 | 4.7424e-06 | 0
[13 empty] | 3:29 | 0.80073 | 0.91146 | 0 |  | 3:29 | 0 | 0 | 0 | 3:29 | 0.44253 | 0.40678 | 0.035743 | 4.7475e-06 | 0
[13 empty] | 3:29 | 0.79211 | 0.91146 | 0 |  | 3:29 | 0 | 0 | 0 | 3:29 | 0.44301 | 0.40722 | 0.035781 | 4.7527e-06 | 0
[13 empty] | 3:29 | 0.78368 | 0.91146 | 0 |  | 3:29 | 0 | 0 | 0 | 3:29 | 0.44347 | 0.40764 | 0.035821 | 4.7577e-06 | 0
[13 empty] | 3:30 | 0.77542 | 0.91146 | 0 |  | 3:30 | 0 | 0 | 0 | 3:30 | 0.44394 | 0.40808 | 0.035858 | 4.7628e-06 | 0
[13 empty] | 3:30 | 0.76733 | 0.91146 | 0 |  | 3:30 | 0 | 0 | 0 | 3:30 | 0.4444 | 0.4085 | 0.035896 | 4.7678e-06 | 0
[13 empty] | 3:30 | 0.7594 | 0.91146 | 0 |  | 3:30 | 0 | 0 | 0 | 3:30 | 0.44488 | 0.40894 | 0.035932 | 4.7727e-06 | 0
[13 empty] | 3:30 | 0.75164 | 0.91146 | 0 |  | 3:30 | 0 | 0 | 0 | 3:30 | 0.44532 | 0.40934 | 0.03597 | 4.7775e-06 | 0
[13 empty] | 3:30 | 0.74403 | 0.91146 | 0 |  | 3:30 | 0 | 0 | 0 | 3:30 | 0.44577 | 0.40976 | 0.036007 | 4.7825e-06 | 0
[13 empty] | 3:31 | 0.73658 | 0.91146 | 0 |  | 3:31 | 0 | 0 | 0 | 3:31 | 0.44623 | 0.41018 | 0.036043 | 4.7873e-06 | 0
[13 empty] | 3:31 | 0.72929 | 0.91146 | 0 |  | 3:31 | 0 | 0 | 0 | 3:31 | 0.44666 | 0.41058 | 0.036077 | 4.792e-06 | 0
[13 empty] | 3:31 | 1.1629 | 0.91146 | 0 |  | 3:31 | 0 | 0 | 0 | 3:31 | 0.44737 | 0.41123 | 0.036135 | 4.7995e-06 | 0
[13 empty] | 3:32 | 1.1468 | 0.91146 | 0 |  | 3:32 | 0 | 0 | 0 | 3:32 | 0.44806 | 0.41186 | 0.03619 | 4.8069e-06 | 0
[13 empty] | 3:32 | 1.1311 | 0.91146 | 0 |  | 3:32 | 0 | 0 | 0 | 3:32 | 0.44874 | 0.41249 | 0.036245 | 4.8144e-06 | 0
[13 empty] | 3:32 | 1.1157 | 0.91146 | 0 |  | 3:32 | 0 | 0 | 0 | 3:32 | 0.44943 | 0.41312 | 0.036301 | 4.8214e-06 | 0
[13 empty] | 3:32 | 1.1006 | 0.91146 | 0 |  | 3:32 | 0 | 0 | 0 | 3:32 | 0.45009 | 0.41373 | 0.036354 | 4.8287e-06 | 0
[13 empty] | 3:32 | 1.0859 | 0.91146 | 0 |  | 3:32 | 0 | 0 | 0 | 3:32 | 0.45074 | 0.41432 | 0.036408 | 4.8358e-06 | 0
[13 empty] | 3:33 | 1.0714 | 0.91146 | 0 |  | 3:33 | 0 | 0 | 0 | 3:33 | 0.4514 | 0.41494 | 0.036459 | 4.8426e-06 | 0
[13 empty] | 3:33 | 1.0572 | 0.91146 | 0 |  | 3:33 | 0 | 0 | 0 | 3:33 | 0.45202 | 0.41551 | 0.036511 | 4.8495e-06 | 0
[13 empty] | 3:33 | 1.0434 | 0.91146 | 0 |  | 3:33 | 0 | 0 | 0 | 3:33 | 0.45267 | 0.4161 | 0.036562 | 4.8564e-06 | 0
[13 empty] | 3:34 | 1.0298 | 0.91146 | 0 |  | 3:34 | 0 | 0 | 0 | 3:34 | 0.45329 | 0.41667 | 0.036614 | 4.8631e-06 | 0
[13 empty] | 3:34 | 1.0164 | 0.91146 | 0 |  | 3:34 | 0 | 0 | 0 | 3:34 | 0.4539 | 0.41723 | 0.036664 | 4.8696e-06 | 0
[13 empty] | 3:34 | 1.0034 | 0.91146 | 0 |  | 3:34 | 0 | 0 | 0 | 3:34 | 0.45452 | 0.4178 | 0.036711 | 4.8761e-06 | 0
[13 empty] | 3:34 | 0.99062 | 0.91146 | 0 |  | 3:34 | 0 | 0 | 0 | 3:34 | 0.45512 | 0.41835 | 0.036761 | 4.8826e-06 | 0
[13 empty] | 3:34 | 0.97811 | 0.91146 | 0 |  | 3:34 | 0 | 0 | 0 | 3:34 | 0.4557 | 0.41889 | 0.036809 | 4.8889e-06 | 0
[13 empty] | 3:35 | 0.96585 | 0.91146 | 0 |  | 3:35 | 0 | 0 | 0 | 3:35 | 0.45628 | 0.41942 | 0.036855 | 4.8952e-06 | 0
[13 empty] | 3:35 | 0.95385 | 0.91146 | 0 |  | 3:35 | 0 | 0 | 0 | 3:35 | 0.45687 | 0.41996 | 0.036902 | 4.9015e-06 | 0
[13 empty] | 3:35 | 0.94209 | 0.91146 | 0 |  | 3:35 | 0 | 0 | 0 | 3:35 | 0.45743 | 0.42047 | 0.036948 | 4.9076e-06 | 0
[13 empty] | 3:36 | 0.93058 | 0.91146 | 0 |  | 3:36 | 0 | 0 | 0 | 3:36 | 0.45801 | 0.42101 | 0.036994 | 4.9135e-06 | 0
[13 empty] | 3:36 | 0.9193 | 0.91146 | 0 |  | 3:36 | 0 | 0 | 0 | 3:36 | 0.45855 | 0.42151 | 0.037038 | 4.9196e-06 | 0
[13 empty] | 3:36 | 0.90825 | 0.91146 | 0 |  | 3:36 | 0 | 0 | 0 | 3:36 | 0.45911 | 0.42202 | 0.037084 | 4.9253e-06 | 0
[13 empty] | 3:36 | 0.89743 | 0.91146 | 0 |  | 3:36 | 0 | 0 | 0 | 3:36 | 0.45965 | 0.42252 | 0.037128 | 4.9313e-06 | 0
[13 empty] | 3:36 | 0.88683 | 0.91146 | 0 |  | 3:36 | 0 | 0 | 0 | 3:36 | 0.46019 | 0.42301 | 0.03717 | 4.937e-06 | 0
[13 empty] | 3:37 | 0.87645 | 0.91146 | 0 |  | 3:37 | 0 | 0 | 0 | 3:37 | 0.46071 | 0.42349 | 0.037214 | 4.9427e-06 | 0
[13 empty] | 3:37 | 0.86628 | 0.91146 | 0 |  | 3:37 | 0 | 0 | 0 | 3:37 | 0.46125 | 0.42399 | 0.037256 | 4.9483e-06 | 0
[13 empty] | 3:37 | 0.85633 | 0.91146 | 0 |  | 3:37 | 0 | 0 | 0 | 3:37 | 0.46175 | 0.42445 | 0.037298 | 4.954e-06 | 0
[13 empty] | 3:38 | 0.84657 | 0.91146 | 0 |  | 3:38 | 0 | 0 | 0 | 3:38 | 0.46227 | 0.42492 | 0.037338 | 4.9593e-06 | 0
[13 empty] | 3:38 | 0.83702 | 0.91146 | 0 |  | 3:38 | 0 | 0 | 0 | 3:38 | 0.46279 | 0.4254 | 0.03738 | 4.9649e-06 | 0
[13 empty] | 3:38 | 0.82766 | 0.91146 | 0 |  | 3:38 | 0 | 0 | 0 | 3:38 | 0.46329 | 0.42586 | 0.03742 | 4.9702e-06 | 0
[13 empty] | 3:38 | 0.8185 | 0.91146 | 0 |  | 3:38 | 0 | 0 | 0 | 3:38 | 0.46378 | 0.42632 | 0.03746 | 4.9756e-06 | 0
[13 empty] | 3:38 | 0.80952 | 0.91146 | 0 |  | 3:38 | 0 | 0 | 0 | 3:38 | 0.46426 | 0.42676 | 0.0375 | 4.9807e-06 | 0
[13 empty] | 3:39 | 0.80073 | 0.91146 | 0 |  | 3:39 | 0 | 0 | 0 | 3:39 | 0.46474 | 0.4272 | 0.037538 | 4.9861e-06 | 0
[13 empty] | 3:39 | 0.79211 | 0.91146 | 0 |  | 3:39 | 0 | 0 | 0 | 3:39 | 0.46524 | 0.42766 | 0.037578 | 4.991e-06 | 0
[13 empty] | 3:39 | 0.78368 | 0.91146 | 0 |  | 3:39 | 0 | 0 | 0 | 3:39 | 0.4657 | 0.42808 | 0.037617 | 4.9962e-06 | 0
[13 empty] | 3:39 | 0.77542 | 0.91146 | 0 |  | 3:39 | 0 | 0 | 0 | 3:39 | 0.46617 | 0.42852 | 0.037653 | 5.0013e-06 | 0
[13 empty] | 3:40 | 0.76733 | 0.91146 | 0 |  | 3:40 | 0 | 0 | 0 | 3:40 | 0.46663 | 0.42894 | 0.037691 | 5.0063e-06 | 0
[13 empty] | 3:40 | 0.7594 | 0.91146 | 0 |  | 3:40 | 0 | 0 | 0 | 3:40 | 0.46709 | 0.42936 | 0.037729 | 5.0111e-06 | 0
[13 empty] | 3:40 | 0.75164 | 0.91146 | 0 |  | 3:40 | 0 | 0 | 0 | 3:40 | 0.46755 | 0.42978 | 0.037766 | 5.0161e-06 | 0
[13 empty] | 3:40 | 0.74403 | 0.91146 | 0 |  | 3:40 | 0 | 0 | 0 | 3:40 | 0.468 | 0.4302 | 0.037802 | 5.0208e-06 | 0
[13 empty] | 3:41 | 0.73658 | 0.91146 | 0 |  | 3:41 | 0 | 0 | 0 | 3:41 | 0.46844 | 0.4306 | 0.037838 | 5.0256e-06 | 0
[13 empty] | 3:41 | 0.72929 | 0.91146 | 0 |  | 3:41 | 0 | 0 | 0 | 3:41 | 0.46889 | 0.43102 | 0.037873 | 5.0304e-06 | 0
[13 empty] | 3:41 | 1.1629 | 0.91146 | 0 |  | 3:41 | 0 | 0 | 0 | 3:41 | 0.4696 | 0.43167 | 0.03793 | 5.038e-06 | 0
[13 empty] | 3:41 | 1.1468 | 0.91146 | 0 |  | 3:41 | 0 | 0 | 0 | 3:41 | 0.47029 | 0.4323 | 0.037987 | 5.0455e-06 | 0
[13 empty] | 3:42 | 1.1311 | 0.91146 | 0 |  | 3:42 | 0 | 0 | 0 | 3:42 | 0.47097 | 0.43293 | 0.038041 | 5.0527e-06 | 0
[13 empty] | 3:42 | 1.1157 | 0.91146 | 0 |  | 3:42 | 0 | 0 | 0 | 3:42 | 0.47164 | 0.43354 | 0.038096 | 5.06e-06 | 0
[13 empty] | 3:42 | 1.1006 | 0.91146 | 0 |  | 3:42 | 0 | 0 | 0 | 3:42 | 0.47232 | 0.43417 | 0.038149 | 5.0672e-06 | 0
[13 empty] | 3:42 | 1.0859 | 0.91146 | 0 |  | 3:42 | 0 | 0 | 0 | 3:42 | 0.47297 | 0.43476 | 0.038203 | 5.0741e-06 | 0
[13 empty] | 3:43 | 1.0714 | 0.91146 | 0 |  | 3:43 | 0 | 0 | 0 | 3:43 | 0.47361 | 0.43535 | 0.038254 | 5.0812e-06 | 0
[13 empty] | 3:43 | 1.0572 | 0.91146 | 0 |  | 3:43 | 0 | 0 | 0 | 3:43 | 0.47426 | 0.43594 | 0.038308 | 5.0881e-06 | 0
[13 empty] | 3:43 | 1.0434 | 0.91146 | 0 |  | 3:43 | 0 | 0 | 0 | 3:43 | 0.4749 | 0.43654 | 0.038358 | 5.0947e-06 | 0
[13 empty] | 3:44 | 1.0298 | 0.91146 | 0 |  | 3:44 | 0 | 0 | 0 | 3:44 | 0.47552 | 0.43711 | 0.038409 | 5.1014e-06 | 0
[13 empty] | 3:44 | 1.0164 | 0.91146 | 0 |  | 3:44 | 0 | 0 | 0 | 3:44 | 0.47613 | 0.43766 | 0.038459 | 5.1081e-06 | 0
[13 empty] | 3:44 | 1.0034 | 0.91146 | 0 |  | 3:44 | 0 | 0 | 0 | 3:44 | 0.47673 | 0.43822 | 0.038507 | 5.1146e-06 | 0
[13 empty] | 3:44 | 0.99062 | 0.91146 | 0 |  | 3:44 | 0 | 0 | 0 | 3:44 | 0.47733 | 0.43877 | 0.038556 | 5.1211e-06 | 0
[13 empty] | 3:44 | 0.97811 | 0.91146 | 0 |  | 3:44 | 0 | 0 | 0 | 3:44 | 0.47793 | 0.43932 | 0.038604 | 5.1274e-06 | 0
[13 empty] | 3:45 | 0.96585 | 0.91146 | 0 |  | 3:45 | 0 | 0 | 0 | 3:45 | 0.47851 | 0.43986 | 0.03865 | 5.1337e-06 | 0
[13 empty] | 3:45 | 0.95385 | 0.91146 | 0 |  | 3:45 | 0 | 0 | 0 | 3:45 | 0.4791 | 0.44039 | 0.038698 | 5.1398e-06 | 0
[13 empty] | 3:45 | 0.94209 | 0.91146 | 0 |  | 3:45 | 0 | 0 | 0 | 3:45 | 0.47966 | 0.44091 | 0.038743 | 5.1459e-06 | 0
[13 empty] | 3:46 | 0.93058 | 0.91146 | 0 |  | 3:46 | 0 | 0 | 0 | 3:46 | 0.48022 | 0.44143 | 0.038789 | 5.152e-06 | 0
[13 empty] | 3:46 | 0.9193 | 0.91146 | 0 |  | 3:46 | 0 | 0 | 0 | 3:46 | 0.48078 | 0.44194 | 0.038833 | 5.158e-06 | 0
[13 empty] | 3:46 | 0.90825 | 0.91146 | 0 |  | 3:46 | 0 | 0 | 0 | 3:46 | 0.48134 | 0.44246 | 0.038879 | 5.1639e-06 | 0
[13 empty] | 3:46 | 0.89743 | 0.91146 | 0 |  | 3:46 | 0 | 0 | 0 | 3:46 | 0.48188 | 0.44295 | 0.038923 | 5.1698e-06 | 0
[13 empty] | 3:46 | 0.88683 | 0.91146 | 0 |  | 3:46 | 0 | 0 | 0 | 3:46 | 0.48242 | 0.44345 | 0.038965 | 5.1755e-06 | 0
[13 empty] | 3:47 | 0.87645 | 0.91146 | 0 |  | 3:47 | 0 | 0 | 0 | 3:47 | 0.48294 | 0.44393 | 0.039009 | 5.1813e-06 | 0
[13 empty] | 3:47 | 0.86628 | 0.91146 | 0 |  | 3:47 | 0 | 0 | 0 | 3:47 | 0.48346 | 0.44441 | 0.039051 | 5.1868e-06 | 0
[13 empty] | 3:47 | 0.85633 | 0.91146 | 0 |  | 3:47 | 0 | 0 | 0 | 3:47 | 0.48398 | 0.44488 | 0.039093 | 5.1923e-06 | 0
[13 empty] | 3:48 | 0.84657 | 0.91146 | 0 |  | 3:48 | 0 | 0 | 0 | 3:48 | 0.4845 | 0.44536 | 0.039135 | 5.1979e-06 | 0
[13 empty] | 3:48 | 0.83702 | 0.91146 | 0 |  | 3:48 | 0 | 0 | 0 | 3:48 | 0.485 | 0.44582 | 0.039175 | 5.2032e-06 | 0
[13 empty] | 3:48 | 0.82766 | 0.91146 | 0 |  | 3:48 | 0 | 0 | 0 | 3:48 | 0.4855 | 0.44628 | 0.039215 | 5.2088e-06 | 0
[13 empty] | 3:48 | 0.8185 | 0.91146 | 0 |  | 3:48 | 0 | 0 | 0 | 3:48 | 0.486 | 0.44674 | 0.039255 | 5.2139e-06 | 0
[13 empty] | 3:49 | 0.80952 | 0.91146 | 0 |  | 3:49 | 0 | 0 | 0 | 3:49 | 0.48649 | 0.44719 | 0.039295 | 5.2193e-06 | 0
[13 empty] | 3:49 | 0.80073 | 0.91146 | 0 |  | 3:49 | 0 | 0 | 0 | 3:49 | 0.48697 | 0.44763 | 0.039334 | 5.2244e-06 | 0
[13 empty] | 3:49 | 0.79211 | 0.91146 | 0 |  | 3:49 | 0 | 0 | 0 | 3:49 | 0.48745 | 0.44807 | 0.039374 | 5.2296e-06 | 0
[13 empty] | 3:49 | 0.78368 | 0.91146 | 0 |  | 3:49 | 0 | 0 | 0 | 3:49 | 0.48793 | 0.44851 | 0.039412 | 5.2347e-06 | 0
[13 empty] | 3:50 | 0.77542 | 0.91146 | 0 |  | 3:50 | 0 | 0 | 0 | 3:50 | 0.48841 | 0.44895 | 0.03945 | 5.2397e-06 | 0
[13 empty] | 3:50 | 0.76733 | 0.91146 | 0 |  | 3:50 | 0 | 0 | 0 | 3:50 | 0.48886 | 0.44937 | 0.039486 | 5.2447e-06 | 0
[13 empty] | 3:50 | 0.7594 | 0.91146 | 0 |  | 3:50 | 0 | 0 | 0 | 3:50 | 0.48932 | 0.44979 | 0.039525 | 5.2496e-06 | 0
[13 empty] | 3:50 | 0.75164 | 0.91146 | 0 |  | 3:50 | 0 | 0 | 0 | 3:50 | 0.48978 | 0.45021 | 0.039561 | 5.2546e-06 | 0
[13 empty] | 3:51 | 0.74403 | 0.91146 | 0 |  | 3:51 | 0 | 0 | 0 | 3:51 | 0.49023 | 0.45063 | 0.039597 | 5.2594e-06 | 0
[13 empty] | 3:51 | 0.73658 | 0.91146 | 0 |  | 3:51 | 0 | 0 | 0 | 3:51 | 0.49067 | 0.45103 | 0.039633 | 5.2641e-06 | 0
[13 empty] | 3:51 | 0.72929 | 0.91146 | 0 |  | 3:51 | 0 | 0 | 0 | 3:51 | 0.49113 | 0.45145 | 0.039668 | 5.2689e-06 | 0
[13 empty] | 3:51 | 1.1629 | 0.91146 | 0 |  | 3:51 | 0 | 0 | 0 | 3:51 | 0.49181 | 0.45208 | 0.039725 | 5.2764e-06 | 0
[13 empty] | 3:52 | 1.1468 | 0.91146 | 0 |  | 3:52 | 0 | 0 | 0 | 3:52 | 0.49252 | 0.45273 | 0.039782 | 5.2838e-06 | 0
[13 empty] | 3:52 | 1.1311 | 0.91146 | 0 |  | 3:52 | 0 | 0 | 0 | 3:52 | 0.49321 | 0.45336 | 0.039838 | 5.2913e-06 | 0
[13 empty] | 3:52 | 1.1157 | 0.91146 | 0 |  | 3:52 | 0 | 0 | 0 | 3:52 | 0.49387 | 0.45397 | 0.039891 | 5.2985e-06 | 0
[13 empty] | 3:52 | 1.1006 | 0.91146 | 0 |  | 3:52 | 0 | 0 | 0 | 3:52 | 0.49453 | 0.45458 | 0.039945 | 5.3056e-06 | 0
[13 empty] | 3:52 | 1.0859 | 0.91146 | 0 |  | 3:52 | 0 | 0 | 0 | 3:52 | 0.4952 | 0.4552 | 0.039998 | 5.3127e-06 | 0
[13 empty] | 3:53 | 1.0714 | 0.91146 | 0 |  | 3:53 | 0 | 0 | 0 | 3:53 | 0.49584 | 0.45579 | 0.040052 | 5.3197e-06 | 0
[13 empty] | 3:53 | 1.0572 | 0.91146 | 0 |  | 3:53 | 0 | 0 | 0 | 3:53 | 0.49649 | 0.45638 | 0.040103 | 5.3264e-06 | 0
[13 empty] | 3:53 | 1.0434 | 0.91146 | 0 |  | 3:53 | 0 | 0 | 0 | 3:53 | 0.49711 | 0.45695 | 0.040153 | 5.3333e-06 | 0
[13 empty] | 3:54 | 1.0298 | 0.91146 | 0 |  | 3:54 | 0 | 0 | 0 | 3:54 | 0.49774 | 0.45753 | 0.040204 | 5.34e-06 | 0
[13 empty] | 3:54 | 1.0164 | 0.91146 | 0 |  | 3:54 | 0 | 0 | 0 | 3:54 | 0.49836 | 0.4581 | 0.040254 | 5.3467e-06 | 0
[13 empty] | 3:54 | 1.0034 | 0.91146 | 0 |  | 3:54 | 0 | 0 | 0 | 3:54 | 0.49896 | 0.45865 | 0.040302 | 5.3531e-06 | 0
[13 empty] | 3:54 | 0.99062 | 0.91146 | 0 |  | 3:54 | 0 | 0 | 0 | 3:54 | 0.49956 | 0.45921 | 0.040352 | 5.3594e-06 | 0
[13 empty] | 3:54 | 0.97811 | 0.91146 | 0 |  | 3:54 | 0 | 0 | 0 | 3:54 | 0.50017 | 0.45976 | 0.040399 | 5.3659e-06 | 0
[13 empty] | 3:55 | 0.96585 | 0.91146 | 0 |  | 3:55 | 0 | 0 | 0 | 3:55 | 0.50075 | 0.4603 | 0.040447 | 5.3721e-06 | 0
[13 empty] | 3:55 | 0.95385 | 0.91146 | 0 |  | 3:55 | 0 | 0 | 0 | 3:55 | 0.50133 | 0.46083 | 0.040493 | 5.3784e-06 | 0
[13 empty] | 3:55 | 0.94209 | 0.91146 | 0 |  | 3:55 | 0 | 0 | 0 | 3:55 | 0.50189 | 0.46135 | 0.040539 | 5.3845e-06 | 0
[13 empty] | 3:56 | 0.93058 | 0.91146 | 0 |  | 3:56 | 0 | 0 | 0 | 3:56 | 0.50245 | 0.46186 | 0.040585 | 5.3906e-06 | 0
[13 empty] | 3:56 | 0.9193 | 0.91146 | 0 |  | 3:56 | 0 | 0 | 0 | 3:56 | 0.50301 | 0.46238 | 0.040628 | 5.3965e-06 | 0
[13 empty] | 3:56 | 0.90825 | 0.91146 | 0 |  | 3:56 | 0 | 0 | 0 | 3:56 | 0.50355 | 0.46287 | 0.040674 | 5.4024e-06 | 0
[13 empty] | 3:56 | 0.89743 | 0.91146 | 0 |  | 3:56 | 0 | 0 | 0 | 3:56 | 0.50411 | 0.46339 | 0.040718 | 5.4081e-06 | 0
[13 empty] | 3:56 | 0.88683 | 0.91146 | 0 |  | 3:56 | 0 | 0 | 0 | 3:56 | 0.50463 | 0.46387 | 0.04076 | 5.4139e-06 | 0
[13 empty] | 3:57 | 0.87645 | 0.91146 | 0 |  | 3:57 | 0 | 0 | 0 | 3:57 | 0.50517 | 0.46436 | 0.040804 | 5.4196e-06 | 0
[13 empty] | 3:57 | 0.86628 | 0.91146 | 0 |  | 3:57 | 0 | 0 | 0 | 3:57 | 0.50569 | 0.46484 | 0.040846 | 5.4253e-06 | 0
[13 empty] | 3:57 | 0.85633 | 0.91146 | 0 |  | 3:57 | 0 | 0 | 0 | 3:57 | 0.50621 | 0.46532 | 0.040888 | 5.4309e-06 | 0
[13 empty] | 3:58 | 0.84657 | 0.91146 | 0 |  | 3:58 | 0 | 0 | 0 | 3:58 | 0.50673 | 0.4658 | 0.04093 | 5.4364e-06 | 0
[13 empty] | 3:58 | 0.83702 | 0.91146 | 0 |  | 3:58 | 0 | 0 | 0 | 3:58 | 0.50723 | 0.46625 | 0.04097 | 5.4418e-06 | 0
[13 empty] | 3:58 | 0.82766 | 0.91146 | 0 |  | 3:58 | 0 | 0 | 0 | 3:58 | 0.50773 | 0.46671 | 0.04101 | 5.4471e-06 | 0
[13 empty] | 3:58 | 0.8185 | 0.91146 | 0 |  | 3:58 | 0 | 0 | 0 | 3:58 | 0.50823 | 0.46717 | 0.041051 | 5.4525e-06 | 0
[13 empty] | 3:58 | 0.80952 | 0.91146 | 0 |  | 3:58 | 0 | 0 | 0 | 3:58 | 0.50873 | 0.46763 | 0.041091 | 5.4578e-06 | 0
[13 empty] | 3:59 | 0.80073 | 0.91146 | 0 |  | 3:59 | 0 | 0 | 0 | 3:59 | 0.5092 | 0.46807 | 0.041129 | 5.463e-06 | 0
[13 empty] | 3:59 | 0.79211 | 0.91146 | 0 |  | 3:59 | 0 | 0 | 0 | 3:59 | 0.50968 | 0.46851 | 0.041169 | 5.4681e-06 | 0
[13 empty] | 3:59 | 0.78368 | 0.91146 | 0 |  | 3:59 | 0 | 0 | 0 | 3:59 | 0.51016 | 0.46895 | 0.041207 | 5.4731e-06 | 0
[13 empty] | 4:00 | 0.77542 | 0.91146 | 0 |  | 4:00 | 0 | 0 | 0 | 4:00 | 0.51064 | 0.46939 | 0.041245 | 5.4782e-06 | 0
[13 empty] | 4:00 | 0.76733 | 0.91146 | 0 |  | 4:00 | 0 | 0 | 0 | 4:00 | 0.51109 | 0.46981 | 0.041282 | 5.4832e-06 | 0
[13 empty] | 4:00 | 0.7594 | 0.91146 | 0 |  | 4:00 | 0 | 0 | 0 | 4:00 | 0.51155 | 0.47023 | 0.04132 | 5.4882e-06 | 0
[13 empty] | 4:00 | 0.75164 | 0.91146 | 0 |  | 4:00 | 0 | 0 | 0 | 4:00 | 0.51201 | 0.47065 | 0.041356 | 5.4929e-06 | 0
[13 empty] | 4:01 | 0.74403 | 0.91146 | 0 |  | 4:01 | 0 | 0 | 0 | 4:01 | 0.51246 | 0.47107 | 0.041392 | 5.4979e-06 | 0
[13 empty] | 4:01 | 0.73658 | 0.91146 | 0 |  | 4:01 | 0 | 0 | 0 | 4:01 | 0.5129 | 0.47147 | 0.041429 | 5.5027e-06 | 0
[13 empty] | 4:01 | 0.72929 | 0.91146 | 0 |  | 4:01 | 0 | 0 | 0 | 4:01 | 0.51334 | 0.47187 | 0.041465 | 5.5073e-06 | 0
[13 empty] | 4:01 | 1.1629 | 0.91146 | 0 |  | 4:01 | 0 | 0 | 0 | 4:01 | 0.51404 | 0.47252 | 0.04152 | 5.5149e-06 | 0
[13 empty] | 4:02 | 1.1468 | 0.91146 | 0 |  | 4:02 | 0 | 0 | 0 | 4:02 | 0.51475 | 0.47317 | 0.041578 | 5.5224e-06 | 0
[13 empty] | 4:02 | 1.1311 | 0.91146 | 0 |  | 4:02 | 0 | 0 | 0 | 4:02 | 0.51544 | 0.4738 | 0.041633 | 5.5296e-06 | 0
[13 empty] | 4:02 | 1.1157 | 0.91146 | 0 |  | 4:02 | 0 | 0 | 0 | 4:02 | 0.5161 | 0.47441 | 0.041686 | 5.5369e-06 | 0
[13 empty] | 4:02 | 1.1006 | 0.91146 | 0 |  | 4:02 | 0 | 0 | 0 | 4:02 | 0.51677 | 0.47502 | 0.04174 | 5.5441e-06 | 0
[13 empty] | 4:03 | 1.0859 | 0.91146 | 0 |  | 4:03 | 0 | 0 | 0 | 4:03 | 0.51743 | 0.47563 | 0.041793 | 5.5512e-06 | 0
[13 empty] | 4:03 | 1.0714 | 0.91146 | 0 |  | 4:03 | 0 | 0 | 0 | 4:03 | 0.51808 | 0.47622 | 0.041847 | 5.5581e-06 | 0
[13 empty] | 4:03 | 1.0572 | 0.91146 | 0 |  | 4:03 | 0 | 0 | 0 | 4:03 | 0.51872 | 0.47682 | 0.041898 | 5.5649e-06 | 0
[13 empty] | 4:03 | 1.0434 | 0.91146 | 0 |  | 4:03 | 0 | 0 | 0 | 4:03 | 0.51934 | 0.47739 | 0.041948 | 5.5718e-06 | 0
[13 empty] | 4:04 | 1.0298 | 0.91146 | 0 |  | 4:04 | 0 | 0 | 0 | 4:04 | 0.51997 | 0.47796 | 0.042 | 5.5785e-06 | 0
[13 empty] | 4:04 | 1.0164 | 0.91146 | 0 |  | 4:04 | 0 | 0 | 0 | 4:04 | 0.52059 | 0.47853 | 0.042049 | 5.585e-06 | 0
[13 empty] | 4:04 | 1.0034 | 0.91146 | 0 |  | 4:04 | 0 | 0 | 0 | 4:04 | 0.52119 | 0.47909 | 0.042097 | 5.5915e-06 | 0
[13 empty] | 4:04 | 0.99062 | 0.91146 | 0 |  | 4:04 | 0 | 0 | 0 | 4:04 | 0.52179 | 0.47964 | 0.042147 | 5.598e-06 | 0
[13 empty] | 4:04 | 0.97811 | 0.91146 | 0 |  | 4:04 | 0 | 0 | 0 | 4:04 | 0.5224 | 0.4802 | 0.042195 | 5.6043e-06 | 0
[13 empty] | 4:05 | 0.96585 | 0.91146 | 0 |  | 4:05 | 0 | 0 | 0 | 4:05 | 0.52298 | 0.48073 | 0.042242 | 5.6106e-06 | 0
[13 empty] | 4:05 | 0.95385 | 0.91146 | 0 |  | 4:05 | 0 | 0 | 0 | 4:05 | 0.52354 | 0.48125 | 0.042288 | 5.6169e-06 | 0
[13 empty] | 4:05 | 0.94209 | 0.91146 | 0 |  | 4:05 | 0 | 0 | 0 | 4:05 | 0.52412 | 0.48178 | 0.042334 | 5.623e-06 | 0
[13 empty] | 4:06 | 0.93058 | 0.91146 | 0 |  | 4:06 | 0 | 0 | 0 | 4:06 | 0.52468 | 0.4823 | 0.04238 | 5.6289e-06 | 0
[13 empty] | 4:06 | 0.9193 | 0.91146 | 0 |  | 4:06 | 0 | 0 | 0 | 4:06 | 0.52524 | 0.48281 | 0.042426 | 5.6348e-06 | 0
[13 empty] | 4:06 | 0.90825 | 0.91146 | 0 |  | 4:06 | 0 | 0 | 0 | 4:06 | 0.52578 | 0.48331 | 0.04247 | 5.6408e-06 | 0
[13 empty] | 4:06 | 0.89743 | 0.91146 | 0 |  | 4:06 | 0 | 0 | 0 | 4:06 | 0.52632 | 0.48381 | 0.042513 | 5.6467e-06 | 0
[13 empty] | 4:06 | 0.88683 | 0.91146 | 0 |  | 4:06 | 0 | 0 | 0 | 4:06 | 0.52686 | 0.4843 | 0.042555 | 5.6524e-06 | 0
[13 empty] | 4:07 | 0.87645 | 0.91146 | 0 |  | 4:07 | 0 | 0 | 0 | 4:07 | 0.5274 | 0.4848 | 0.042599 | 5.6581e-06 | 0
[13 empty] | 4:07 | 0.86628 | 0.91146 | 0 |  | 4:07 | 0 | 0 | 0 | 4:07 | 0.52792 | 0.48528 | 0.042641 | 5.6637e-06 | 0
[13 empty] | 4:07 | 0.85633 | 0.91146 | 0 |  | 4:07 | 0 | 0 | 0 | 4:07 | 0.52844 | 0.48575 | 0.042683 | 5.6692e-06 | 0
[13 empty] | 4:08 | 0.84657 | 0.91146 | 0 |  | 4:08 | 0 | 0 | 0 | 4:08 | 0.52896 | 0.48623 | 0.042725 | 5.6748e-06 | 0
[13 empty] | 4:08 | 0.83702 | 0.91146 | 0 |  | 4:08 | 0 | 0 | 0 | 4:08 | 0.52946 | 0.48669 | 0.042766 | 5.6803e-06 | 0
[13 empty] | 4:08 | 0.82766 | 0.91146 | 0 |  | 4:08 | 0 | 0 | 0 | 4:08 | 0.52996 | 0.48715 | 0.042806 | 5.6857e-06 | 0
[13 empty] | 4:08 | 0.8185 | 0.91146 | 0 |  | 4:08 | 0 | 0 | 0 | 4:08 | 0.53046 | 0.48761 | 0.042846 | 5.691e-06 | 0
[13 empty] | 4:08 | 0.80952 | 0.91146 | 0 |  | 4:08 | 0 | 0 | 0 | 4:08 | 0.53096 | 0.48806 | 0.042886 | 5.6962e-06 | 0
[13 empty] | 4:09 | 0.80073 | 0.91146 | 0 |  | 4:09 | 0 | 0 | 0 | 4:09 | 0.53144 | 0.4885 | 0.042926 | 5.7013e-06 | 0
[13 empty] | 4:09 | 0.79211 | 0.91146 | 0 |  | 4:09 | 0 | 0 | 0 | 4:09 | 0.53191 | 0.48894 | 0.042964 | 5.7065e-06 | 0
[13 empty] | 4:09 | 0.78368 | 0.91146 | 0 |  | 4:09 | 0 | 0 | 0 | 4:09 | 0.53239 | 0.48938 | 0.043002 | 5.7116e-06 | 0
[13 empty] | 4:10 | 0.77542 | 0.91146 | 0 |  | 4:10 | 0 | 0 | 0 | 4:10 | 0.53285 | 0.4898 | 0.043041 | 5.7166e-06 | 0
[13 empty] | 4:10 | 0.76733 | 0.91146 | 0 |  | 4:10 | 0 | 0 | 0 | 4:10 | 0.53332 | 0.49024 | 0.043077 | 5.7216e-06 | 0
[13 empty] | 4:10 | 0.7594 | 0.91146 | 0 |  | 4:10 | 0 | 0 | 0 | 4:10 | 0.53378 | 0.49066 | 0.043115 | 5.7265e-06 | 0
[13 empty] | 4:10 | 0.75164 | 0.91146 | 0 |  | 4:10 | 0 | 0 | 0 | 4:10 | 0.53424 | 0.49108 | 0.043151 | 5.7315e-06 | 0
[13 empty] | 4:10 | 0.74403 | 0.91146 | 0 |  | 4:10 | 0 | 0 | 0 | 4:10 | 0.5347 | 0.4915 | 0.043188 | 5.7363e-06 | 0
[13 empty] | 4:11 | 0.73658 | 0.91146 | 0 |  | 4:11 | 0 | 0 | 0 | 4:11 | 0.53513 | 0.4919 | 0.043224 | 5.741e-06 | 0
[13 empty] | 4:11 | 0.72929 | 0.91146 | 0 |  | 4:11 | 0 | 0 | 0 | 4:11 | 0.53557 | 0.4923 | 0.04326 | 5.7458e-06 | 0
[13 empty] | 4:11 | 1.1629 | 0.91146 | 0 |  | 4:11 | 0 | 0 | 0 | 4:11 | 0.53628 | 0.49295 | 0.043316 | 5.7535e-06 | 0
[13 empty] | 4:12 | 1.1468 | 0.91146 | 0 |  | 4:12 | 0 | 0 | 0 | 4:12 | 0.53698 | 0.4936 | 0.043373 | 5.7609e-06 | 0
[13 empty] | 4:12 | 1.1311 | 0.91146 | 0 |  | 4:12 | 0 | 0 | 0 | 4:12 | 0.53767 | 0.49423 | 0.043428 | 5.7682e-06 | 0
[13 empty] | 4:12 | 1.1157 | 0.91146 | 0 |  | 4:12 | 0 | 0 | 0 | 4:12 | 0.53833 | 0.49484 | 0.043482 | 5.7754e-06 | 0
[13 empty] | 4:12 | 1.1006 | 0.91146 | 0 |  | 4:12 | 0 | 0 | 0 | 4:12 | 0.539 | 0.49546 | 0.043535 | 5.7825e-06 | 0
[13 empty] | 4:12 | 1.0859 | 0.91146 | 0 |  | 4:12 | 0 | 0 | 0 | 4:12 | 0.53966 | 0.49607 | 0.043589 | 5.7895e-06 | 0
[13 empty] | 4:13 | 1.0714 | 0.91146 | 0 |  | 4:13 | 0 | 0 | 0 | 4:13 | 0.54031 | 0.49666 | 0.043642 | 5.7966e-06 | 0
[13 empty] | 4:13 | 1.0572 | 0.91146 | 0 |  | 4:13 | 0 | 0 | 0 | 4:13 | 0.54095 | 0.49725 | 0.043694 | 5.8035e-06 | 0
[13 empty] | 4:13 | 1.0434 | 0.91146 | 0 |  | 4:13 | 0 | 0 | 0 | 4:13 | 0.54157 | 0.49782 | 0.043743 | 5.8102e-06 | 0
[13 empty] | 4:13 | 1.0298 | 0.91146 | 0 |  | 4:13 | 0 | 0 | 0 | 4:13 | 0.5422 | 0.4984 | 0.043795 | 5.8169e-06 | 0
[13 empty] | 4:14 | 1.0164 | 0.91146 | 0 |  | 4:14 | 0 | 0 | 0 | 4:14 | 0.54282 | 0.49897 | 0.043845 | 5.8235e-06 | 0
[13 empty] | 4:14 | 1.0034 | 0.91146 | 0 |  | 4:14 | 0 | 0 | 0 | 4:14 | 0.54342 | 0.49952 | 0.043894 | 5.83e-06 | 0
[13 empty] | 4:14 | 0.99062 | 0.91146 | 0 |  | 4:14 | 0 | 0 | 0 | 4:14 | 0.54403 | 0.50008 | 0.043942 | 5.8365e-06 | 0
[13 empty] | 4:14 | 0.97811 | 0.91146 | 0 |  | 4:14 | 0 | 0 | 0 | 4:14 | 0.54461 | 0.50061 | 0.04399 | 5.8428e-06 | 0
[13 empty] | 4:15 | 0.96585 | 0.91146 | 0 |  | 4:15 | 0 | 0 | 0 | 4:15 | 0.54521 | 0.50117 | 0.044038 | 5.8491e-06 | 0
[13 empty] | 4:15 | 0.95385 | 0.91146 | 0 |  | 4:15 | 0 | 0 | 0 | 4:15 | 0.54577 | 0.50168 | 0.044083 | 5.8552e-06 | 0
[13 empty] | 4:15 | 0.94209 | 0.91146 | 0 |  | 4:15 | 0 | 0 | 0 | 4:15 | 0.54635 | 0.50222 | 0.044129 | 5.8614e-06 | 0
[13 empty] | 4:16 | 0.93058 | 0.91146 | 0 |  | 4:16 | 0 | 0 | 0 | 4:16 | 0.54691 | 0.50273 | 0.044175 | 5.8675e-06 | 0
[13 empty] | 4:16 | 0.9193 | 0.91146 | 0 |  | 4:16 | 0 | 0 | 0 | 4:16 | 0.54747 | 0.50325 | 0.044221 | 5.8734e-06 | 0
[13 empty] | 4:16 | 0.90825 | 0.91146 | 0 |  | 4:16 | 0 | 0 | 0 | 4:16 | 0.54802 | 0.50374 | 0.044265 | 5.8793e-06 | 0
[13 empty] | 4:16 | 0.89743 | 0.91146 | 0 |  | 4:16 | 0 | 0 | 0 | 4:16 | 0.54856 | 0.50424 | 0.044309 | 5.8852e-06 | 0
[13 empty] | 4:16 | 0.88683 | 0.91146 | 0 |  | 4:16 | 0 | 0 | 0 | 4:16 | 0.5491 | 0.50474 | 0.044353 | 5.891e-06 | 0
[13 empty] | 4:17 | 0.87645 | 0.91146 | 0 |  | 4:17 | 0 | 0 | 0 | 4:17 | 0.54963 | 0.50523 | 0.044395 | 5.8965e-06 | 0
[13 empty] | 4:17 | 0.86628 | 0.91146 | 0 |  | 4:17 | 0 | 0 | 0 | 4:17 | 0.55015 | 0.50571 | 0.044437 | 5.9022e-06 | 0
[13 empty] | 4:17 | 0.85633 | 0.91146 | 0 |  | 4:17 | 0 | 0 | 0 | 4:17 | 0.55067 | 0.50619 | 0.044479 | 5.9078e-06 | 0
[13 empty] | 4:18 | 0.84657 | 0.91146 | 0 |  | 4:18 | 0 | 0 | 0 | 4:18 | 0.55119 | 0.50667 | 0.044521 | 5.9133e-06 | 0
[13 empty] | 4:18 | 0.83702 | 0.91146 | 0 |  | 4:18 | 0 | 0 | 0 | 4:18 | 0.55169 | 0.50712 | 0.044561 | 5.9187e-06 | 0
[13 empty] | 4:18 | 0.82766 | 0.91146 | 0 |  | 4:18 | 0 | 0 | 0 | 4:18 | 0.55219 | 0.50758 | 0.044601 | 5.924e-06 | 0
[13 empty] | 4:18 | 0.8185 | 0.91146 | 0 |  | 4:18 | 0 | 0 | 0 | 4:18 | 0.55269 | 0.50804 | 0.044641 | 5.9293e-06 | 0
[13 empty] | 4:18 | 0.80952 | 0.91146 | 0 |  | 4:18 | 0 | 0 | 0 | 4:18 | 0.55317 | 0.50848 | 0.044681 | 5.9347e-06 | 0
[13 empty] | 4:19 | 0.80073 | 0.91146 | 0 |  | 4:19 | 0 | 0 | 0 | 4:19 | 0.55367 | 0.50894 | 0.044721 | 5.9399e-06 | 0
[13 empty] | 4:19 | 0.79211 | 0.91146 | 0 |  | 4:19 | 0 | 0 | 0 | 4:19 | 0.55414 | 0.50938 | 0.044759 | 5.945e-06 | 0
[13 empty] | 4:19 | 0.78368 | 0.91146 | 0 |  | 4:19 | 0 | 0 | 0 | 4:19 | 0.55462 | 0.50982 | 0.044798 | 5.9502e-06 | 0
[13 empty] | 4:20 | 0.77542 | 0.91146 | 0 |  | 4:20 | 0 | 0 | 0 | 4:20 | 0.55508 | 0.51024 | 0.044836 | 5.9551e-06 | 0
[13 empty] | 4:20 | 0.76733 | 0.91146 | 0 |  | 4:20 | 0 | 0 | 0 | 4:20 | 0.55556 | 0.51068 | 0.044872 | 5.9601e-06 | 0
[13 empty] | 4:20 | 0.7594 | 0.91146 | 0 |  | 4:20 | 0 | 0 | 0 | 4:20 | 0.55601 | 0.5111 | 0.04491 | 5.9651e-06 | 0
[13 empty] | 4:20 | 0.75164 | 0.91146 | 0 |  | 4:20 | 0 | 0 | 0 | 4:20 | 0.55647 | 0.51152 | 0.044947 | 5.97e-06 | 0
[13 empty] | 4:20 | 0.74403 | 0.91146 | 0 |  | 4:20 | 0 | 0 | 0 | 4:20 | 0.55691 | 0.51192 | 0.044983 | 5.9748e-06 | 0
[13 empty] | 4:21 | 0.73658 | 0.91146 | 0 |  | 4:21 | 0 | 0 | 0 | 4:21 | 0.55736 | 0.51234 | 0.045019 | 5.9796e-06 | 0
[13 empty] | 4:21 | 0.72929 | 0.91146 | 0 |  | 4:21 | 0 | 0 | 0 | 4:21 | 0.5578 | 0.51274 | 0.045055 | 5.9844e-06 | 0
[13 empty] | 4:21 | 1.1629 | 0.91146 | 0 |  | 4:21 | 0 | 0 | 0 | 4:21 | 0.55851 | 0.51339 | 0.045111 | 5.9918e-06 | 0
[13 empty] | 4:22 | 1.1468 | 0.91146 | 0 |  | 4:22 | 0 | 0 | 0 | 4:22 | 0.55919 | 0.51402 | 0.045168 | 5.9992e-06 | 0
[13 empty] | 4:22 | 1.1311 | 0.91146 | 0 |  | 4:22 | 0 | 0 | 0 | 4:22 | 0.55988 | 0.51465 | 0.045224 | 6.0067e-06 | 0
[13 empty] | 4:22 | 1.1157 | 0.91146 | 0 |  | 4:22 | 0 | 0 | 0 | 4:22 | 0.56056 | 0.51528 | 0.045277 | 6.014e-06 | 0
[13 empty] | 4:22 | 1.1006 | 0.91146 | 0 |  | 4:22 | 0 | 0 | 0 | 4:22 | 0.56123 | 0.51589 | 0.045332 | 6.021e-06 | 0
[13 empty] | 4:22 | 1.0859 | 0.91146 | 0 |  | 4:22 | 0 | 0 | 0 | 4:22 | 0.56189 | 0.5165 | 0.045384 | 6.0281e-06 | 0
[13 empty] | 4:23 | 1.0714 | 0.91146 | 0 |  | 4:23 | 0 | 0 | 0 | 4:23 | 0.56254 | 0.51709 | 0.045437 | 6.035e-06 | 0
[13 empty] | 4:23 | 1.0572 | 0.91146 | 0 |  | 4:23 | 0 | 0 | 0 | 4:23 | 0.56318 | 0.51769 | 0.045489 | 6.0418e-06 | 0
[13 empty] | 4:23 | 1.0434 | 0.91146 | 0 |  | 4:23 | 0 | 0 | 0 | 4:23 | 0.56381 | 0.51826 | 0.045541 | 6.0487e-06 | 0
[13 empty] | 4:24 | 1.0298 | 0.91146 | 0 |  | 4:24 | 0 | 0 | 0 | 4:24 | 0.56443 | 0.51883 | 0.04559 | 6.0554e-06 | 0
[13 empty] | 4:24 | 1.0164 | 0.91146 | 0 |  | 4:24 | 0 | 0 | 0 | 4:24 | 0.56505 | 0.51941 | 0.04564 | 6.0619e-06 | 0
[13 empty] | 4:24 | 1.0034 | 0.91146 | 0 |  | 4:24 | 0 | 0 | 0 | 4:24 | 0.56565 | 0.51996 | 0.04569 | 6.0686e-06 | 0
[13 empty] | 4:24 | 0.99062 | 0.91146 | 0 |  | 4:24 | 0 | 0 | 0 | 4:24 | 0.56626 | 0.52051 | 0.045737 | 6.0749e-06 | 0
[13 empty] | 4:24 | 0.97811 | 0.91146 | 0 |  | 4:24 | 0 | 0 | 0 | 4:24 | 0.56684 | 0.52105 | 0.045785 | 6.0814e-06 | 0
[13 empty] | 4:25 | 0.96585 | 0.91146 | 0 |  | 4:25 | 0 | 0 | 0 | 4:25 | 0.56742 | 0.52158 | 0.045833 | 6.0875e-06 | 0
[13 empty] | 4:25 | 0.95385 | 0.91146 | 0 |  | 4:25 | 0 | 0 | 0 | 4:25 | 0.568 | 0.52212 | 0.045879 | 6.0938e-06 | 0
[13 empty] | 4:25 | 0.94209 | 0.91146 | 0 |  | 4:25 | 0 | 0 | 0 | 4:25 | 0.56858 | 0.52265 | 0.045924 | 6.0999e-06 | 0
[13 empty] | 4:26 | 0.93058 | 0.91146 | 0 |  | 4:26 | 0 | 0 | 0 | 4:26 | 0.56914 | 0.52317 | 0.04597 | 6.1058e-06 | 0
[13 empty] | 4:26 | 0.9193 | 0.91146 | 0 |  | 4:26 | 0 | 0 | 0 | 4:26 | 0.56971 | 0.52368 | 0.046016 | 6.1119e-06 | 0
[13 empty] | 4:26 | 0.90825 | 0.91146 | 0 |  | 4:26 | 0 | 0 | 0 | 4:26 | 0.57025 | 0.52418 | 0.04606 | 6.1179e-06 | 0
[13 empty] | 4:26 | 0.89743 | 0.91146 | 0 |  | 4:26 | 0 | 0 | 0 | 4:26 | 0.57079 | 0.52468 | 0.046104 | 6.1236e-06 | 0
[13 empty] | 4:26 | 0.88683 | 0.91146 | 0 |  | 4:26 | 0 | 0 | 0 | 4:26 | 0.57133 | 0.52517 | 0.046148 | 6.1293e-06 | 0
[13 empty] | 4:27 | 0.87645 | 0.91146 | 0 |  | 4:27 | 0 | 0 | 0 | 4:27 | 0.57187 | 0.52567 | 0.04619 | 6.135e-06 | 0
[13 empty] | 4:27 | 0.86628 | 0.91146 | 0 |  | 4:27 | 0 | 0 | 0 | 4:27 | 0.57239 | 0.52615 | 0.046232 | 6.1408e-06 | 0
[13 empty] | 4:27 | 0.85633 | 0.91146 | 0 |  | 4:27 | 0 | 0 | 0 | 4:27 | 0.5729 | 0.52662 | 0.046274 | 6.1463e-06 | 0
[13 empty] | 4:27 | 0.84657 | 0.91146 | 0 |  | 4:27 | 0 | 0 | 0 | 4:27 | 0.57341 | 0.52708 | 0.046316 | 6.1517e-06 | 0
[13 empty] | 4:28 | 0.83702 | 0.91146 | 0 |  | 4:28 | 0 | 0 | 0 | 4:28 | 0.57392 | 0.52756 | 0.046356 | 6.1572e-06 | 0
[13 empty] | 4:28 | 0.82766 | 0.91146 | 0 |  | 4:28 | 0 | 0 | 0 | 4:28 | 0.57442 | 0.52802 | 0.046396 | 6.1625e-06 | 0
[13 empty] | 4:28 | 0.8185 | 0.91146 | 0 |  | 4:28 | 0 | 0 | 0 | 4:28 | 0.57492 | 0.52848 | 0.046436 | 6.1679e-06 | 0
[13 empty] | 4:28 | 0.80952 | 0.91146 | 0 |  | 4:28 | 0 | 0 | 0 | 4:28 | 0.5754 | 0.52892 | 0.046476 | 6.173e-06 | 0
[13 empty] | 4:29 | 0.80073 | 0.91146 | 0 |  | 4:29 | 0 | 0 | 0 | 4:29 | 0.5759 | 0.52937 | 0.046517 | 6.1784e-06 | 0
[13 empty] | 4:29 | 0.79211 | 0.91146 | 0 |  | 4:29 | 0 | 0 | 0 | 4:29 | 0.57637 | 0.52981 | 0.046555 | 6.1836e-06 | 0
[13 empty] | 4:29 | 0.78368 | 0.91146 | 0 |  | 4:29 | 0 | 0 | 0 | 4:29 | 0.57685 | 0.53025 | 0.046593 | 6.1885e-06 | 0
[13 empty] | 4:29 | 0.77542 | 0.91146 | 0 |  | 4:29 | 0 | 0 | 0 | 4:29 | 0.57731 | 0.53067 | 0.046631 | 6.1937e-06 | 0
[13 empty] | 4:30 | 0.76733 | 0.91146 | 0 |  | 4:30 | 0 | 0 | 0 | 4:30 | 0.57779 | 0.53111 | 0.046669 | 6.1986e-06 | 0
[13 empty] | 4:30 | 0.7594 | 0.91146 | 0 |  | 4:30 | 0 | 0 | 0 | 4:30 | 0.57824 | 0.53153 | 0.046706 | 6.2036e-06 | 0
[13 empty] | 4:30 | 0.75164 | 0.91146 | 0 |  | 4:30 | 0 | 0 | 0 | 4:30 | 0.5787 | 0.53195 | 0.046742 | 6.2084e-06 | 0
[13 empty] | 4:30 | 0.74403 | 0.91146 | 0 |  | 4:30 | 0 | 0 | 0 | 4:30 | 0.57914 | 0.53235 | 0.046778 | 6.2132e-06 | 0
[13 empty] | 4:31 | 0.73658 | 0.91146 | 0 |  | 4:31 | 0 | 0 | 0 | 4:31 | 0.5796 | 0.53277 | 0.046814 | 6.2179e-06 | 0
[13 empty] | 4:31 | 0.72929 | 0.91146 | 0 |  | 4:31 | 0 | 0 | 0 | 4:31 | 0.58003 | 0.53318 | 0.046851 | 6.2227e-06 | 0
[13 empty] | 4:31 | 1.1629 | 0.91146 | 0 |  | 4:31 | 0 | 0 | 0 | 4:31 | 0.58074 | 0.53382 | 0.046908 | 6.2303e-06 | 0
[13 empty] | 4:32 | 1.1468 | 0.91146 | 0 |  | 4:32 | 0 | 0 | 0 | 4:32 | 0.58142 | 0.53446 | 0.046963 | 6.2378e-06 | 0
[13 empty] | 4:32 | 1.1311 | 0.91146 | 0 |  | 4:32 | 0 | 0 | 0 | 4:32 | 0.58211 | 0.53509 | 0.047019 | 6.245e-06 | 0
[13 empty] | 4:32 | 1.1157 | 0.91146 | 0 |  | 4:32 | 0 | 0 | 0 | 4:32 | 0.58279 | 0.53572 | 0.047072 | 6.2523e-06 | 0
[13 empty] | 4:32 | 1.1006 | 0.91146 | 0 |  | 4:32 | 0 | 0 | 0 | 4:32 | 0.58346 | 0.53633 | 0.047128 | 6.2596e-06 | 0
[13 empty] | 4:33 | 1.0859 | 0.91146 | 0 |  | 4:33 | 0 | 0 | 0 | 4:33 | 0.5841 | 0.53692 | 0.047179 | 6.2666e-06 | 0
[13 empty] | 4:33 | 1.0714 | 0.91146 | 0 |  | 4:33 | 0 | 0 | 0 | 4:33 | 0.58477 | 0.53753 | 0.047233 | 6.2735e-06 | 0
[13 empty] | 4:33 | 1.0572 | 0.91146 | 0 |  | 4:33 | 0 | 0 | 0 | 4:33 | 0.58539 | 0.5381 | 0.047284 | 6.2804e-06 | 0
[13 empty] | 4:33 | 1.0434 | 0.91146 | 0 |  | 4:33 | 0 | 0 | 0 | 4:33 | 0.58604 | 0.53869 | 0.047336 | 6.2871e-06 | 0
[13 empty] | 4:34 | 1.0298 | 0.91146 | 0 |  | 4:34 | 0 | 0 | 0 | 4:34 | 0.58666 | 0.53927 | 0.047386 | 6.2939e-06 | 0
[13 empty] | 4:34 | 1.0164 | 0.91146 | 0 |  | 4:34 | 0 | 0 | 0 | 4:34 | 0.58726 | 0.53982 | 0.047435 | 6.3004e-06 | 0
[13 empty] | 4:34 | 1.0034 | 0.91146 | 0 |  | 4:34 | 0 | 0 | 0 | 4:34 | 0.58789 | 0.54039 | 0.047485 | 6.3069e-06 | 0
[13 empty] | 4:34 | 0.99062 | 0.91146 | 0 |  | 4:34 | 0 | 0 | 0 | 4:34 | 0.58849 | 0.54095 | 0.047533 | 6.3134e-06 | 0
[13 empty] | 4:34 | 0.97811 | 0.91146 | 0 |  | 4:34 | 0 | 0 | 0 | 4:34 | 0.58907 | 0.54148 | 0.04758 | 6.3197e-06 | 0
[13 empty] | 4:35 | 0.96585 | 0.91146 | 0 |  | 4:35 | 0 | 0 | 0 | 4:35 | 0.58965 | 0.54202 | 0.047628 | 6.326e-06 | 0
[13 empty] | 4:35 | 0.95385 | 0.91146 | 0 |  | 4:35 | 0 | 0 | 0 | 4:35 | 0.59023 | 0.54255 | 0.047674 | 6.3321e-06 | 0
[13 empty] | 4:35 | 0.94209 | 0.91146 | 0 |  | 4:35 | 0 | 0 | 0 | 4:35 | 0.59079 | 0.54307 | 0.04772 | 6.3382e-06 | 0
[13 empty] | 4:36 | 0.93058 | 0.91146 | 0 |  | 4:36 | 0 | 0 | 0 | 4:36 | 0.59138 | 0.5436 | 0.047766 | 6.3444e-06 | 0
[13 empty] | 4:36 | 0.9193 | 0.91146 | 0 |  | 4:36 | 0 | 0 | 0 | 4:36 | 0.59192 | 0.5441 | 0.047811 | 6.3503e-06 | 0
[13 empty] | 4:36 | 0.90825 | 0.91146 | 0 |  | 4:36 | 0 | 0 | 0 | 4:36 | 0.59248 | 0.54462 | 0.047855 | 6.3562e-06 | 0
[13 empty] | 4:36 | 0.89743 | 0.91146 | 0 |  | 4:36 | 0 | 0 | 0 | 4:36 | 0.59302 | 0.54511 | 0.047899 | 6.3621e-06 | 0
[13 empty] | 4:36 | 0.88683 | 0.91146 | 0 |  | 4:36 | 0 | 0 | 0 | 4:36 | 0.59356 | 0.54561 | 0.047943 | 6.3679e-06 | 0
[13 empty] | 4:37 | 0.87645 | 0.91146 | 0 |  | 4:37 | 0 | 0 | 0 | 4:37 | 0.59408 | 0.54609 | 0.047985 | 6.3736e-06 | 0
[13 empty] | 4:37 | 0.86628 | 0.91146 | 0 |  | 4:37 | 0 | 0 | 0 | 4:37 | 0.59462 | 0.54658 | 0.048027 | 6.3791e-06 | 0
[13 empty] | 4:37 | 0.85633 | 0.91146 | 0 |  | 4:37 | 0 | 0 | 0 | 4:37 | 0.59514 | 0.54706 | 0.048069 | 6.3847e-06 | 0
[13 empty] | 4:38 | 0.84657 | 0.91146 | 0 |  | 4:38 | 0 | 0 | 0 | 4:38 | 0.59564 | 0.54752 | 0.048111 | 6.3902e-06 | 0
[13 empty] | 4:38 | 0.83702 | 0.91146 | 0 |  | 4:38 | 0 | 0 | 0 | 4:38 | 0.59615 | 0.548 | 0.048151 | 6.3957e-06 | 0
[13 empty] | 4:38 | 0.82766 | 0.91146 | 0 |  | 4:38 | 0 | 0 | 0 | 4:38 | 0.59665 | 0.54845 | 0.048193 | 6.4011e-06 | 0
[13 empty] | 4:38 | 0.8185 | 0.91146 | 0 |  | 4:38 | 0 | 0 | 0 | 4:38 | 0.59715 | 0.54891 | 0.048233 | 6.4064e-06 | 0
[13 empty] | 4:38 | 0.80952 | 0.91146 | 0 |  | 4:38 | 0 | 0 | 0 | 4:38 | 0.59763 | 0.54935 | 0.048272 | 6.4116e-06 | 0
[13 empty] | 4:39 | 0.80073 | 0.91146 | 0 |  | 4:39 | 0 | 0 | 0 | 4:39 | 0.59811 | 0.54979 | 0.048312 | 6.4167e-06 | 0
[13 empty] | 4:39 | 0.79211 | 0.91146 | 0 |  | 4:39 | 0 | 0 | 0 | 4:39 | 0.59861 | 0.55025 | 0.04835 | 6.4219e-06 | 0
[13 empty] | 4:39 | 0.78368 | 0.91146 | 0 |  | 4:39 | 0 | 0 | 0 | 4:39 | 0.59906 | 0.55067 | 0.048388 | 6.4271e-06 | 0
[13 empty] | 4:40 | 0.77542 | 0.91146 | 0 |  | 4:40 | 0 | 0 | 0 | 4:40 | 0.59954 | 0.55111 | 0.048426 | 6.432e-06 | 0
[13 empty] | 4:40 | 0.76733 | 0.91146 | 0 |  | 4:40 | 0 | 0 | 0 | 4:40 | 0.6 | 0.55153 | 0.048465 | 6.437e-06 | 0
[13 empty] | 4:40 | 0.7594 | 0.91146 | 0 |  | 4:40 | 0 | 0 | 0 | 4:40 | 0.60046 | 0.55195 | 0.048501 | 6.442e-06 | 0
[13 empty] | 4:40 | 0.75164 | 0.91146 | 0 |  | 4:40 | 0 | 0 | 0 | 4:40 | 0.60091 | 0.55237 | 0.048537 | 6.4469e-06 | 0
[13 empty] | 4:40 | 0.74403 | 0.91146 | 0 |  | 4:40 | 0 | 0 | 0 | 4:40 | 0.60137 | 0.55279 | 0.048573 | 6.4517e-06 | 0
[13 empty] | 4:41 | 0.73658 | 0.91146 | 0 |  | 4:41 | 0 | 0 | 0 | 4:41 | 0.60183 | 0.55321 | 0.04861 | 6.4565e-06 | 0
[13 empty] | 4:41 | 0.72929 | 0.91146 | 0 |  | 4:41 | 0 | 0 | 0 | 4:41 | 0.60226 | 0.55361 | 0.048646 | 6.4612e-06 | 0
[13 empty] | 4:41 | 1.1629 | 0.91146 | 0 |  | 4:41 | 0 | 0 | 0 | 4:41 | 0.60297 | 0.55426 | 0.048703 | 6.4687e-06 | 0
[13 empty] | 4:42 | 1.1468 | 0.91146 | 0 |  | 4:42 | 0 | 0 | 0 | 4:42 | 0.60366 | 0.55489 | 0.048759 | 6.4761e-06 | 0
[13 empty] | 4:42 | 1.1311 | 0.91146 | 0 |  | 4:42 | 0 | 0 | 0 | 4:42 | 0.60434 | 0.55552 | 0.048814 | 6.4836e-06 | 0
[13 empty] | 4:42 | 1.1157 | 0.91146 | 0 |  | 4:42 | 0 | 0 | 0 | 4:42 | 0.60503 | 0.55615 | 0.048869 | 6.4908e-06 | 0
[13 empty] | 4:42 | 1.1006 | 0.91146 | 0 |  | 4:42 | 0 | 0 | 0 | 4:42 | 0.60569 | 0.55676 | 0.048923 | 6.4979e-06 | 0
[13 empty] | 4:42 | 1.0859 | 0.91146 | 0 |  | 4:42 | 0 | 0 | 0 | 4:42 | 0.60634 | 0.55735 | 0.048976 | 6.505e-06 | 0
[13 empty] | 4:43 | 1.0714 | 0.91146 | 0 |  | 4:43 | 0 | 0 | 0 | 4:43 | 0.60698 | 0.55795 | 0.049028 | 6.512e-06 | 0
[13 empty] | 4:43 | 1.0572 | 0.91146 | 0 |  | 4:43 | 0 | 0 | 0 | 4:43 | 0.60762 | 0.55854 | 0.04908 | 6.5189e-06 | 0
[13 empty] | 4:43 | 1.0434 | 0.91146 | 0 |  | 4:43 | 0 | 0 | 0 | 4:43 | 0.60827 | 0.55913 | 0.049131 | 6.5256e-06 | 0
[13 empty] | 4:44 | 1.0298 | 0.91146 | 0 |  | 4:44 | 0 | 0 | 0 | 4:44 | 0.60889 | 0.5597 | 0.049181 | 6.5323e-06 | 0
[13 empty] | 4:44 | 1.0164 | 0.91146 | 0 |  | 4:44 | 0 | 0 | 0 | 4:44 | 0.60949 | 0.56026 | 0.04923 | 6.539e-06 | 0
[13 empty] | 4:44 | 1.0034 | 0.91146 | 0 |  | 4:44 | 0 | 0 | 0 | 4:44 | 0.61012 | 0.56083 | 0.04928 | 6.5455e-06 | 0
[13 empty] | 4:44 | 0.99062 | 0.91146 | 0 |  | 4:44 | 0 | 0 | 0 | 4:44 | 0.6107 | 0.56136 | 0.049328 | 6.552e-06 | 0
[13 empty] | 4:44 | 0.97811 | 0.91146 | 0 |  | 4:44 | 0 | 0 | 0 | 4:44 | 0.6113 | 0.56192 | 0.049376 | 6.5583e-06 | 0
[13 empty] | 4:45 | 0.96585 | 0.91146 | 0 |  | 4:45 | 0 | 0 | 0 | 4:45 | 0.61188 | 0.56245 | 0.049423 | 6.5646e-06 | 0
[13 empty] | 4:45 | 0.95385 | 0.91146 | 0 |  | 4:45 | 0 | 0 | 0 | 4:45 | 0.61246 | 0.56299 | 0.049469 | 6.5707e-06 | 0
[13 empty] | 4:45 | 0.94209 | 0.91146 | 0 |  | 4:45 | 0 | 0 | 0 | 4:45 | 0.61303 | 0.5635 | 0.049515 | 6.5768e-06 | 0
[13 empty] | 4:46 | 0.93058 | 0.91146 | 0 |  | 4:46 | 0 | 0 | 0 | 4:46 | 0.61359 | 0.56402 | 0.049561 | 6.5829e-06 | 0
[13 empty] | 4:46 | 0.9193 | 0.91146 | 0 |  | 4:46 | 0 | 0 | 0 | 4:46 | 0.61415 | 0.56454 | 0.049607 | 6.5888e-06 | 0
[13 empty] | 4:46 | 0.90825 | 0.91146 | 0 |  | 4:46 | 0 | 0 | 0 | 4:46 | 0.61471 | 0.56505 | 0.049651 | 6.5947e-06 | 0
[13 empty] | 4:46 | 0.89743 | 0.91146 | 0 |  | 4:46 | 0 | 0 | 0 | 4:46 | 0.61525 | 0.56555 | 0.049695 | 6.6005e-06 | 0
[13 empty] | 4:46 | 0.88683 | 0.91146 | 0 |  | 4:46 | 0 | 0 | 0 | 4:46 | 0.61579 | 0.56604 | 0.049738 | 6.6064e-06 | 0
[13 empty] | 4:47 | 0.87645 | 0.91146 | 0 |  | 4:47 | 0 | 0 | 0 | 4:47 | 0.61631 | 0.56652 | 0.04978 | 6.6119e-06 | 0
[13 empty] | 4:47 | 0.86628 | 0.91146 | 0 |  | 4:47 | 0 | 0 | 0 | 4:47 | 0.61683 | 0.567 | 0.049822 | 6.6177e-06 | 0
[13 empty] | 4:47 | 0.85633 | 0.91146 | 0 |  | 4:47 | 0 | 0 | 0 | 4:47 | 0.61735 | 0.56748 | 0.049865 | 6.6232e-06 | 0
[13 empty] | 4:48 | 0.84657 | 0.91146 | 0 |  | 4:48 | 0 | 0 | 0 | 4:48 | 0.61787 | 0.56795 | 0.049907 | 6.6287e-06 | 0
[13 empty] | 4:48 | 0.83702 | 0.91146 | 0 |  | 4:48 | 0 | 0 | 0 | 4:48 | 0.61837 | 0.56841 | 0.049947 | 6.6341e-06 | 0
[13 empty] | 4:48 | 0.82766 | 0.91146 | 0 |  | 4:48 | 0 | 0 | 0 | 4:48 | 0.61889 | 0.56889 | 0.049989 | 6.6394e-06 | 0
[13 empty] | 4:48 | 0.8185 | 0.91146 | 0 |  | 4:48 | 0 | 0 | 0 | 4:48 | 0.61936 | 0.56933 | 0.050029 | 6.6448e-06 | 0
[13 empty] | 4:48 | 0.80952 | 0.91146 | 0 |  | 4:48 | 0 | 0 | 0 | 4:48 | 0.61986 | 0.56979 | 0.050067 | 6.6501e-06 | 0
[13 empty] | 4:49 | 0.80073 | 0.91146 | 0 |  | 4:49 | 0 | 0 | 0 | 4:49 | 0.62034 | 0.57023 | 0.050107 | 6.6553e-06 | 0
[13 empty] | 4:49 | 0.79211 | 0.91146 | 0 |  | 4:49 | 0 | 0 | 0 | 4:49 | 0.62082 | 0.57067 | 0.050145 | 6.6604e-06 | 0
[13 empty] | 4:49 | 0.78368 | 0.91146 | 0 |  | 4:49 | 0 | 0 | 0 | 4:49 | 0.6213 | 0.57111 | 0.050183 | 6.6656e-06 | 0
[13 empty] | 4:50 | 0.77542 | 0.91146 | 0 |  | 4:50 | 0 | 0 | 0 | 4:50 | 0.62177 | 0.57154 | 0.050222 | 6.6706e-06 | 0
[13 empty] | 4:50 | 0.76733 | 0.91146 | 0 |  | 4:50 | 0 | 0 | 0 | 4:50 | 0.62223 | 0.57196 | 0.05026 | 6.6755e-06 | 0
[13 empty] | 4:50 | 0.7594 | 0.91146 | 0 |  | 4:50 | 0 | 0 | 0 | 4:50 | 0.62269 | 0.57238 | 0.050296 | 6.6805e-06 | 0
[13 empty] | 4:50 | 0.75164 | 0.91146 | 0 |  | 4:50 | 0 | 0 | 0 | 4:50 | 0.62314 | 0.5728 | 0.050332 | 6.6853e-06 | 0
[13 empty] | 4:50 | 0.74403 | 0.91146 | 0 |  | 4:50 | 0 | 0 | 0 | 4:50 | 0.6236 | 0.57323 | 0.050369 | 6.6902e-06 | 0
[13 empty] | 4:51 | 0.73658 | 0.91146 | 0 |  | 4:51 | 0 | 0 | 0 | 4:51 | 0.62404 | 0.57363 | 0.050405 | 6.695e-06 | 0
[13 empty] | 4:51 | 0.72929 | 0.91146 | 0 |  | 4:51 | 0 | 0 | 0 | 4:51 | 0.62449 | 0.57405 | 0.050441 | 6.6998e-06 | 0
[13 empty] | 4:51 | 1.1629 | 0.91146 | 0 |  | 4:51 | 0 | 0 | 0 | 4:51 | 0.62518 | 0.57468 | 0.050499 | 6.7072e-06 | 0
[13 empty] | 4:52 | 1.1468 | 0.91146 | 0 |  | 4:52 | 0 | 0 | 0 | 4:52 | 0.62589 | 0.57533 | 0.050554 | 6.7147e-06 | 0
[13 empty] | 4:52 | 1.1311 | 0.91146 | 0 |  | 4:52 | 0 | 0 | 0 | 4:52 | 0.62657 | 0.57596 | 0.050609 | 6.7221e-06 | 0
[13 empty] | 4:52 | 1.1157 | 0.91146 | 0 |  | 4:52 | 0 | 0 | 0 | 4:52 | 0.62724 | 0.57657 | 0.050665 | 6.7294e-06 | 0
[13 empty] | 4:52 | 1.1006 | 0.91146 | 0 |  | 4:52 | 0 | 0 | 0 | 4:52 | 0.6279 | 0.57718 | 0.050718 | 6.7365e-06 | 0
[13 empty] | 4:52 | 1.0859 | 0.91146 | 0 |  | 4:52 | 0 | 0 | 0 | 4:52 | 0.62857 | 0.57779 | 0.050772 | 6.7435e-06 | 0
[13 empty] | 4:53 | 1.0714 | 0.91146 | 0 |  | 4:53 | 0 | 0 | 0 | 4:53 | 0.62921 | 0.57838 | 0.050823 | 6.7504e-06 | 0
[13 empty] | 4:53 | 1.0572 | 0.91146 | 0 |  | 4:53 | 0 | 0 | 0 | 4:53 | 0.62986 | 0.57897 | 0.050875 | 6.7573e-06 | 0
[13 empty] | 4:53 | 1.0434 | 0.91146 | 0 |  | 4:53 | 0 | 0 | 0 | 4:53 | 0.6305 | 0.57957 | 0.050926 | 6.7641e-06 | 0
[13 empty] | 4:54 | 1.0298 | 0.91146 | 0 |  | 4:54 | 0 | 0 | 0 | 4:54 | 0.63112 | 0.58014 | 0.050976 | 6.7708e-06 | 0
[13 empty] | 4:54 | 1.0164 | 0.91146 | 0 |  | 4:54 | 0 | 0 | 0 | 4:54 | 0.63173 | 0.58069 | 0.051026 | 6.7773e-06 | 0
[13 empty] | 4:54 | 1.0034 | 0.91146 | 0 |  | 4:54 | 0 | 0 | 0 | 4:54 | 0.63233 | 0.58125 | 0.051075 | 6.7838e-06 | 0
[13 empty] | 4:54 | 0.99062 | 0.91146 | 0 |  | 4:54 | 0 | 0 | 0 | 4:54 | 0.63293 | 0.5818 | 0.051123 | 6.7903e-06 | 0
[13 empty] | 4:54 | 0.97811 | 0.91146 | 0 |  | 4:54 | 0 | 0 | 0 | 4:54 | 0.63353 | 0.58235 | 0.051171 | 6.7966e-06 | 0
[13 empty] | 4:55 | 0.96585 | 0.91146 | 0 |  | 4:55 | 0 | 0 | 0 | 4:55 | 0.63411 | 0.58289 | 0.051219 | 6.8029e-06 | 0
[13 empty] | 4:55 | 0.95385 | 0.91146 | 0 |  | 4:55 | 0 | 0 | 0 | 4:55 | 0.6347 | 0.58342 | 0.051264 | 6.8092e-06 | 0
[13 empty] | 4:55 | 0.94209 | 0.91146 | 0 |  | 4:55 | 0 | 0 | 0 | 4:55 | 0.63526 | 0.58394 | 0.051312 | 6.8153e-06 | 0
[13 empty] | 4:56 | 0.93058 | 0.91146 | 0 |  | 4:56 | 0 | 0 | 0 | 4:56 | 0.63582 | 0.58446 | 0.051356 | 6.8213e-06 | 0
[13 empty] | 4:56 | 0.9193 | 0.91146 | 0 |  | 4:56 | 0 | 0 | 0 | 4:56 | 0.63638 | 0.58497 | 0.051402 | 6.8274e-06 | 0
[13 empty] | 4:56 | 0.90825 | 0.91146 | 0 |  | 4:56 | 0 | 0 | 0 | 4:56 | 0.63694 | 0.58549 | 0.051446 | 6.8333e-06 | 0
[13 empty] | 4:56 | 0.89743 | 0.91146 | 0 |  | 4:56 | 0 | 0 | 0 | 4:56 | 0.63748 | 0.58598 | 0.05149 | 6.839e-06 | 0
[13 empty] | 4:56 | 0.88683 | 0.91146 | 0 |  | 4:56 | 0 | 0 | 0 | 4:56 | 0.638 | 0.58646 | 0.051534 | 6.8447e-06 | 0
[13 empty] | 4:57 | 0.87645 | 0.91146 | 0 |  | 4:57 | 0 | 0 | 0 | 4:57 | 0.63854 | 0.58696 | 0.051576 | 6.8505e-06 | 0
[13 empty] | 4:57 | 0.86628 | 0.91146 | 0 |  | 4:57 | 0 | 0 | 0 | 4:57 | 0.63906 | 0.58743 | 0.051618 | 6.856e-06 | 0
[13 empty] | 4:57 | 0.85633 | 0.91146 | 0 |  | 4:57 | 0 | 0 | 0 | 4:57 | 0.63958 | 0.58791 | 0.05166 | 6.8617e-06 | 0
[13 empty] | 4:58 | 0.84657 | 0.91146 | 0 |  | 4:58 | 0 | 0 | 0 | 4:58 | 0.6401 | 0.58839 | 0.051702 | 6.8671e-06 | 0
[13 empty] | 4:58 | 0.83702 | 0.91146 | 0 |  | 4:58 | 0 | 0 | 0 | 4:58 | 0.6406 | 0.58885 | 0.051744 | 6.8726e-06 | 0
[13 empty] | 4:58 | 0.82766 | 0.91146 | 0 |  | 4:58 | 0 | 0 | 0 | 4:58 | 0.6411 | 0.58931 | 0.051784 | 6.878e-06 | 0
[13 empty] | 4:58 | 0.8185 | 0.91146 | 0 |  | 4:58 | 0 | 0 | 0 | 4:58 | 0.6416 | 0.58976 | 0.051824 | 6.8833e-06 | 0
[13 empty] | 4:58 | 0.80952 | 0.91146 | 0 |  | 4:58 | 0 | 0 | 0 | 4:58 | 0.64209 | 0.59022 | 0.051862 | 6.8885e-06 | 0
[13 empty] | 4:59 | 0.80073 | 0.91146 | 0 |  | 4:59 | 0 | 0 | 0 | 4:59 | 0.64257 | 0.59066 | 0.051902 | 6.8938e-06 | 0
[13 empty] | 4:59 | 0.79211 | 0.91146 | 0 |  | 4:59 | 0 | 0 | 0 | 4:59 | 0.64305 | 0.5911 | 0.051941 | 6.899e-06 | 0
[13 empty] | 4:59 | 0.78368 | 0.91146 | 0 |  | 4:59 | 0 | 0 | 0 | 4:59 | 0.64353 | 0.59154 | 0.051979 | 6.904e-06 | 0
[13 empty] | 5:00 | 0.77542 | 0.91146 | 0 |  | 5:00 | 0 | 0 | 0 | 5:00 | 0.644 | 0.59198 | 0.052017 | 6.9091e-06 | 0
[13 empty] | 5:00 | 0.76733 | 0.91146 | 0 |  | 5:00 | 0 | 0 | 0 | 5:00 | 0.64446 | 0.5924 | 0.052055 | 6.9141e-06 | 0
[13 empty] | 5:00 | 0.7594 | 0.91146 | 0 |  | 5:00 | 0 | 0 | 0 | 5:00 | 0.64492 | 0.59282 | 0.052091 | 6.9188e-06 | 0
[13 empty] | 5:00 | 0.75164 | 0.91146 | 0 |  | 5:00 | 0 | 0 | 0 | 5:00 | 0.64538 | 0.59324 | 0.052128 | 6.9238e-06 | 0
[13 empty] | 5:00 | 0.74403 | 0.91146 | 0 |  | 5:00 | 0 | 0 | 0 | 5:00 | 0.64583 | 0.59366 | 0.052164 | 6.9286e-06 | 0
[13 empty] | 5:01 | 0.73658 | 0.91146 | 0 |  | 5:01 | 0 | 0 | 0 | 5:01 | 0.64627 | 0.59406 | 0.0522 | 6.9334e-06 | 0
[13 empty] | 5:01 | 0.72929 | 0.91146 | 0 |  | 5:01 | 0 | 0 | 0 | 5:01 | 0.64671 | 0.59446 | 0.052237 | 6.9381e-06 | 0
[13 empty] | 5:01 | 1.1629 | 0.91146 | 0 |  | 5:01 | 0 | 0 | 0 | 5:01 | 0.64741 | 0.59511 | 0.052294 | 6.9458e-06 | 0
[13 empty] | 5:02 | 1.1468 | 0.91146 | 0 |  | 5:02 | 0 | 0 | 0 | 5:02 | 0.64812 | 0.59576 | 0.052349 | 6.9532e-06 | 0
[13 empty] | 5:02 | 1.1311 | 0.91146 | 0 |  | 5:02 | 0 | 0 | 0 | 5:02 | 0.6488 | 0.59639 | 0.052405 | 6.9605e-06 | 0
[13 empty] | 5:02 | 1.1157 | 0.91146 | 0 |  | 5:02 | 0 | 0 | 0 | 5:02 | 0.64947 | 0.597 | 0.05246 | 6.9677e-06 | 0
[13 empty] | 5:02 | 1.1006 | 0.91146 | 0 |  | 5:02 | 0 | 0 | 0 | 5:02 | 0.65013 | 0.59761 | 0.052513 | 6.975e-06 | 0
[13 empty] | 5:02 | 1.0859 | 0.91146 | 0 |  | 5:02 | 0 | 0 | 0 | 5:02 | 0.6508 | 0.59823 | 0.052567 | 6.9821e-06 | 0
[13 empty] | 5:03 | 1.0714 | 0.91146 | 0 |  | 5:03 | 0 | 0 | 0 | 5:03 | 0.65144 | 0.59882 | 0.052619 | 6.9889e-06 | 0
[13 empty] | 5:03 | 1.0572 | 0.91146 | 0 |  | 5:03 | 0 | 0 | 0 | 5:03 | 0.65209 | 0.59941 | 0.05267 | 6.9958e-06 | 0
[13 empty] | 5:03 | 1.0434 | 0.91146 | 0 |  | 5:03 | 0 | 0 | 0 | 5:03 | 0.65271 | 0.59998 | 0.052722 | 7.0025e-06 | 0
[13 empty] | 5:04 | 1.0298 | 0.91146 | 0 |  | 5:04 | 0 | 0 | 0 | 5:04 | 0.65333 | 0.60056 | 0.052771 | 7.0092e-06 | 0
[13 empty] | 5:04 | 1.0164 | 0.91146 | 0 |  | 5:04 | 0 | 0 | 0 | 5:04 | 0.65396 | 0.60113 | 0.052821 | 7.0159e-06 | 0
[13 empty] | 5:04 | 1.0034 | 0.91146 | 0 |  | 5:04 | 0 | 0 | 0 | 5:04 | 0.65456 | 0.60168 | 0.052871 | 7.0224e-06 | 0
[13 empty] | 5:04 | 0.99062 | 0.91146 | 0 |  | 5:04 | 0 | 0 | 0 | 5:04 | 0.65516 | 0.60224 | 0.052918 | 7.0289e-06 | 0
[13 empty] | 5:04 | 0.97811 | 0.91146 | 0 |  | 5:04 | 0 | 0 | 0 | 5:04 | 0.65576 | 0.60279 | 0.052966 | 7.0352e-06 | 0
[13 empty] | 5:05 | 0.96585 | 0.91146 | 0 |  | 5:05 | 0 | 0 | 0 | 5:05 | 0.65635 | 0.60332 | 0.053014 | 7.0415e-06 | 0
[13 empty] | 5:05 | 0.95385 | 0.91146 | 0 |  | 5:05 | 0 | 0 | 0 | 5:05 | 0.65693 | 0.60386 | 0.053062 | 7.0476e-06 | 0
[13 empty] | 5:05 | 0.94209 | 0.91146 | 0 |  | 5:05 | 0 | 0 | 0 | 5:05 | 0.65749 | 0.60437 | 0.053107 | 7.0537e-06 | 0
[13 empty] | 5:06 | 0.93058 | 0.91146 | 0 |  | 5:06 | 0 | 0 | 0 | 5:06 | 0.65805 | 0.60489 | 0.053151 | 7.0598e-06 | 0
[13 empty] | 5:06 | 0.9193 | 0.91146 | 0 |  | 5:06 | 0 | 0 | 0 | 5:06 | 0.65861 | 0.60541 | 0.053197 | 7.0657e-06 | 0
[13 empty] | 5:06 | 0.90825 | 0.91146 | 0 |  | 5:06 | 0 | 0 | 0 | 5:06 | 0.65915 | 0.6059 | 0.053241 | 7.0716e-06 | 0
[13 empty] | 5:06 | 0.89743 | 0.91146 | 0 |  | 5:06 | 0 | 0 | 0 | 5:06 | 0.65969 | 0.6064 | 0.053285 | 7.0776e-06 | 0
[13 empty] | 5:06 | 0.88683 | 0.91146 | 0 |  | 5:06 | 0 | 0 | 0 | 5:06 | 0.66023 | 0.6069 | 0.053329 | 7.0833e-06 | 0
[13 empty] | 5:07 | 0.87645 | 0.91146 | 0 |  | 5:07 | 0 | 0 | 0 | 5:07 | 0.66077 | 0.60739 | 0.053371 | 7.089e-06 | 0
[13 empty] | 5:07 | 0.86628 | 0.91146 | 0 |  | 5:07 | 0 | 0 | 0 | 5:07 | 0.66129 | 0.60787 | 0.053415 | 7.0946e-06 | 0
[13 empty] | 5:07 | 0.85633 | 0.91146 | 0 |  | 5:07 | 0 | 0 | 0 | 5:07 | 0.66181 | 0.60835 | 0.053455 | 7.1001e-06 | 0
[13 empty] | 5:08 | 0.84657 | 0.91146 | 0 |  | 5:08 | 0 | 0 | 0 | 5:08 | 0.66233 | 0.60882 | 0.053497 | 7.1056e-06 | 0
[13 empty] | 5:08 | 0.83702 | 0.91146 | 0 |  | 5:08 | 0 | 0 | 0 | 5:08 | 0.66283 | 0.60928 | 0.053539 | 7.111e-06 | 0
[13 empty] | 5:08 | 0.82766 | 0.91146 | 0 |  | 5:08 | 0 | 0 | 0 | 5:08 | 0.66333 | 0.60974 | 0.053579 | 7.1165e-06 | 0
[13 empty] | 5:08 | 0.8185 | 0.91146 | 0 |  | 5:08 | 0 | 0 | 0 | 5:08 | 0.66383 | 0.6102 | 0.053619 | 7.1217e-06 | 0
[13 empty] | 5:08 | 0.80952 | 0.91146 | 0 |  | 5:08 | 0 | 0 | 0 | 5:08 | 0.66432 | 0.61066 | 0.053657 | 7.127e-06 | 0
[13 empty] | 5:09 | 0.80073 | 0.91146 | 0 |  | 5:09 | 0 | 0 | 0 | 5:09 | 0.6648 | 0.6111 | 0.053698 | 7.1322e-06 | 0
[13 empty] | 5:09 | 0.79211 | 0.91146 | 0 |  | 5:09 | 0 | 0 | 0 | 5:09 | 0.66528 | 0.61154 | 0.053736 | 7.1373e-06 | 0
[13 empty] | 5:09 | 0.78368 | 0.91146 | 0 |  | 5:09 | 0 | 0 | 0 | 5:09 | 0.66576 | 0.61198 | 0.053774 | 7.1425e-06 | 0
[13 empty] | 5:10 | 0.77542 | 0.91146 | 0 |  | 5:10 | 0 | 0 | 0 | 5:10 | 0.66623 | 0.61242 | 0.053812 | 7.1475e-06 | 0
[13 empty] | 5:10 | 0.76733 | 0.91146 | 0 |  | 5:10 | 0 | 0 | 0 | 5:10 | 0.66669 | 0.61284 | 0.05385 | 7.1524e-06 | 0
[13 empty] | 5:10 | 0.7594 | 0.91146 | 0 |  | 5:10 | 0 | 0 | 0 | 5:10 | 0.66715 | 0.61326 | 0.053887 | 7.1574e-06 | 0
[13 empty] | 5:10 | 0.75164 | 0.91146 | 0 |  | 5:10 | 0 | 0 | 0 | 5:10 | 0.66761 | 0.61368 | 0.053925 | 7.1624e-06 | 0
[13 empty] | 5:10 | 0.74403 | 0.91146 | 0 |  | 5:10 | 0 | 0 | 0 | 5:10 | 0.66806 | 0.6141 | 0.053961 | 7.1671e-06 | 0
[13 empty] | 5:11 | 0.73658 | 0.91146 | 0 |  | 5:11 | 0 | 0 | 0 | 5:11 | 0.6685 | 0.6145 | 0.053996 | 7.1719e-06 | 0
[13 empty] | 5:11 | 0.72929 | 0.91146 | 0 |  | 5:11 | 0 | 0 | 0 | 5:11 | 0.66894 | 0.6149 | 0.054032 | 7.1767e-06 | 0
[13 empty] | 5:11 | 1.1629 | 0.91146 | 0 |  | 5:11 | 0 | 0 | 0 | 5:11 | 0.66964 | 0.61555 | 0.054089 | 7.1841e-06 | 0
[13 empty] | 5:12 | 1.1468 | 0.91146 | 0 |  | 5:12 | 0 | 0 | 0 | 5:12 | 0.67035 | 0.6162 | 0.054145 | 7.1916e-06 | 0
[13 empty] | 5:12 | 1.1311 | 0.91146 | 0 |  | 5:12 | 0 | 0 | 0 | 5:12 | 0.67103 | 0.61683 | 0.0542 | 7.199e-06 | 0
[13 empty] | 5:12 | 1.1157 | 0.91146 | 0 |  | 5:12 | 0 | 0 | 0 | 5:12 | 0.6717 | 0.61744 | 0.054255 | 7.2063e-06 | 0
[13 empty] | 5:12 | 1.1006 | 0.91146 | 0 |  | 5:12 | 0 | 0 | 0 | 5:12 | 0.67237 | 0.61805 | 0.054309 | 7.2133e-06 | 0
[13 empty] | 5:12 | 1.0859 | 0.91146 | 0 |  | 5:12 | 0 | 0 | 0 | 5:12 | 0.67303 | 0.61866 | 0.054362 | 7.2204e-06 | 0
[13 empty] | 5:13 | 1.0714 | 0.91146 | 0 |  | 5:13 | 0 | 0 | 0 | 5:13 | 0.67367 | 0.61925 | 0.054414 | 7.2275e-06 | 0
[13 empty] | 5:13 | 1.0572 | 0.91146 | 0 |  | 5:13 | 0 | 0 | 0 | 5:13 | 0.67432 | 0.61984 | 0.054465 | 7.2344e-06 | 0
[13 empty] | 5:13 | 1.0434 | 0.91146 | 0 |  | 5:13 | 0 | 0 | 0 | 5:13 | 0.67494 | 0.62042 | 0.054517 | 7.241e-06 | 0
[13 empty] | 5:13 | 1.0298 | 0.91146 | 0 |  | 5:13 | 0 | 0 | 0 | 5:13 | 0.67556 | 0.62099 | 0.054567 | 7.2477e-06 | 0
[13 empty] | 5:14 | 1.0164 | 0.91146 | 0 |  | 5:14 | 0 | 0 | 0 | 5:14 | 0.67619 | 0.62156 | 0.054616 | 7.2544e-06 | 0
[13 empty] | 5:14 | 1.0034 | 0.91146 | 0 |  | 5:14 | 0 | 0 | 0 | 5:14 | 0.67679 | 0.62212 | 0.054666 | 7.2609e-06 | 0
[13 empty] | 5:14 | 0.99062 | 0.91146 | 0 |  | 5:14 | 0 | 0 | 0 | 5:14 | 0.67739 | 0.62267 | 0.054714 | 7.2672e-06 | 0
[13 empty] | 5:14 | 0.97811 | 0.91146 | 0 |  | 5:14 | 0 | 0 | 0 | 5:14 | 0.67797 | 0.62321 | 0.054761 | 7.2737e-06 | 0
[13 empty] | 5:15 | 0.96585 | 0.91146 | 0 |  | 5:15 | 0 | 0 | 0 | 5:15 | 0.67858 | 0.62376 | 0.054809 | 7.28e-06 | 0
[13 empty] | 5:15 | 0.95385 | 0.91146 | 0 |  | 5:15 | 0 | 0 | 0 | 5:15 | 0.67914 | 0.62428 | 0.054857 | 7.2861e-06 | 0
[13 empty] | 5:15 | 0.94209 | 0.91146 | 0 |  | 5:15 | 0 | 0 | 0 | 5:15 | 0.67972 | 0.62481 | 0.054903 | 7.2922e-06 | 0
[13 empty] | 5:16 | 0.93058 | 0.91146 | 0 |  | 5:16 | 0 | 0 | 0 | 5:16 | 0.68028 | 0.62533 | 0.054949 | 7.2983e-06 | 0
[13 empty] | 5:16 | 0.9193 | 0.91146 | 0 |  | 5:16 | 0 | 0 | 0 | 5:16 | 0.68084 | 0.62584 | 0.054992 | 7.3043e-06 | 0
[13 empty] | 5:16 | 0.90825 | 0.91146 | 0 |  | 5:16 | 0 | 0 | 0 | 5:16 | 0.68138 | 0.62634 | 0.055036 | 7.3102e-06 | 0
[13 empty] | 5:16 | 0.89743 | 0.91146 | 0 |  | 5:16 | 0 | 0 | 0 | 5:16 | 0.68192 | 0.62683 | 0.05508 | 7.3159e-06 | 0
[13 empty] | 5:17 | 0.88683 | 0.91146 | 0 |  | 5:17 | 0 | 0 | 0 | 5:17 | 0.68246 | 0.62733 | 0.055124 | 7.3216e-06 | 0
[13 empty] | 5:17 | 0.87645 | 0.91146 | 0 |  | 5:17 | 0 | 0 | 0 | 5:17 | 0.683 | 0.62783 | 0.055166 | 7.3274e-06 | 0
[13 empty] | 5:17 | 0.86628 | 0.91146 | 0 |  | 5:17 | 0 | 0 | 0 | 5:17 | 0.68352 | 0.62831 | 0.05521 | 7.3331e-06 | 0
[13 empty] | 5:17 | 0.85633 | 0.91146 | 0 |  | 5:17 | 0 | 0 | 0 | 5:17 | 0.68404 | 0.62878 | 0.055252 | 7.3386e-06 | 0
[13 empty] | 5:18 | 0.84657 | 0.91146 | 0 |  | 5:18 | 0 | 0 | 0 | 5:18 | 0.68456 | 0.62926 | 0.055292 | 7.3442e-06 | 0
[13 empty] | 5:18 | 0.83702 | 0.91146 | 0 |  | 5:18 | 0 | 0 | 0 | 5:18 | 0.68506 | 0.62972 | 0.055334 | 7.3495e-06 | 0
[13 empty] | 5:18 | 0.82766 | 0.91146 | 0 |  | 5:18 | 0 | 0 | 0 | 5:18 | 0.68556 | 0.63018 | 0.055374 | 7.3549e-06 | 0
[13 empty] | 5:18 | 0.8185 | 0.91146 | 0 |  | 5:18 | 0 | 0 | 0 | 5:18 | 0.68606 | 0.63064 | 0.055415 | 7.3602e-06 | 0
[13 empty] | 5:18 | 0.80952 | 0.91146 | 0 |  | 5:18 | 0 | 0 | 0 | 5:18 | 0.68656 | 0.63109 | 0.055455 | 7.3656e-06 | 0
[13 empty] | 5:19 | 0.80073 | 0.91146 | 0 |  | 5:19 | 0 | 0 | 0 | 5:19 | 0.68703 | 0.63153 | 0.055493 | 7.3707e-06 | 0
[13 empty] | 5:19 | 0.79211 | 0.91146 | 0 |  | 5:19 | 0 | 0 | 0 | 5:19 | 0.68751 | 0.63197 | 0.055531 | 7.3759e-06 | 0
[13 empty] | 5:19 | 0.78368 | 0.91146 | 0 |  | 5:19 | 0 | 0 | 0 | 5:19 | 0.68799 | 0.63241 | 0.055569 | 7.3808e-06 | 0
[13 empty] | 5:20 | 0.77542 | 0.91146 | 0 |  | 5:20 | 0 | 0 | 0 | 5:20 | 0.68845 | 0.63283 | 0.055607 | 7.386e-06 | 0
[13 empty] | 5:20 | 0.76733 | 0.91146 | 0 |  | 5:20 | 0 | 0 | 0 | 5:20 | 0.68892 | 0.63327 | 0.055646 | 7.391e-06 | 0
[13 empty] | 5:20 | 0.7594 | 0.91146 | 0 |  | 5:20 | 0 | 0 | 0 | 5:20 | 0.68938 | 0.63369 | 0.055682 | 7.3959e-06 | 0
[13 empty] | 5:20 | 0.75164 | 0.91146 | 0 |  | 5:20 | 0 | 0 | 0 | 5:20 | 0.68984 | 0.63411 | 0.05572 | 7.4007e-06 | 0
[13 empty] | 5:20 | 0.74403 | 0.91146 | 0 |  | 5:20 | 0 | 0 | 0 | 5:20 | 0.69028 | 0.63451 | 0.055756 | 7.4057e-06 | 0
[13 empty] | 5:21 | 0.73658 | 0.91146 | 0 |  | 5:21 | 0 | 0 | 0 | 5:21 | 0.69073 | 0.63493 | 0.055791 | 7.4104e-06 | 0
[13 empty] | 5:21 | 0.72929 | 0.91146 | 0 |  | 5:21 | 0 | 0 | 0 | 5:21 | 0.69117 | 0.63533 | 0.055827 | 7.415e-06 | 0
[13 empty] | 5:21 | 1.1629 | 0.91146 | 0 |  | 5:21 | 0 | 0 | 0 | 5:21 | 0.69187 | 0.63598 | 0.055884 | 7.4227e-06 | 0
[13 empty] | 5:22 | 1.1468 | 0.91146 | 0 |  | 5:22 | 0 | 0 | 0 | 5:22 | 0.69256 | 0.63661 | 0.05594 | 7.4301e-06 | 0
[13 empty] | 5:22 | 1.1311 | 0.91146 | 0 |  | 5:22 | 0 | 0 | 0 | 5:22 | 0.69325 | 0.63724 | 0.055995 | 7.4374e-06 | 0
[13 empty] | 5:22 | 1.1157 | 0.91146 | 0 |  | 5:22 | 0 | 0 | 0 | 5:22 | 0.69393 | 0.63787 | 0.056051 | 7.4446e-06 | 0
[13 empty] | 5:22 | 1.1006 | 0.91146 | 0 |  | 5:22 | 0 | 0 | 0 | 5:22 | 0.6946 | 0.63849 | 0.056104 | 7.4519e-06 | 0
[13 empty] | 5:22 | 1.0859 | 0.91146 | 0 |  | 5:22 | 0 | 0 | 0 | 5:22 | 0.69526 | 0.6391 | 0.056158 | 7.459e-06 | 0
[13 empty] | 5:23 | 1.0714 | 0.91146 | 0 |  | 5:23 | 0 | 0 | 0 | 5:23 | 0.6959 | 0.63969 | 0.056209 | 7.4658e-06 | 0
[13 empty] | 5:23 | 1.0572 | 0.91146 | 0 |  | 5:23 | 0 | 0 | 0 | 5:23 | 0.69655 | 0.64028 | 0.056261 | 7.4727e-06 | 0
[13 empty] | 5:23 | 1.0434 | 0.91146 | 0 |  | 5:23 | 0 | 0 | 0 | 5:23 | 0.69717 | 0.64085 | 0.056312 | 7.4796e-06 | 0
[13 empty] | 5:24 | 1.0298 | 0.91146 | 0 |  | 5:24 | 0 | 0 | 0 | 5:24 | 0.6978 | 0.64143 | 0.056362 | 7.4863e-06 | 0
[13 empty] | 5:24 | 1.0164 | 0.91146 | 0 |  | 5:24 | 0 | 0 | 0 | 5:24 | 0.69842 | 0.642 | 0.056412 | 7.4928e-06 | 0
[13 empty] | 5:24 | 1.0034 | 0.91146 | 0 |  | 5:24 | 0 | 0 | 0 | 5:24 | 0.69902 | 0.64255 | 0.056461 | 7.4993e-06 | 0
[13 empty] | 5:24 | 0.99062 | 0.91146 | 0 |  | 5:24 | 0 | 0 | 0 | 5:24 | 0.69962 | 0.64311 | 0.056509 | 7.5057e-06 | 0
[13 empty] | 5:24 | 0.97811 | 0.91146 | 0 |  | 5:24 | 0 | 0 | 0 | 5:24 | 0.70021 | 0.64364 | 0.056559 | 7.512e-06 | 0
[13 empty] | 5:25 | 0.96585 | 0.91146 | 0 |  | 5:25 | 0 | 0 | 0 | 5:25 | 0.70079 | 0.64418 | 0.056604 | 7.5184e-06 | 0
[13 empty] | 5:25 | 0.95385 | 0.91146 | 0 |  | 5:25 | 0 | 0 | 0 | 5:25 | 0.70137 | 0.64471 | 0.056652 | 7.5247e-06 | 0
[13 empty] | 5:25 | 0.94209 | 0.91146 | 0 |  | 5:25 | 0 | 0 | 0 | 5:25 | 0.70195 | 0.64525 | 0.056698 | 7.5308e-06 | 0
[13 empty] | 5:26 | 0.93058 | 0.91146 | 0 |  | 5:26 | 0 | 0 | 0 | 5:26 | 0.70251 | 0.64576 | 0.056744 | 7.5367e-06 | 0
[13 empty] | 5:26 | 0.9193 | 0.91146 | 0 |  | 5:26 | 0 | 0 | 0 | 5:26 | 0.70307 | 0.64628 | 0.056788 | 7.5428e-06 | 0
[13 empty] | 5:26 | 0.90825 | 0.91146 | 0 |  | 5:26 | 0 | 0 | 0 | 5:26 | 0.70361 | 0.64677 | 0.056832 | 7.5485e-06 | 0
[13 empty] | 5:26 | 0.89743 | 0.91146 | 0 |  | 5:26 | 0 | 0 | 0 | 5:26 | 0.70415 | 0.64727 | 0.056876 | 7.5544e-06 | 0
[13 empty] | 5:26 | 0.88683 | 0.91146 | 0 |  | 5:26 | 0 | 0 | 0 | 5:26 | 0.70469 | 0.64777 | 0.05692 | 7.5602e-06 | 0
[13 empty] | 5:27 | 0.87645 | 0.91146 | 0 |  | 5:27 | 0 | 0 | 0 | 5:27 | 0.70523 | 0.64826 | 0.056963 | 7.5659e-06 | 0
[13 empty] | 5:27 | 0.86628 | 0.91146 | 0 |  | 5:27 | 0 | 0 | 0 | 5:27 | 0.70575 | 0.64874 | 0.057005 | 7.5714e-06 | 0
[13 empty] | 5:27 | 0.85633 | 0.91146 | 0 |  | 5:27 | 0 | 0 | 0 | 5:27 | 0.70627 | 0.64922 | 0.057047 | 7.577e-06 | 0
[13 empty] | 5:28 | 0.84657 | 0.91146 | 0 |  | 5:28 | 0 | 0 | 0 | 5:28 | 0.70677 | 0.64968 | 0.057088 | 7.5825e-06 | 0
[13 empty] | 5:28 | 0.83702 | 0.91146 | 0 |  | 5:28 | 0 | 0 | 0 | 5:28 | 0.70729 | 0.65015 | 0.05713 | 7.5881e-06 | 0
[13 empty] | 5:28 | 0.82766 | 0.91146 | 0 |  | 5:28 | 0 | 0 | 0 | 5:28 | 0.70779 | 0.65061 | 0.05717 | 7.5934e-06 | 0
[13 empty] | 5:28 | 0.8185 | 0.91146 | 0 |  | 5:28 | 0 | 0 | 0 | 5:28 | 0.70829 | 0.65107 | 0.05721 | 7.5988e-06 | 0
[13 empty] | 5:28 | 0.80952 | 0.91146 | 0 |  | 5:28 | 0 | 0 | 0 | 5:28 | 0.70877 | 0.65151 | 0.05725 | 7.6039e-06 | 0
[13 empty] | 5:29 | 0.80073 | 0.91146 | 0 |  | 5:29 | 0 | 0 | 0 | 5:29 | 0.70926 | 0.65197 | 0.057288 | 7.6091e-06 | 0
[13 empty] | 5:29 | 0.79211 | 0.91146 | 0 |  | 5:29 | 0 | 0 | 0 | 5:29 | 0.70974 | 0.65241 | 0.057326 | 7.6142e-06 | 0
[13 empty] | 5:29 | 0.78368 | 0.91146 | 0 |  | 5:29 | 0 | 0 | 0 | 5:29 | 0.71022 | 0.65285 | 0.057365 | 7.6194e-06 | 0
[13 empty] | 5:30 | 0.77542 | 0.91146 | 0 |  | 5:30 | 0 | 0 | 0 | 5:30 | 0.71068 | 0.65327 | 0.057403 | 7.6243e-06 | 0
[13 empty] | 5:30 | 0.76733 | 0.91146 | 0 |  | 5:30 | 0 | 0 | 0 | 5:30 | 0.71116 | 0.65371 | 0.057441 | 7.6295e-06 | 0
[13 empty] | 5:30 | 0.7594 | 0.91146 | 0 |  | 5:30 | 0 | 0 | 0 | 5:30 | 0.71161 | 0.65413 | 0.057477 | 7.6343e-06 | 0
[13 empty] | 5:30 | 0.75164 | 0.91146 | 0 |  | 5:30 | 0 | 0 | 0 | 5:30 | 0.71207 | 0.65455 | 0.057515 | 7.6392e-06 | 0
[13 empty] | 5:30 | 0.74403 | 0.91146 | 0 |  | 5:30 | 0 | 0 | 0 | 5:30 | 0.71251 | 0.65495 | 0.057552 | 7.644e-06 | 0
[13 empty] | 5:31 | 0.73658 | 0.91146 | 0 |  | 5:31 | 0 | 0 | 0 | 5:31 | 0.71296 | 0.65537 | 0.057588 | 7.6488e-06 | 0
[13 empty] | 5:31 | 0.72929 | 0.91146 | 0 |  | 5:31 | 0 | 0 | 0 | 5:31 | 0.7134 | 0.65577 | 0.057622 | 7.6536e-06 | 0
[13 empty] | 5:31 | 1.1629 | 0.91146 | 0 |  | 5:31 | 0 | 0 | 0 | 5:31 | 0.71411 | 0.65642 | 0.05768 | 7.6612e-06 | 0
[13 empty] | 5:32 | 1.1468 | 0.91146 | 0 |  | 5:32 | 0 | 0 | 0 | 5:32 | 0.71479 | 0.65705 | 0.057735 | 7.6687e-06 | 0
[13 empty] | 5:32 | 1.1311 | 0.91146 | 0 |  | 5:32 | 0 | 0 | 0 | 5:32 | 0.71548 | 0.65768 | 0.05779 | 7.6759e-06 | 0
[13 empty] | 5:32 | 1.1157 | 0.91146 | 0 |  | 5:32 | 0 | 0 | 0 | 5:32 | 0.71616 | 0.65831 | 0.057846 | 7.6832e-06 | 0
[13 empty] | 5:32 | 1.1006 | 0.91146 | 0 |  | 5:32 | 0 | 0 | 0 | 5:32 | 0.71683 | 0.65892 | 0.057899 | 7.6902e-06 | 0
[13 empty] | 5:32 | 1.0859 | 0.91146 | 0 |  | 5:32 | 0 | 0 | 0 | 5:32 | 0.71747 | 0.65951 | 0.057953 | 7.6973e-06 | 0
[13 empty] | 5:33 | 1.0714 | 0.91146 | 0 |  | 5:33 | 0 | 0 | 0 | 5:33 | 0.71814 | 0.66012 | 0.058004 | 7.7044e-06 | 0
[13 empty] | 5:33 | 1.0572 | 0.91146 | 0 |  | 5:33 | 0 | 0 | 0 | 5:33 | 0.71876 | 0.6607 | 0.058056 | 7.7112e-06 | 0
[13 empty] | 5:33 | 1.0434 | 0.91146 | 0 |  | 5:33 | 0 | 0 | 0 | 5:33 | 0.7194 | 0.66129 | 0.058107 | 7.7179e-06 | 0
[13 empty] | 5:34 | 1.0298 | 0.91146 | 0 |  | 5:34 | 0 | 0 | 0 | 5:34 | 0.72003 | 0.66186 | 0.058157 | 7.7246e-06 | 0
[13 empty] | 5:34 | 1.0164 | 0.91146 | 0 |  | 5:34 | 0 | 0 | 0 | 5:34 | 0.72065 | 0.66243 | 0.058209 | 7.7313e-06 | 0
[13 empty] | 5:34 | 1.0034 | 0.91146 | 0 |  | 5:34 | 0 | 0 | 0 | 5:34 | 0.72125 | 0.66299 | 0.058256 | 7.7378e-06 | 0
[13 empty] | 5:34 | 0.99062 | 0.91146 | 0 |  | 5:34 | 0 | 0 | 0 | 5:34 | 0.72186 | 0.66354 | 0.058306 | 7.7443e-06 | 0
[13 empty] | 5:34 | 0.97811 | 0.91146 | 0 |  | 5:34 | 0 | 0 | 0 | 5:34 | 0.72244 | 0.66408 | 0.058354 | 7.7506e-06 | 0
[13 empty] | 5:35 | 0.96585 | 0.91146 | 0 |  | 5:35 | 0 | 0 | 0 | 5:35 | 0.72302 | 0.66461 | 0.0584 | 7.7569e-06 | 0
[13 empty] | 5:35 | 0.95385 | 0.91146 | 0 |  | 5:35 | 0 | 0 | 0 | 5:35 | 0.7236 | 0.66515 | 0.058447 | 7.763e-06 | 0
[13 empty] | 5:35 | 0.94209 | 0.91146 | 0 |  | 5:35 | 0 | 0 | 0 | 5:35 | 0.72418 | 0.66568 | 0.058493 | 7.7691e-06 | 0
[13 empty] | 5:36 | 0.93058 | 0.91146 | 0 |  | 5:36 | 0 | 0 | 0 | 5:36 | 0.72474 | 0.6662 | 0.058539 | 7.7752e-06 | 0
[13 empty] | 5:36 | 0.9193 | 0.91146 | 0 |  | 5:36 | 0 | 0 | 0 | 5:36 | 0.72528 | 0.66669 | 0.058583 | 7.7811e-06 | 0
[13 empty] | 5:36 | 0.90825 | 0.91146 | 0 |  | 5:36 | 0 | 0 | 0 | 5:36 | 0.72584 | 0.66721 | 0.058627 | 7.7871e-06 | 0
[13 empty] | 5:36 | 0.89743 | 0.91146 | 0 |  | 5:36 | 0 | 0 | 0 | 5:36 | 0.72638 | 0.66771 | 0.058671 | 7.793e-06 | 0
[13 empty] | 5:36 | 0.88683 | 0.91146 | 0 |  | 5:36 | 0 | 0 | 0 | 5:36 | 0.72693 | 0.6682 | 0.058715 | 7.7987e-06 | 0
[13 empty] | 5:37 | 0.87645 | 0.91146 | 0 |  | 5:37 | 0 | 0 | 0 | 5:37 | 0.72745 | 0.66868 | 0.058759 | 7.8044e-06 | 0
[13 empty] | 5:37 | 0.86628 | 0.91146 | 0 |  | 5:37 | 0 | 0 | 0 | 5:37 | 0.72799 | 0.66918 | 0.058801 | 7.81e-06 | 0
[13 empty] | 5:37 | 0.85633 | 0.91146 | 0 |  | 5:37 | 0 | 0 | 0 | 5:37 | 0.7285 | 0.66965 | 0.058843 | 7.8155e-06 | 0
[13 empty] | 5:38 | 0.84657 | 0.91146 | 0 |  | 5:38 | 0 | 0 | 0 | 5:38 | 0.729 | 0.67011 | 0.058883 | 7.8211e-06 | 0
[13 empty] | 5:38 | 0.83702 | 0.91146 | 0 |  | 5:38 | 0 | 0 | 0 | 5:38 | 0.72952 | 0.67059 | 0.058925 | 7.8264e-06 | 0
[13 empty] | 5:38 | 0.82766 | 0.91146 | 0 |  | 5:38 | 0 | 0 | 0 | 5:38 | 0.73002 | 0.67105 | 0.058965 | 7.832e-06 | 0
[13 empty] | 5:38 | 0.8185 | 0.91146 | 0 |  | 5:38 | 0 | 0 | 0 | 5:38 | 0.73052 | 0.67151 | 0.059005 | 7.8371e-06 | 0
[13 empty] | 5:38 | 0.80952 | 0.91146 | 0 |  | 5:38 | 0 | 0 | 0 | 5:38 | 0.731 | 0.67195 | 0.059045 | 7.8425e-06 | 0
[13 empty] | 5:39 | 0.80073 | 0.91146 | 0 |  | 5:39 | 0 | 0 | 0 | 5:39 | 0.7315 | 0.6724 | 0.059083 | 7.8476e-06 | 0
[13 empty] | 5:39 | 0.79211 | 0.91146 | 0 |  | 5:39 | 0 | 0 | 0 | 5:39 | 0.73197 | 0.67284 | 0.059122 | 7.8528e-06 | 0
[13 empty] | 5:39 | 0.78368 | 0.91146 | 0 |  | 5:39 | 0 | 0 | 0 | 5:39 | 0.73243 | 0.67326 | 0.059162 | 7.8579e-06 | 0
[13 empty] | 5:40 | 0.77542 | 0.91146 | 0 |  | 5:40 | 0 | 0 | 0 | 5:40 | 0.73291 | 0.6737 | 0.059198 | 7.8629e-06 | 0
[13 empty] | 5:40 | 0.76733 | 0.91146 | 0 |  | 5:40 | 0 | 0 | 0 | 5:40 | 0.73337 | 0.67412 | 0.059236 | 7.8679e-06 | 0
[13 empty] | 5:40 | 0.7594 | 0.91146 | 0 |  | 5:40 | 0 | 0 | 0 | 5:40 | 0.73384 | 0.67456 | 0.059272 | 7.8728e-06 | 0
[13 empty] | 5:40 | 0.75164 | 0.91146 | 0 |  | 5:40 | 0 | 0 | 0 | 5:40 | 0.73428 | 0.67496 | 0.059311 | 7.8778e-06 | 0
[13 empty] | 5:40 | 0.74403 | 0.91146 | 0 |  | 5:40 | 0 | 0 | 0 | 5:40 | 0.73474 | 0.67538 | 0.059347 | 7.8826e-06 | 0
[13 empty] | 5:41 | 0.73658 | 0.91146 | 0 |  | 5:41 | 0 | 0 | 0 | 5:41 | 0.73519 | 0.6758 | 0.059383 | 7.8873e-06 | 0
[13 empty] | 5:41 | 0.72929 | 0.91146 | 0 |  | 5:41 | 0 | 0 | 0 | 5:41 | 0.73563 | 0.6762 | 0.059418 | 7.8921e-06 | 0
[13 empty] | 5:41 | 1.1629 | 0.91146 | 0 |  | 5:41 | 0 | 0 | 0 | 5:41 | 0.73634 | 0.67685 | 0.059475 | 7.8996e-06 | 0
[13 empty] | 5:42 | 1.1468 | 0.91146 | 0 |  | 5:42 | 0 | 0 | 0 | 5:42 | 0.73702 | 0.67748 | 0.05953 | 7.907e-06 | 0
[13 empty] | 5:42 | 1.1311 | 0.91146 | 0 |  | 5:42 | 0 | 0 | 0 | 5:42 | 0.73771 | 0.67811 | 0.059586 | 7.9145e-06 | 0
[13 empty] | 5:42 | 1.1157 | 0.91146 | 0 |  | 5:42 | 0 | 0 | 0 | 5:42 | 0.73839 | 0.67874 | 0.059641 | 7.9217e-06 | 0
[13 empty] | 5:42 | 1.1006 | 0.91146 | 0 |  | 5:42 | 0 | 0 | 0 | 5:42 | 0.73906 | 0.67936 | 0.059695 | 7.9288e-06 | 0
[13 empty] | 5:42 | 1.0859 | 0.91146 | 0 |  | 5:42 | 0 | 0 | 0 | 5:42 | 0.7397 | 0.67995 | 0.059748 | 7.9358e-06 | 0
[13 empty] | 5:43 | 1.0714 | 0.91146 | 0 |  | 5:43 | 0 | 0 | 0 | 5:43 | 0.74037 | 0.68056 | 0.0598 | 7.9427e-06 | 0
[13 empty] | 5:43 | 1.0572 | 0.91146 | 0 |  | 5:43 | 0 | 0 | 0 | 5:43 | 0.74099 | 0.68113 | 0.059851 | 7.9496e-06 | 0
[13 empty] | 5:43 | 1.0434 | 0.91146 | 0 |  | 5:43 | 0 | 0 | 0 | 5:43 | 0.74163 | 0.68172 | 0.059903 | 7.9565e-06 | 0
[13 empty] | 5:44 | 1.0298 | 0.91146 | 0 |  | 5:44 | 0 | 0 | 0 | 5:44 | 0.74226 | 0.6823 | 0.059954 | 7.9632e-06 | 0
[13 empty] | 5:44 | 1.0164 | 0.91146 | 0 |  | 5:44 | 0 | 0 | 0 | 5:44 | 0.74286 | 0.68285 | 0.060004 | 7.9697e-06 | 0
[13 empty] | 5:44 | 1.0034 | 0.91146 | 0 |  | 5:44 | 0 | 0 | 0 | 5:44 | 0.74348 | 0.68342 | 0.060052 | 7.9763e-06 | 0
[13 empty] | 5:44 | 0.99062 | 0.91146 | 0 |  | 5:44 | 0 | 0 | 0 | 5:44 | 0.74407 | 0.68396 | 0.060101 | 7.9826e-06 | 0
[13 empty] | 5:44 | 0.97811 | 0.91146 | 0 |  | 5:44 | 0 | 0 | 0 | 5:44 | 0.74467 | 0.68451 | 0.060149 | 7.9891e-06 | 0
[13 empty] | 5:45 | 0.96585 | 0.91146 | 0 |  | 5:45 | 0 | 0 | 0 | 5:45 | 0.74525 | 0.68505 | 0.060195 | 7.9952e-06 | 0
[13 empty] | 5:45 | 0.95385 | 0.91146 | 0 |  | 5:45 | 0 | 0 | 0 | 5:45 | 0.74583 | 0.68558 | 0.060243 | 8.0015e-06 | 0
[13 empty] | 5:45 | 0.94209 | 0.91146 | 0 |  | 5:45 | 0 | 0 | 0 | 5:45 | 0.74639 | 0.6861 | 0.060289 | 8.0077e-06 | 0
[13 empty] | 5:46 | 0.93058 | 0.91146 | 0 |  | 5:46 | 0 | 0 | 0 | 5:46 | 0.74696 | 0.68661 | 0.060334 | 8.0138e-06 | 0
[13 empty] | 5:46 | 0.9193 | 0.91146 | 0 |  | 5:46 | 0 | 0 | 0 | 5:46 | 0.74752 | 0.68713 | 0.060378 | 8.0197e-06 | 0
[13 empty] | 5:46 | 0.90825 | 0.91146 | 0 |  | 5:46 | 0 | 0 | 0 | 5:46 | 0.74808 | 0.68764 | 0.060424 | 8.0256e-06 | 0
[13 empty] | 5:46 | 0.89743 | 0.91146 | 0 |  | 5:46 | 0 | 0 | 0 | 5:46 | 0.74862 | 0.68814 | 0.060468 | 8.0313e-06 | 0
[13 empty] | 5:46 | 0.88683 | 0.91146 | 0 |  | 5:46 | 0 | 0 | 0 | 5:46 | 0.74916 | 0.68864 | 0.06051 | 8.0371e-06 | 0
[13 empty] | 5:47 | 0.87645 | 0.91146 | 0 |  | 5:47 | 0 | 0 | 0 | 5:47 | 0.74968 | 0.68912 | 0.060554 | 8.0428e-06 | 0
[13 empty] | 5:47 | 0.86628 | 0.91146 | 0 |  | 5:47 | 0 | 0 | 0 | 5:47 | 0.7502 | 0.68959 | 0.060596 | 8.0485e-06 | 0
[13 empty] | 5:47 | 0.85633 | 0.91146 | 0 |  | 5:47 | 0 | 0 | 0 | 5:47 | 0.75072 | 0.69007 | 0.060638 | 8.0541e-06 | 0
[13 empty] | 5:48 | 0.84657 | 0.91146 | 0 |  | 5:48 | 0 | 0 | 0 | 5:48 | 0.75123 | 0.69055 | 0.060678 | 8.0596e-06 | 0
[13 empty] | 5:48 | 0.83702 | 0.91146 | 0 |  | 5:48 | 0 | 0 | 0 | 5:48 | 0.75173 | 0.69101 | 0.06072 | 8.065e-06 | 0
[13 empty] | 5:48 | 0.82766 | 0.91146 | 0 |  | 5:48 | 0 | 0 | 0 | 5:48 | 0.75225 | 0.69148 | 0.06076 | 8.0703e-06 | 0
[13 empty] | 5:48 | 0.8185 | 0.91146 | 0 |  | 5:48 | 0 | 0 | 0 | 5:48 | 0.75273 | 0.69192 | 0.0608 | 8.0756e-06 | 0
[13 empty] | 5:48 | 0.80952 | 0.91146 | 0 |  | 5:48 | 0 | 0 | 0 | 5:48 | 0.75323 | 0.69238 | 0.06084 | 8.081e-06 | 0
[13 empty] | 5:49 | 0.80073 | 0.91146 | 0 |  | 5:49 | 0 | 0 | 0 | 5:49 | 0.75371 | 0.69282 | 0.060879 | 8.0862e-06 | 0
[13 empty] | 5:49 | 0.79211 | 0.91146 | 0 |  | 5:49 | 0 | 0 | 0 | 5:49 | 0.75419 | 0.69326 | 0.060919 | 8.0913e-06 | 0
[13 empty] | 5:49 | 0.78368 | 0.91146 | 0 |  | 5:49 | 0 | 0 | 0 | 5:49 | 0.75466 | 0.6937 | 0.060957 | 8.0963e-06 | 0
[13 empty] | 5:50 | 0.77542 | 0.91146 | 0 |  | 5:50 | 0 | 0 | 0 | 5:50 | 0.75514 | 0.69414 | 0.060993 | 8.1014e-06 | 0
[13 empty] | 5:50 | 0.76733 | 0.91146 | 0 |  | 5:50 | 0 | 0 | 0 | 5:50 | 0.7556 | 0.69456 | 0.061031 | 8.1064e-06 | 0
[13 empty] | 5:50 | 0.7594 | 0.91146 | 0 |  | 5:50 | 0 | 0 | 0 | 5:50 | 0.75606 | 0.69498 | 0.06107 | 8.1114e-06 | 0
[13 empty] | 5:50 | 0.75164 | 0.91146 | 0 |  | 5:50 | 0 | 0 | 0 | 5:50 | 0.75651 | 0.6954 | 0.061106 | 8.1161e-06 | 0
[13 empty] | 5:50 | 0.74403 | 0.91146 | 0 |  | 5:50 | 0 | 0 | 0 | 5:50 | 0.75697 | 0.69582 | 0.061142 | 8.1209e-06 | 0
[13 empty] | 5:51 | 0.73658 | 0.91146 | 0 |  | 5:51 | 0 | 0 | 0 | 5:51 | 0.75741 | 0.69622 | 0.061179 | 8.1259e-06 | 0
[13 empty] | 5:51 | 0.72929 | 0.91146 | 0 |  | 5:51 | 0 | 0 | 0 | 5:51 | 0.75786 | 0.69664 | 0.061213 | 8.1305e-06 | 0
[13 empty] | 5:51 | 1.1629 | 0.91146 | 0 |  | 5:51 | 0 | 0 | 0 | 5:51 | 0.75857 | 0.69729 | 0.06127 | 8.1381e-06 | 0
[13 empty] | 5:52 | 1.1468 | 0.91146 | 0 |  | 5:52 | 0 | 0 | 0 | 5:52 | 0.75926 | 0.69792 | 0.061327 | 8.1455e-06 | 0
[13 empty] | 5:52 | 1.1311 | 0.91146 | 0 |  | 5:52 | 0 | 0 | 0 | 5:52 | 0.75994 | 0.69855 | 0.061383 | 8.1528e-06 | 0
[13 empty] | 5:52 | 1.1157 | 0.91146 | 0 |  | 5:52 | 0 | 0 | 0 | 5:52 | 0.76061 | 0.69916 | 0.061436 | 8.1601e-06 | 0
[13 empty] | 5:52 | 1.1006 | 0.91146 | 0 |  | 5:52 | 0 | 0 | 0 | 5:52 | 0.76129 | 0.69979 | 0.06149 | 8.1673e-06 | 0
[13 empty] | 5:52 | 1.0859 | 0.91146 | 0 |  | 5:52 | 0 | 0 | 0 | 5:52 | 0.76194 | 0.70038 | 0.061543 | 8.1744e-06 | 0
[13 empty] | 5:53 | 1.0714 | 0.91146 | 0 |  | 5:53 | 0 | 0 | 0 | 5:53 | 0.76258 | 0.70098 | 0.061595 | 8.1813e-06 | 0
[13 empty] | 5:53 | 1.0572 | 0.91146 | 0 |  | 5:53 | 0 | 0 | 0 | 5:53 | 0.76322 | 0.70157 | 0.061648 | 8.1881e-06 | 0
[13 empty] | 5:53 | 1.0434 | 0.91146 | 0 |  | 5:53 | 0 | 0 | 0 | 5:53 | 0.76387 | 0.70216 | 0.061698 | 8.195e-06 | 0
[13 empty] | 5:54 | 1.0298 | 0.91146 | 0 |  | 5:54 | 0 | 0 | 0 | 5:54 | 0.76449 | 0.70273 | 0.06175 | 8.2017e-06 | 0
[13 empty] | 5:54 | 1.0164 | 0.91146 | 0 |  | 5:54 | 0 | 0 | 0 | 5:54 | 0.76509 | 0.70329 | 0.061799 | 8.2082e-06 | 0
[13 empty] | 5:54 | 1.0034 | 0.91146 | 0 |  | 5:54 | 0 | 0 | 0 | 5:54 | 0.7657 | 0.70384 | 0.061847 | 8.2147e-06 | 0
[13 empty] | 5:54 | 0.99062 | 0.91146 | 0 |  | 5:54 | 0 | 0 | 0 | 5:54 | 0.7663 | 0.70439 | 0.061897 | 8.2212e-06 | 0
[13 empty] | 5:54 | 0.97811 | 0.91146 | 0 |  | 5:54 | 0 | 0 | 0 | 5:54 | 0.7669 | 0.70495 | 0.061944 | 8.2275e-06 | 0
[13 empty] | 5:55 | 0.96585 | 0.91146 | 0 |  | 5:55 | 0 | 0 | 0 | 5:55 | 0.76748 | 0.70548 | 0.06199 | 8.2338e-06 | 0
[13 empty] | 5:55 | 0.95385 | 0.91146 | 0 |  | 5:55 | 0 | 0 | 0 | 5:55 | 0.76806 | 0.70602 | 0.062038 | 8.2399e-06 | 0
[13 empty] | 5:55 | 0.94209 | 0.91146 | 0 |  | 5:55 | 0 | 0 | 0 | 5:55 | 0.76863 | 0.70653 | 0.062084 | 8.2462e-06 | 0
[13 empty] | 5:56 | 0.93058 | 0.91146 | 0 |  | 5:56 | 0 | 0 | 0 | 5:56 | 0.76919 | 0.70705 | 0.06213 | 8.2521e-06 | 0
[13 empty] | 5:56 | 0.9193 | 0.91146 | 0 |  | 5:56 | 0 | 0 | 0 | 5:56 | 0.76975 | 0.70756 | 0.062174 | 8.258e-06 | 0
[13 empty] | 5:56 | 0.90825 | 0.91146 | 0 |  | 5:56 | 0 | 0 | 0 | 5:56 | 0.77031 | 0.70808 | 0.062219 | 8.264e-06 | 0
[13 empty] | 5:56 | 0.89743 | 0.91146 | 0 |  | 5:56 | 0 | 0 | 0 | 5:56 | 0.77085 | 0.70858 | 0.062263 | 8.2699e-06 | 0
[13 empty] | 5:56 | 0.88683 | 0.91146 | 0 |  | 5:56 | 0 | 0 | 0 | 5:56 | 0.77139 | 0.70907 | 0.062305 | 8.2756e-06 | 0
[13 empty] | 5:57 | 0.87645 | 0.91146 | 0 |  | 5:57 | 0 | 0 | 0 | 5:57 | 0.77191 | 0.70955 | 0.062349 | 8.2813e-06 | 0
[13 empty] | 5:57 | 0.86628 | 0.91146 | 0 |  | 5:57 | 0 | 0 | 0 | 5:57 | 0.77243 | 0.71003 | 0.062391 | 8.2869e-06 | 0
[13 empty] | 5:57 | 0.85633 | 0.91146 | 0 |  | 5:57 | 0 | 0 | 0 | 5:57 | 0.77295 | 0.71051 | 0.062433 | 8.2924e-06 | 0
[13 empty] | 5:57 | 0.84657 | 0.91146 | 0 |  | 5:57 | 0 | 0 | 0 | 5:57 | 0.77347 | 0.71098 | 0.062475 | 8.298e-06 | 0
[13 empty] | 5:58 | 0.83702 | 0.91146 | 0 |  | 5:58 | 0 | 0 | 0 | 5:58 | 0.77397 | 0.71144 | 0.062515 | 8.3035e-06 | 0
[13 empty] | 5:58 | 0.82766 | 0.91146 | 0 |  | 5:58 | 0 | 0 | 0 | 5:58 | 0.77446 | 0.7119 | 0.062556 | 8.3088e-06 | 0
[13 empty] | 5:58 | 0.8185 | 0.91146 | 0 |  | 5:58 | 0 | 0 | 0 | 5:58 | 0.77496 | 0.71236 | 0.062596 | 8.3142e-06 | 0
[13 empty] | 5:58 | 0.80952 | 0.91146 | 0 |  | 5:58 | 0 | 0 | 0 | 5:58 | 0.77546 | 0.71282 | 0.062636 | 8.3193e-06 | 0
[13 empty] | 5:59 | 0.80073 | 0.91146 | 0 |  | 5:59 | 0 | 0 | 0 | 5:59 | 0.77594 | 0.71326 | 0.062674 | 8.3245e-06 | 0
[13 empty] | 5:59 | 0.79211 | 0.91146 | 0 |  | 5:59 | 0 | 0 | 0 | 5:59 | 0.77642 | 0.7137 | 0.062714 | 8.3297e-06 | 0
[13 empty] | 5:59 | 0.78368 | 0.91146 | 0 |  | 5:59 | 0 | 0 | 0 | 5:59 | 0.7769 | 0.71413 | 0.062752 | 8.3348e-06 | 0
[13 empty] | 6:00 | 0.77542 | 0.91146 | 0 |  | 6:00 | 0 | 0 | 0 | 6:00 | 0.77737 | 0.71457 | 0.06279 | 8.3398e-06 | 0
[13 empty] | 6:00 | 0.76733 | 0.91146 | 0 |  | 6:00 | 0 | 0 | 0 | 6:00 | 0.77783 | 0.71499 | 0.062827 | 8.3447e-06 | 0
[13 empty] | 6:00 | 0.7594 | 0.91146 | 0 |  | 6:00 | 0 | 0 | 0 | 6:00 | 0.77829 | 0.71541 | 0.062865 | 8.3497e-06 | 0
[13 empty] | 6:00 | 0.75164 | 0.91146 | 0 |  | 6:00 | 0 | 0 | 0 | 6:00 | 0.77874 | 0.71583 | 0.062901 | 8.3547e-06 | 0
[13 empty] | 6:00 | 0.74403 | 0.91146 | 0 |  | 6:00 | 0 | 0 | 0 | 6:00 | 0.7792 | 0.71625 | 0.062938 | 8.3595e-06 | 0
[13 empty] | 6:01 | 0.73658 | 0.91146 | 0 |  | 6:01 | 0 | 0 | 0 | 6:01 | 0.77964 | 0.71666 | 0.062974 | 8.3642e-06 | 0
[13 empty] | 6:01 | 0.72929 | 0.91146 | 0 |  | 6:01 | 0 | 0 | 0 | 6:01 | 0.78009 | 0.71708 | 0.063008 | 8.369e-06 | 0
[13 empty] | 6:01 | 1.1629 | 0.91146 | 0 |  | 6:01 | 0 | 0 | 0 | 6:01 | 0.78078 | 0.71771 | 0.063065 | 8.3766e-06 | 0
[13 empty] | 6:02 | 1.1468 | 0.91146 | 0 |  | 6:02 | 0 | 0 | 0 | 6:02 | 0.78149 | 0.71836 | 0.063123 | 8.3841e-06 | 0
[13 empty] | 6:02 | 1.1311 | 0.91146 | 0 |  | 6:02 | 0 | 0 | 0 | 6:02 | 0.78217 | 0.71899 | 0.063178 | 8.3913e-06 | 0
[13 empty] | 6:02 | 1.1157 | 0.91146 | 0 |  | 6:02 | 0 | 0 | 0 | 6:02 | 0.78284 | 0.7196 | 0.063232 | 8.3986e-06 | 0
[13 empty] | 6:02 | 1.1006 | 0.91146 | 0 |  | 6:02 | 0 | 0 | 0 | 6:02 | 0.7835 | 0.72021 | 0.063285 | 8.4057e-06 | 0
[13 empty] | 6:02 | 1.0859 | 0.91146 | 0 |  | 6:02 | 0 | 0 | 0 | 6:02 | 0.78417 | 0.72082 | 0.063339 | 8.4127e-06 | 0
[13 empty] | 6:03 | 1.0714 | 0.91146 | 0 |  | 6:03 | 0 | 0 | 0 | 6:03 | 0.78481 | 0.72141 | 0.063392 | 8.4198e-06 | 0
[13 empty] | 6:03 | 1.0572 | 0.91146 | 0 |  | 6:03 | 0 | 0 | 0 | 6:03 | 0.78546 | 0.722 | 0.063444 | 8.4267e-06 | 0
[13 empty] | 6:03 | 1.0434 | 0.91146 | 0 |  | 6:03 | 0 | 0 | 0 | 6:03 | 0.78608 | 0.72258 | 0.063493 | 8.4334e-06 | 0
[13 empty] | 6:04 | 1.0298 | 0.91146 | 0 |  | 6:04 | 0 | 0 | 0 | 6:04 | 0.7867 | 0.72315 | 0.063545 | 8.4401e-06 | 0
[13 empty] | 6:04 | 1.0164 | 0.91146 | 0 |  | 6:04 | 0 | 0 | 0 | 6:04 | 0.78733 | 0.72372 | 0.063594 | 8.4467e-06 | 0
[13 empty] | 6:04 | 1.0034 | 0.91146 | 0 |  | 6:04 | 0 | 0 | 0 | 6:04 | 0.78793 | 0.72428 | 0.063642 | 8.4532e-06 | 0
[13 empty] | 6:04 | 0.99062 | 0.91146 | 0 |  | 6:04 | 0 | 0 | 0 | 6:04 | 0.78853 | 0.72483 | 0.063692 | 8.4597e-06 | 0
[13 empty] | 6:04 | 0.97811 | 0.91146 | 0 |  | 6:04 | 0 | 0 | 0 | 6:04 | 0.78913 | 0.72538 | 0.06374 | 8.466e-06 | 0
[13 empty] | 6:05 | 0.96585 | 0.91146 | 0 |  | 6:05 | 0 | 0 | 0 | 6:05 | 0.78971 | 0.72592 | 0.063787 | 8.4723e-06 | 0
[13 empty] | 6:05 | 0.95385 | 0.91146 | 0 |  | 6:05 | 0 | 0 | 0 | 6:05 | 0.79029 | 0.72645 | 0.063833 | 8.4784e-06 | 0
[13 empty] | 6:05 | 0.94209 | 0.91146 | 0 |  | 6:05 | 0 | 0 | 0 | 6:05 | 0.79086 | 0.72697 | 0.063879 | 8.4845e-06 | 0
[13 empty] | 6:06 | 0.93058 | 0.91146 | 0 |  | 6:06 | 0 | 0 | 0 | 6:06 | 0.79142 | 0.72748 | 0.063925 | 8.4907e-06 | 0
[13 empty] | 6:06 | 0.9193 | 0.91146 | 0 |  | 6:06 | 0 | 0 | 0 | 6:06 | 0.79198 | 0.728 | 0.063969 | 8.4966e-06 | 0
[13 empty] | 6:06 | 0.90825 | 0.91146 | 0 |  | 6:06 | 0 | 0 | 0 | 6:06 | 0.79252 | 0.7285 | 0.064015 | 8.5025e-06 | 0
[13 empty] | 6:06 | 0.89743 | 0.91146 | 0 |  | 6:06 | 0 | 0 | 0 | 6:06 | 0.79308 | 0.72901 | 0.064059 | 8.5082e-06 | 0
[13 empty] | 6:06 | 0.88683 | 0.91146 | 0 |  | 6:06 | 0 | 0 | 0 | 6:06 | 0.7936 | 0.72949 | 0.064101 | 8.5142e-06 | 0
[13 empty] | 6:07 | 0.87645 | 0.91146 | 0 |  | 6:07 | 0 | 0 | 0 | 6:07 | 0.79414 | 0.72999 | 0.064145 | 8.5197e-06 | 0
[13 empty] | 6:07 | 0.86628 | 0.91146 | 0 |  | 6:07 | 0 | 0 | 0 | 6:07 | 0.79466 | 0.73046 | 0.064187 | 8.5254e-06 | 0
[13 empty] | 6:07 | 0.85633 | 0.91146 | 0 |  | 6:07 | 0 | 0 | 0 | 6:07 | 0.79518 | 0.73094 | 0.064229 | 8.531e-06 | 0
[13 empty] | 6:08 | 0.84657 | 0.91146 | 0 |  | 6:08 | 0 | 0 | 0 | 6:08 | 0.7957 | 0.73142 | 0.064271 | 8.5365e-06 | 0
[13 empty] | 6:08 | 0.83702 | 0.91146 | 0 |  | 6:08 | 0 | 0 | 0 | 6:08 | 0.7962 | 0.73188 | 0.064311 | 8.5418e-06 | 0
[13 empty] | 6:08 | 0.82766 | 0.91146 | 0 |  | 6:08 | 0 | 0 | 0 | 6:08 | 0.79669 | 0.73234 | 0.064351 | 8.5472e-06 | 0
[13 empty] | 6:08 | 0.8185 | 0.91146 | 0 |  | 6:08 | 0 | 0 | 0 | 6:08 | 0.79719 | 0.73279 | 0.064391 | 8.5525e-06 | 0
[13 empty] | 6:08 | 0.80952 | 0.91146 | 0 |  | 6:08 | 0 | 0 | 0 | 6:08 | 0.79769 | 0.73325 | 0.064431 | 8.5579e-06 | 0
[13 empty] | 6:09 | 0.80073 | 0.91146 | 0 |  | 6:09 | 0 | 0 | 0 | 6:09 | 0.79817 | 0.73369 | 0.064469 | 8.563e-06 | 0
[13 empty] | 6:09 | 0.79211 | 0.91146 | 0 |  | 6:09 | 0 | 0 | 0 | 6:09 | 0.79865 | 0.73413 | 0.064509 | 8.5682e-06 | 0
[13 empty] | 6:09 | 0.78368 | 0.91146 | 0 |  | 6:09 | 0 | 0 | 0 | 6:09 | 0.79913 | 0.73457 | 0.064548 | 8.5734e-06 | 0
[13 empty] | 6:09 | 0.77542 | 0.91146 | 0 |  | 6:09 | 0 | 0 | 0 | 6:09 | 0.7996 | 0.73501 | 0.064586 | 8.5783e-06 | 0
[13 empty] | 6:10 | 0.76733 | 0.91146 | 0 |  | 6:10 | 0 | 0 | 0 | 6:10 | 0.80006 | 0.73543 | 0.064622 | 8.5833e-06 | 0
[13 empty] | 6:10 | 0.7594 | 0.91146 | 0 |  | 6:10 | 0 | 0 | 0 | 6:10 | 0.80052 | 0.73585 | 0.06466 | 8.5883e-06 | 0
[13 empty] | 6:10 | 0.75164 | 0.91146 | 0 |  | 6:10 | 0 | 0 | 0 | 6:10 | 0.80097 | 0.73627 | 0.064696 | 8.593e-06 | 0
[13 empty] | 6:10 | 0.74403 | 0.91146 | 0 |  | 6:10 | 0 | 0 | 0 | 6:10 | 0.80143 | 0.73669 | 0.064733 | 8.598e-06 | 0
[13 empty] | 6:11 | 0.73658 | 0.91146 | 0 |  | 6:11 | 0 | 0 | 0 | 6:11 | 0.80187 | 0.73709 | 0.064769 | 8.6028e-06 | 0
[13 empty] | 6:11 | 0.72929 | 0.91146 | 0 |  | 6:11 | 0 | 0 | 0 | 6:11 | 0.80231 | 0.73749 | 0.064805 | 8.6075e-06 | 0
[13 empty] | 6:11 | 1.1629 | 0.91146 | 0 |  | 6:11 | 0 | 0 | 0 | 6:11 | 0.80301 | 0.73814 | 0.064861 | 8.615e-06 | 0
[13 empty] | 6:11 | 1.1468 | 0.91146 | 0 |  | 6:11 | 0 | 0 | 0 | 6:11 | 0.80372 | 0.73879 | 0.064918 | 8.6224e-06 | 0
[13 empty] | 6:12 | 1.1311 | 0.91146 | 0 |  | 6:12 | 0 | 0 | 0 | 6:12 | 0.8044 | 0.73942 | 0.064973 | 8.6299e-06 | 0
[13 empty] | 6:12 | 1.1157 | 0.91146 | 0 |  | 6:12 | 0 | 0 | 0 | 6:12 | 0.80507 | 0.74003 | 0.065027 | 8.6371e-06 | 0
[13 empty] | 6:12 | 1.1006 | 0.91146 | 0 |  | 6:12 | 0 | 0 | 0 | 6:12 | 0.80573 | 0.74064 | 0.06508 | 8.6442e-06 | 0
[13 empty] | 6:12 | 1.0859 | 0.91146 | 0 |  | 6:12 | 0 | 0 | 0 | 6:12 | 0.8064 | 0.74125 | 0.065134 | 8.6513e-06 | 0
[13 empty] | 6:13 | 1.0714 | 0.91146 | 0 |  | 6:13 | 0 | 0 | 0 | 6:13 | 0.80704 | 0.74185 | 0.065187 | 8.6582e-06 | 0
[13 empty] | 6:13 | 1.0572 | 0.91146 | 0 |  | 6:13 | 0 | 0 | 0 | 6:13 | 0.80769 | 0.74244 | 0.065239 | 8.665e-06 | 0
[13 empty] | 6:13 | 1.0434 | 0.91146 | 0 |  | 6:13 | 0 | 0 | 0 | 6:13 | 0.80831 | 0.74301 | 0.065289 | 8.6719e-06 | 0
[13 empty] | 6:13 | 1.0298 | 0.91146 | 0 |  | 6:13 | 0 | 0 | 0 | 6:13 | 0.80893 | 0.74358 | 0.06534 | 8.6786e-06 | 0
[13 empty] | 6:14 | 1.0164 | 0.91146 | 0 |  | 6:14 | 0 | 0 | 0 | 6:14 | 0.80956 | 0.74416 | 0.06539 | 8.6851e-06 | 0
[13 empty] | 6:14 | 1.0034 | 0.91146 | 0 |  | 6:14 | 0 | 0 | 0 | 6:14 | 0.81016 | 0.74471 | 0.065439 | 8.6918e-06 | 0
[13 empty] | 6:14 | 0.99062 | 0.91146 | 0 |  | 6:14 | 0 | 0 | 0 | 6:14 | 0.81076 | 0.74527 | 0.065487 | 8.6981e-06 | 0
[13 empty] | 6:14 | 0.97811 | 0.91146 | 0 |  | 6:14 | 0 | 0 | 0 | 6:14 | 0.81134 | 0.7458 | 0.065535 | 8.7044e-06 | 0
[13 empty] | 6:15 | 0.96585 | 0.91146 | 0 |  | 6:15 | 0 | 0 | 0 | 6:15 | 0.81195 | 0.74635 | 0.065583 | 8.7107e-06 | 0
[13 empty] | 6:15 | 0.95385 | 0.91146 | 0 |  | 6:15 | 0 | 0 | 0 | 6:15 | 0.81251 | 0.74687 | 0.065628 | 8.717e-06 | 0
[13 empty] | 6:15 | 0.94209 | 0.91146 | 0 |  | 6:15 | 0 | 0 | 0 | 6:15 | 0.81309 | 0.7474 | 0.065674 | 8.7231e-06 | 0
[13 empty] | 6:16 | 0.93058 | 0.91146 | 0 |  | 6:16 | 0 | 0 | 0 | 6:16 | 0.81365 | 0.74792 | 0.06572 | 8.729e-06 | 0
[13 empty] | 6:16 | 0.9193 | 0.91146 | 0 |  | 6:16 | 0 | 0 | 0 | 6:16 | 0.81421 | 0.74844 | 0.065766 | 8.7351e-06 | 0
[13 empty] | 6:16 | 0.90825 | 0.91146 | 0 |  | 6:16 | 0 | 0 | 0 | 6:16 | 0.81475 | 0.74893 | 0.06581 | 8.741e-06 | 0
[13 empty] | 6:16 | 0.89743 | 0.91146 | 0 |  | 6:16 | 0 | 0 | 0 | 6:16 | 0.81529 | 0.74943 | 0.065854 | 8.7468e-06 | 0
[13 empty] | 6:16 | 0.88683 | 0.91146 | 0 |  | 6:16 | 0 | 0 | 0 | 6:16 | 0.81583 | 0.74993 | 0.065896 | 8.7525e-06 | 0
[13 empty] | 6:17 | 0.87645 | 0.91146 | 0 |  | 6:17 | 0 | 0 | 0 | 6:17 | 0.81637 | 0.75042 | 0.06594 | 8.7582e-06 | 0
[13 empty] | 6:17 | 0.86628 | 0.91146 | 0 |  | 6:17 | 0 | 0 | 0 | 6:17 | 0.81689 | 0.7509 | 0.065982 | 8.764e-06 | 0
[13 empty] | 6:17 | 0.85633 | 0.91146 | 0 |  | 6:17 | 0 | 0 | 0 | 6:17 | 0.81741 | 0.75138 | 0.066024 | 8.7695e-06 | 0
[13 empty] | 6:18 | 0.84657 | 0.91146 | 0 |  | 6:18 | 0 | 0 | 0 | 6:18 | 0.81793 | 0.75185 | 0.066066 | 8.7748e-06 | 0
[13 empty] | 6:18 | 0.83702 | 0.91146 | 0 |  | 6:18 | 0 | 0 | 0 | 6:18 | 0.81843 | 0.75231 | 0.066106 | 8.7804e-06 | 0
[13 empty] | 6:18 | 0.82766 | 0.91146 | 0 |  | 6:18 | 0 | 0 | 0 | 6:18 | 0.81893 | 0.75277 | 0.066146 | 8.7857e-06 | 0
[13 empty] | 6:18 | 0.8185 | 0.91146 | 0 |  | 6:18 | 0 | 0 | 0 | 6:18 | 0.81942 | 0.75323 | 0.066186 | 8.7911e-06 | 0
[13 empty] | 6:18 | 0.80952 | 0.91146 | 0 |  | 6:18 | 0 | 0 | 0 | 6:18 | 0.81992 | 0.75369 | 0.066226 | 8.7962e-06 | 0
[13 empty] | 6:19 | 0.80073 | 0.91146 | 0 |  | 6:19 | 0 | 0 | 0 | 6:19 | 0.8204 | 0.75413 | 0.066266 | 8.8016e-06 | 0
[13 empty] | 6:19 | 0.79211 | 0.91146 | 0 |  | 6:19 | 0 | 0 | 0 | 6:19 | 0.82088 | 0.75457 | 0.066305 | 8.8067e-06 | 0
[13 empty] | 6:19 | 0.78368 | 0.91146 | 0 |  | 6:19 | 0 | 0 | 0 | 6:19 | 0.82136 | 0.75501 | 0.066343 | 8.8117e-06 | 0
[13 empty] | 6:20 | 0.77542 | 0.91146 | 0 |  | 6:20 | 0 | 0 | 0 | 6:20 | 0.82182 | 0.75543 | 0.066381 | 8.8169e-06 | 0
[13 empty] | 6:20 | 0.76733 | 0.91146 | 0 |  | 6:20 | 0 | 0 | 0 | 6:20 | 0.82229 | 0.75587 | 0.066417 | 8.8218e-06 | 0
[13 empty] | 6:20 | 0.7594 | 0.91146 | 0 |  | 6:20 | 0 | 0 | 0 | 6:20 | 0.82275 | 0.75629 | 0.066455 | 8.8268e-06 | 0
[13 empty] | 6:20 | 0.75164 | 0.91146 | 0 |  | 6:20 | 0 | 0 | 0 | 6:20 | 0.82321 | 0.75671 | 0.066492 | 8.8316e-06 | 0
[13 empty] | 6:20 | 0.74403 | 0.91146 | 0 |  | 6:20 | 0 | 0 | 0 | 6:20 | 0.82364 | 0.75711 | 0.066528 | 8.8363e-06 | 0
[13 empty] | 6:21 | 0.73658 | 0.91146 | 0 |  | 6:21 | 0 | 0 | 0 | 6:21 | 0.8241 | 0.75753 | 0.066564 | 8.8411e-06 | 0
[13 empty] | 6:21 | 0.72929 | 0.91146 | 0 |  | 6:21 | 0 | 0 | 0 | 6:21 | 0.82454 | 0.75793 | 0.066601 | 8.8459e-06 | 0
[13 empty] | 6:21 | 1.1629 | 0.91146 | 0 |  | 6:21 | 0 | 0 | 0 | 6:21 | 0.82524 | 0.75858 | 0.066656 | 8.8535e-06 | 0
[13 empty] | 6:22 | 1.1468 | 0.91146 | 0 |  | 6:22 | 0 | 0 | 0 | 6:22 | 0.82595 | 0.75923 | 0.066713 | 8.861e-06 | 0
[13 empty] | 6:22 | 1.1311 | 0.91146 | 0 |  | 6:22 | 0 | 0 | 0 | 6:22 | 0.82662 | 0.75984 | 0.066769 | 8.8682e-06 | 0
[13 empty] | 6:22 | 1.1157 | 0.91146 | 0 |  | 6:22 | 0 | 0 | 0 | 6:22 | 0.8273 | 0.76047 | 0.066822 | 8.8755e-06 | 0
[13 empty] | 6:22 | 1.1006 | 0.91146 | 0 |  | 6:22 | 0 | 0 | 0 | 6:22 | 0.82796 | 0.76108 | 0.066876 | 8.8828e-06 | 0
[13 empty] | 6:22 | 1.0859 | 0.91146 | 0 |  | 6:22 | 0 | 0 | 0 | 6:22 | 0.82863 | 0.76169 | 0.066929 | 8.8898e-06 | 0
[13 empty] | 6:23 | 1.0714 | 0.91146 | 0 |  | 6:23 | 0 | 0 | 0 | 6:23 | 0.82927 | 0.76228 | 0.066983 | 8.8967e-06 | 0
[13 empty] | 6:23 | 1.0572 | 0.91146 | 0 |  | 6:23 | 0 | 0 | 0 | 6:23 | 0.82992 | 0.76287 | 0.067034 | 8.9036e-06 | 0
[13 empty] | 6:23 | 1.0434 | 0.91146 | 0 |  | 6:23 | 0 | 0 | 0 | 6:23 | 0.83054 | 0.76345 | 0.067086 | 8.9103e-06 | 0
[13 empty] | 6:24 | 1.0298 | 0.91146 | 0 |  | 6:24 | 0 | 0 | 0 | 6:24 | 0.83116 | 0.76402 | 0.067135 | 8.9169e-06 | 0
[13 empty] | 6:24 | 1.0164 | 0.91146 | 0 |  | 6:24 | 0 | 0 | 0 | 6:24 | 0.83179 | 0.76459 | 0.067185 | 8.9236e-06 | 0
[13 empty] | 6:24 | 1.0034 | 0.91146 | 0 |  | 6:24 | 0 | 0 | 0 | 6:24 | 0.83239 | 0.76515 | 0.067235 | 8.9301e-06 | 0
[13 empty] | 6:24 | 0.99062 | 0.91146 | 0 |  | 6:24 | 0 | 0 | 0 | 6:24 | 0.83299 | 0.7657 | 0.067282 | 8.9366e-06 | 0
[13 empty] | 6:24 | 0.97811 | 0.91146 | 0 |  | 6:24 | 0 | 0 | 0 | 6:24 | 0.83357 | 0.76624 | 0.06733 | 8.9429e-06 | 0
[13 empty] | 6:25 | 0.96585 | 0.91146 | 0 |  | 6:25 | 0 | 0 | 0 | 6:25 | 0.83416 | 0.76677 | 0.067378 | 8.9492e-06 | 0
[13 empty] | 6:25 | 0.95385 | 0.91146 | 0 |  | 6:25 | 0 | 0 | 0 | 6:25 | 0.83474 | 0.76731 | 0.067424 | 8.9553e-06 | 0
[13 empty] | 6:25 | 0.94209 | 0.91146 | 0 |  | 6:25 | 0 | 0 | 0 | 6:25 | 0.83532 | 0.76784 | 0.06747 | 8.9614e-06 | 0
[13 empty] | 6:26 | 0.93058 | 0.91146 | 0 |  | 6:26 | 0 | 0 | 0 | 6:26 | 0.83588 | 0.76836 | 0.067515 | 8.9676e-06 | 0
[13 empty] | 6:26 | 0.9193 | 0.91146 | 0 |  | 6:26 | 0 | 0 | 0 | 6:26 | 0.83644 | 0.76887 | 0.067561 | 8.9735e-06 | 0
[13 empty] | 6:26 | 0.90825 | 0.91146 | 0 |  | 6:26 | 0 | 0 | 0 | 6:26 | 0.83698 | 0.76937 | 0.067605 | 8.9794e-06 | 0
[13 empty] | 6:26 | 0.89743 | 0.91146 | 0 |  | 6:26 | 0 | 0 | 0 | 6:26 | 0.83752 | 0.76986 | 0.067649 | 8.9853e-06 | 0
[13 empty] | 6:26 | 0.88683 | 0.91146 | 0 |  | 6:26 | 0 | 0 | 0 | 6:26 | 0.83806 | 0.77036 | 0.067693 | 8.991e-06 | 0
[13 empty] | 6:27 | 0.87645 | 0.91146 | 0 |  | 6:27 | 0 | 0 | 0 | 6:27 | 0.8386 | 0.77086 | 0.067735 | 8.9968e-06 | 0
[13 empty] | 6:27 | 0.86628 | 0.91146 | 0 |  | 6:27 | 0 | 0 | 0 | 6:27 | 0.83912 | 0.77133 | 0.067777 | 9.0023e-06 | 0
[13 empty] | 6:27 | 0.85633 | 0.91146 | 0 |  | 6:27 | 0 | 0 | 0 | 6:27 | 0.83964 | 0.77181 | 0.067819 | 9.0079e-06 | 0
[13 empty] | 6:28 | 0.84657 | 0.91146 | 0 |  | 6:28 | 0 | 0 | 0 | 6:28 | 0.84014 | 0.77227 | 0.067861 | 9.0134e-06 | 0
[13 empty] | 6:28 | 0.83702 | 0.91146 | 0 |  | 6:28 | 0 | 0 | 0 | 6:28 | 0.84066 | 0.77275 | 0.067901 | 9.0189e-06 | 0
[13 empty] | 6:28 | 0.82766 | 0.91146 | 0 |  | 6:28 | 0 | 0 | 0 | 6:28 | 0.84116 | 0.77321 | 0.067941 | 9.0243e-06 | 0
[13 empty] | 6:28 | 0.8185 | 0.91146 | 0 |  | 6:28 | 0 | 0 | 0 | 6:28 | 0.84166 | 0.77366 | 0.067981 | 9.0296e-06 | 0
[13 empty] | 6:28 | 0.80952 | 0.91146 | 0 |  | 6:28 | 0 | 0 | 0 | 6:28 | 0.84213 | 0.7741 | 0.068022 | 9.0348e-06 | 0
[13 empty] | 6:29 | 0.80073 | 0.91146 | 0 |  | 6:29 | 0 | 0 | 0 | 6:29 | 0.84263 | 0.77456 | 0.068062 | 9.0399e-06 | 0
[13 empty] | 6:29 | 0.79211 | 0.91146 | 0 |  | 6:29 | 0 | 0 | 0 | 6:29 | 0.84311 | 0.775 | 0.0681 | 9.0451e-06 | 0
[13 empty] | 6:29 | 0.78368 | 0.91146 | 0 |  | 6:29 | 0 | 0 | 0 | 6:29 | 0.84359 | 0.77544 | 0.068138 | 9.0503e-06 | 0
[13 empty] | 6:30 | 0.77542 | 0.91146 | 0 |  | 6:30 | 0 | 0 | 0 | 6:30 | 0.84405 | 0.77586 | 0.068176 | 9.0552e-06 | 0
[13 empty] | 6:30 | 0.76733 | 0.91146 | 0 |  | 6:30 | 0 | 0 | 0 | 6:30 | 0.84452 | 0.7763 | 0.068213 | 9.0602e-06 | 0
[13 empty] | 6:30 | 0.7594 | 0.91146 | 0 |  | 6:30 | 0 | 0 | 0 | 6:30 | 0.84498 | 0.77672 | 0.068251 | 9.0651e-06 | 0
[13 empty] | 6:30 | 0.75164 | 0.91146 | 0 |  | 6:30 | 0 | 0 | 0 | 6:30 | 0.84544 | 0.77714 | 0.068287 | 9.0701e-06 | 0
[13 empty] | 6:30 | 0.74403 | 0.91146 | 0 |  | 6:30 | 0 | 0 | 0 | 6:30 | 0.84587 | 0.77754 | 0.068323 | 9.0749e-06 | 0
[13 empty] | 6:31 | 0.73658 | 0.91146 | 0 |  | 6:31 | 0 | 0 | 0 | 6:31 | 0.84633 | 0.77796 | 0.06836 | 9.0797e-06 | 0
[13 empty] | 6:31 | 0.72929 | 0.91146 | 0 |  | 6:31 | 0 | 0 | 0 | 6:31 | 0.84677 | 0.77836 | 0.068396 | 9.0844e-06 | 0
[13 empty] | 6:31 | 1.1629 | 0.91146 | 0 |  | 6:31 | 0 | 0 | 0 | 6:31 | 0.84747 | 0.77901 | 0.068451 | 9.0919e-06 | 0
[13 empty] | 6:32 | 1.1468 | 0.91146 | 0 |  | 6:32 | 0 | 0 | 0 | 6:32 | 0.84816 | 0.77964 | 0.068509 | 9.0993e-06 | 0
[13 empty] | 6:32 | 1.1311 | 0.91146 | 0 |  | 6:32 | 0 | 0 | 0 | 6:32 | 0.84885 | 0.78027 | 0.068564 | 9.1068e-06 | 0
[13 empty] | 6:32 | 1.1157 | 0.91146 | 0 |  | 6:32 | 0 | 0 | 0 | 6:32 | 0.84953 | 0.7809 | 0.068617 | 9.114e-06 | 0
[13 empty] | 6:32 | 1.1006 | 0.91146 | 0 |  | 6:32 | 0 | 0 | 0 | 6:32 | 0.8502 | 0.78151 | 0.068673 | 9.1211e-06 | 0
[13 empty] | 6:33 | 1.0859 | 0.91146 | 0 |  | 6:33 | 0 | 0 | 0 | 6:33 | 0.85086 | 0.78213 | 0.068724 | 9.1282e-06 | 0
[13 empty] | 6:33 | 1.0714 | 0.91146 | 0 |  | 6:33 | 0 | 0 | 0 | 6:33 | 0.8515 | 0.78272 | 0.068778 | 9.1352e-06 | 0
[13 empty] | 6:33 | 1.0572 | 0.91146 | 0 |  | 6:33 | 0 | 0 | 0 | 6:33 | 0.85215 | 0.78331 | 0.068829 | 9.1421e-06 | 0
[13 empty] | 6:33 | 1.0434 | 0.91146 | 0 |  | 6:33 | 0 | 0 | 0 | 6:33 | 0.85277 | 0.78388 | 0.068881 | 9.1488e-06 | 0
[13 empty] | 6:34 | 1.0298 | 0.91146 | 0 |  | 6:34 | 0 | 0 | 0 | 6:34 | 0.8534 | 0.78446 | 0.068931 | 9.1555e-06 | 0
[13 empty] | 6:34 | 1.0164 | 0.91146 | 0 |  | 6:34 | 0 | 0 | 0 | 6:34 | 0.85402 | 0.78503 | 0.06898 | 9.1622e-06 | 0
[13 empty] | 6:34 | 1.0034 | 0.91146 | 0 |  | 6:34 | 0 | 0 | 0 | 6:34 | 0.85462 | 0.78558 | 0.06903 | 9.1687e-06 | 0
[13 empty] | 6:34 | 0.99062 | 0.91146 | 0 |  | 6:34 | 0 | 0 | 0 | 6:34 | 0.85522 | 0.78614 | 0.069078 | 9.175e-06 | 0
[13 empty] | 6:35 | 0.97811 | 0.91146 | 0 |  | 6:35 | 0 | 0 | 0 | 6:35 | 0.85581 | 0.78667 | 0.069125 | 9.1815e-06 | 0
[13 empty] | 6:35 | 0.96585 | 0.91146 | 0 |  | 6:35 | 0 | 0 | 0 | 6:35 | 0.85639 | 0.78721 | 0.069173 | 9.1878e-06 | 0
[13 empty] | 6:35 | 0.95385 | 0.91146 | 0 |  | 6:35 | 0 | 0 | 0 | 6:35 | 0.85697 | 0.78774 | 0.069219 | 9.1939e-06 | 0
[13 empty] | 6:35 | 0.94209 | 0.91146 | 0 |  | 6:35 | 0 | 0 | 0 | 6:35 | 0.85755 | 0.78828 | 0.069265 | 9.2e-06 | 0
[13 empty] | 6:36 | 0.93058 | 0.91146 | 0 |  | 6:36 | 0 | 0 | 0 | 6:36 | 0.85811 | 0.78879 | 0.069311 | 9.2061e-06 | 0
[13 empty] | 6:36 | 0.9193 | 0.91146 | 0 |  | 6:36 | 0 | 0 | 0 | 6:36 | 0.85865 | 0.78929 | 0.069357 | 9.212e-06 | 0
[13 empty] | 6:36 | 0.90825 | 0.91146 | 0 |  | 6:36 | 0 | 0 | 0 | 6:36 | 0.85921 | 0.7898 | 0.0694 | 9.2179e-06 | 0
[13 empty] | 6:36 | 0.89743 | 0.91146 | 0 |  | 6:36 | 0 | 0 | 0 | 6:36 | 0.85975 | 0.7903 | 0.069444 | 9.2237e-06 | 0
[13 empty] | 6:37 | 0.88683 | 0.91146 | 0 |  | 6:37 | 0 | 0 | 0 | 6:37 | 0.86029 | 0.7908 | 0.069488 | 9.2296e-06 | 0
[13 empty] | 6:37 | 0.87645 | 0.91146 | 0 |  | 6:37 | 0 | 0 | 0 | 6:37 | 0.86081 | 0.79127 | 0.06953 | 9.2351e-06 | 0
[13 empty] | 6:37 | 0.86628 | 0.91146 | 0 |  | 6:37 | 0 | 0 | 0 | 6:37 | 0.86135 | 0.79177 | 0.069572 | 9.2409e-06 | 0
[13 empty] | 6:37 | 0.85633 | 0.91146 | 0 |  | 6:37 | 0 | 0 | 0 | 6:37 | 0.86187 | 0.79225 | 0.069614 | 9.2464e-06 | 0
[13 empty] | 6:38 | 0.84657 | 0.91146 | 0 |  | 6:38 | 0 | 0 | 0 | 6:38 | 0.86237 | 0.79271 | 0.069656 | 9.2519e-06 | 0
[13 empty] | 6:38 | 0.83702 | 0.91146 | 0 |  | 6:38 | 0 | 0 | 0 | 6:38 | 0.86289 | 0.79318 | 0.069696 | 9.2573e-06 | 0
[13 empty] | 6:38 | 0.82766 | 0.91146 | 0 |  | 6:38 | 0 | 0 | 0 | 6:38 | 0.86339 | 0.79364 | 0.069737 | 9.2626e-06 | 0
[13 empty] | 6:38 | 0.8185 | 0.91146 | 0 |  | 6:38 | 0 | 0 | 0 | 6:38 | 0.86389 | 0.7941 | 0.069777 | 9.268e-06 | 0
[13 empty] | 6:38 | 0.80952 | 0.91146 | 0 |  | 6:38 | 0 | 0 | 0 | 6:38 | 0.86437 | 0.79454 | 0.069817 | 9.2733e-06 | 0
[13 empty] | 6:39 | 0.80073 | 0.91146 | 0 |  | 6:39 | 0 | 0 | 0 | 6:39 | 0.86486 | 0.795 | 0.069857 | 9.2785e-06 | 0
[13 empty] | 6:39 | 0.79211 | 0.91146 | 0 |  | 6:39 | 0 | 0 | 0 | 6:39 | 0.86534 | 0.79544 | 0.069895 | 9.2836e-06 | 0
[13 empty] | 6:39 | 0.78368 | 0.91146 | 0 |  | 6:39 | 0 | 0 | 0 | 6:39 | 0.86582 | 0.79588 | 0.069933 | 9.2886e-06 | 0
[13 empty] | 6:40 | 0.77542 | 0.91146 | 0 |  | 6:40 | 0 | 0 | 0 | 6:40 | 0.86628 | 0.7963 | 0.069972 | 9.2938e-06 | 0
[13 empty] | 6:40 | 0.76733 | 0.91146 | 0 |  | 6:40 | 0 | 0 | 0 | 6:40 | 0.86674 | 0.79672 | 0.07001 | 9.2987e-06 | 0
[13 empty] | 6:40 | 0.7594 | 0.91146 | 0 |  | 6:40 | 0 | 0 | 0 | 6:40 | 0.86721 | 0.79716 | 0.070046 | 9.3037e-06 | 0
[13 empty] | 6:40 | 0.75164 | 0.91146 | 0 |  | 6:40 | 0 | 0 | 0 | 6:40 | 0.86765 | 0.79756 | 0.070082 | 9.3085e-06 | 0
[13 empty] | 6:40 | 0.74403 | 0.91146 | 0 |  | 6:40 | 0 | 0 | 0 | 6:40 | 0.86811 | 0.79798 | 0.070119 | 9.3134e-06 | 0
[13 empty] | 6:41 | 0.73658 | 0.91146 | 0 |  | 6:41 | 0 | 0 | 0 | 6:41 | 0.86856 | 0.7984 | 0.070155 | 9.3182e-06 | 0
[13 empty] | 6:41 | 0.72929 | 0.91146 | 0 |  | 6:41 | 0 | 0 | 0 | 6:41 | 0.869 | 0.7988 | 0.070191 | 9.3228e-06 | 0
[13 empty] | 6:41 | 1.1629 | 0.91146 | 0 |  | 6:41 | 0 | 0 | 0 | 6:41 | 0.86971 | 0.79945 | 0.070248 | 9.3304e-06 | 0
[13 empty] | 6:42 | 1.1468 | 0.91146 | 0 |  | 6:42 | 0 | 0 | 0 | 6:42 | 0.87039 | 0.80008 | 0.070304 | 9.3379e-06 | 0
[13 empty] | 6:42 | 1.1311 | 0.91146 | 0 |  | 6:42 | 0 | 0 | 0 | 6:42 | 0.87108 | 0.80071 | 0.070359 | 9.3453e-06 | 0
[13 empty] | 6:42 | 1.1157 | 0.91146 | 0 |  | 6:42 | 0 | 0 | 0 | 6:42 | 0.87176 | 0.80134 | 0.070413 | 9.3524e-06 | 0
[13 empty] | 6:42 | 1.1006 | 0.91146 | 0 |  | 6:42 | 0 | 0 | 0 | 6:42 | 0.87243 | 0.80195 | 0.070468 | 9.3596e-06 | 0
[13 empty] | 6:42 | 1.0859 | 0.91146 | 0 |  | 6:42 | 0 | 0 | 0 | 6:42 | 0.87307 | 0.80254 | 0.07052 | 9.3667e-06 | 0
[13 empty] | 6:43 | 1.0714 | 0.91146 | 0 |  | 6:43 | 0 | 0 | 0 | 6:43 | 0.87374 | 0.80315 | 0.070573 | 9.3736e-06 | 0
[13 empty] | 6:43 | 1.0572 | 0.91146 | 0 |  | 6:43 | 0 | 0 | 0 | 6:43 | 0.87436 | 0.80373 | 0.070625 | 9.3805e-06 | 0
[13 empty] | 6:43 | 1.0434 | 0.91146 | 0 |  | 6:43 | 0 | 0 | 0 | 6:43 | 0.875 | 0.80432 | 0.070676 | 9.3873e-06 | 0
[13 empty] | 6:44 | 1.0298 | 0.91146 | 0 |  | 6:44 | 0 | 0 | 0 | 6:44 | 0.87563 | 0.80489 | 0.070726 | 9.394e-06 | 0
[13 empty] | 6:44 | 1.0164 | 0.91146 | 0 |  | 6:44 | 0 | 0 | 0 | 6:44 | 0.87623 | 0.80544 | 0.070776 | 9.4005e-06 | 0
[13 empty] | 6:44 | 1.0034 | 0.91146 | 0 |  | 6:44 | 0 | 0 | 0 | 6:44 | 0.87685 | 0.80602 | 0.070825 | 9.407e-06 | 0
[13 empty] | 6:44 | 0.99062 | 0.91146 | 0 |  | 6:44 | 0 | 0 | 0 | 6:44 | 0.87745 | 0.80657 | 0.070873 | 9.4135e-06 | 0
[13 empty] | 6:44 | 0.97811 | 0.91146 | 0 |  | 6:44 | 0 | 0 | 0 | 6:44 | 0.87804 | 0.80711 | 0.070921 | 9.4198e-06 | 0
[13 empty] | 6:45 | 0.96585 | 0.91146 | 0 |  | 6:45 | 0 | 0 | 0 | 6:45 | 0.87862 | 0.80764 | 0.070968 | 9.4261e-06 | 0
[13 empty] | 6:45 | 0.95385 | 0.91146 | 0 |  | 6:45 | 0 | 0 | 0 | 6:45 | 0.8792 | 0.80818 | 0.071014 | 9.4324e-06 | 0
[13 empty] | 6:45 | 0.94209 | 0.91146 | 0 |  | 6:45 | 0 | 0 | 0 | 6:45 | 0.87976 | 0.80869 | 0.07106 | 9.4385e-06 | 0
[13 empty] | 6:46 | 0.93058 | 0.91146 | 0 |  | 6:46 | 0 | 0 | 0 | 6:46 | 0.88034 | 0.80923 | 0.071106 | 9.4444e-06 | 0
[13 empty] | 6:46 | 0.9193 | 0.91146 | 0 |  | 6:46 | 0 | 0 | 0 | 6:46 | 0.88088 | 0.80972 | 0.071152 | 9.4506e-06 | 0
[13 empty] | 6:46 | 0.90825 | 0.91146 | 0 |  | 6:46 | 0 | 0 | 0 | 6:46 | 0.88144 | 0.81024 | 0.071196 | 9.4563e-06 | 0
[13 empty] | 6:46 | 0.89743 | 0.91146 | 0 |  | 6:46 | 0 | 0 | 0 | 6:46 | 0.88198 | 0.81074 | 0.07124 | 9.4622e-06 | 0
[13 empty] | 6:46 | 0.88683 | 0.91146 | 0 |  | 6:46 | 0 | 0 | 0 | 6:46 | 0.88252 | 0.81123 | 0.071284 | 9.4679e-06 | 0
[13 empty] | 6:47 | 0.87645 | 0.91146 | 0 |  | 6:47 | 0 | 0 | 0 | 6:47 | 0.88304 | 0.81171 | 0.071326 | 9.4737e-06 | 0
[13 empty] | 6:47 | 0.86628 | 0.91146 | 0 |  | 6:47 | 0 | 0 | 0 | 6:47 | 0.88358 | 0.81221 | 0.071368 | 9.4792e-06 | 0
[13 empty] | 6:47 | 0.85633 | 0.91146 | 0 |  | 6:47 | 0 | 0 | 0 | 6:47 | 0.88408 | 0.81266 | 0.07141 | 9.4849e-06 | 0
[13 empty] | 6:48 | 0.84657 | 0.91146 | 0 |  | 6:48 | 0 | 0 | 0 | 6:48 | 0.8846 | 0.81314 | 0.071452 | 9.4903e-06 | 0
[13 empty] | 6:48 | 0.83702 | 0.91146 | 0 |  | 6:48 | 0 | 0 | 0 | 6:48 | 0.88512 | 0.81362 | 0.071492 | 9.4958e-06 | 0
[13 empty] | 6:48 | 0.82766 | 0.91146 | 0 |  | 6:48 | 0 | 0 | 0 | 6:48 | 0.88562 | 0.81408 | 0.071534 | 9.5012e-06 | 0
[13 empty] | 6:48 | 0.8185 | 0.91146 | 0 |  | 6:48 | 0 | 0 | 0 | 6:48 | 0.88612 | 0.81454 | 0.071574 | 9.5065e-06 | 0
[13 empty] | 6:48 | 0.80952 | 0.91146 | 0 |  | 6:48 | 0 | 0 | 0 | 6:48 | 0.8866 | 0.81498 | 0.071612 | 9.5117e-06 | 0
[13 empty] | 6:49 | 0.80073 | 0.91146 | 0 |  | 6:49 | 0 | 0 | 0 | 6:49 | 0.88708 | 0.81541 | 0.071652 | 9.517e-06 | 0
[13 empty] | 6:49 | 0.79211 | 0.91146 | 0 |  | 6:49 | 0 | 0 | 0 | 6:49 | 0.88757 | 0.81587 | 0.07169 | 9.522e-06 | 0
[13 empty] | 6:49 | 0.78368 | 0.91146 | 0 |  | 6:49 | 0 | 0 | 0 | 6:49 | 0.88803 | 0.81629 | 0.071729 | 9.5271e-06 | 0
[13 empty] | 6:50 | 0.77542 | 0.91146 | 0 |  | 6:50 | 0 | 0 | 0 | 6:50 | 0.88851 | 0.81673 | 0.071767 | 9.5321e-06 | 0
[13 empty] | 6:50 | 0.76733 | 0.91146 | 0 |  | 6:50 | 0 | 0 | 0 | 6:50 | 0.88897 | 0.81715 | 0.071805 | 9.5373e-06 | 0
[13 empty] | 6:50 | 0.7594 | 0.91146 | 0 |  | 6:50 | 0 | 0 | 0 | 6:50 | 0.88942 | 0.81757 | 0.071841 | 9.542e-06 | 0
[13 empty] | 6:50 | 0.75164 | 0.91146 | 0 |  | 6:50 | 0 | 0 | 0 | 6:50 | 0.88988 | 0.81799 | 0.071878 | 9.547e-06 | 0
[13 empty] | 6:50 | 0.74403 | 0.91146 | 0 |  | 6:50 | 0 | 0 | 0 | 6:50 | 0.89034 | 0.81841 | 0.071914 | 9.5518e-06 | 0
[13 empty] | 6:51 | 0.73658 | 0.91146 | 0 |  | 6:51 | 0 | 0 | 0 | 6:51 | 0.89077 | 0.81881 | 0.07195 | 9.5566e-06 | 0
[13 empty] | 6:51 | 0.72929 | 0.91146 | 0 |  | 6:51 | 0 | 0 | 0 | 6:51 | 0.89123 | 0.81923 | 0.071986 | 9.5613e-06 | 0
[13 empty] | 6:51 | 1.1629 | 0.91146 | 0 |  | 6:51 | 0 | 0 | 0 | 6:51 | 0.89194 | 0.81988 | 0.072044 | 9.569e-06 | 0
[13 empty] | 6:52 | 1.1468 | 0.91146 | 0 |  | 6:52 | 0 | 0 | 0 | 6:52 | 0.89262 | 0.82051 | 0.072099 | 9.5764e-06 | 0
[13 empty] | 6:52 | 1.1311 | 0.91146 | 0 |  | 6:52 | 0 | 0 | 0 | 6:52 | 0.89331 | 0.82114 | 0.072154 | 9.5837e-06 | 0
[13 empty] | 6:52 | 1.1157 | 0.91146 | 0 |  | 6:52 | 0 | 0 | 0 | 6:52 | 0.89399 | 0.82177 | 0.07221 | 9.5909e-06 | 0
[13 empty] | 6:52 | 1.1006 | 0.91146 | 0 |  | 6:52 | 0 | 0 | 0 | 6:52 | 0.89466 | 0.82239 | 0.072263 | 9.5982e-06 | 0
[13 empty] | 6:52 | 1.0859 | 0.91146 | 0 |  | 6:52 | 0 | 0 | 0 | 6:52 | 0.8953 | 0.82298 | 0.072317 | 9.6051e-06 | 0
[13 empty] | 6:53 | 1.0714 | 0.91146 | 0 |  | 6:53 | 0 | 0 | 0 | 6:53 | 0.89595 | 0.82357 | 0.072368 | 9.6121e-06 | 0
[13 empty] | 6:53 | 1.0572 | 0.91146 | 0 |  | 6:53 | 0 | 0 | 0 | 6:53 | 0.89659 | 0.82416 | 0.07242 | 9.619e-06 | 0
[13 empty] | 6:53 | 1.0434 | 0.91146 | 0 |  | 6:53 | 0 | 0 | 0 | 6:53 | 0.89723 | 0.82475 | 0.072472 | 9.6257e-06 | 0
[13 empty] | 6:53 | 1.0298 | 0.91146 | 0 |  | 6:53 | 0 | 0 | 0 | 6:53 | 0.89786 | 0.82533 | 0.072521 | 9.6324e-06 | 0
[13 empty] | 6:54 | 1.0164 | 0.91146 | 0 |  | 6:54 | 0 | 0 | 0 | 6:54 | 0.89846 | 0.82588 | 0.072571 | 9.6391e-06 | 0
[13 empty] | 6:54 | 1.0034 | 0.91146 | 0 |  | 6:54 | 0 | 0 | 0 | 6:54 | 0.89908 | 0.82645 | 0.07262 | 9.6456e-06 | 0
[13 empty] | 6:54 | 0.99062 | 0.91146 | 0 |  | 6:54 | 0 | 0 | 0 | 6:54 | 0.89967 | 0.82699 | 0.072668 | 9.652e-06 | 0
[13 empty] | 6:54 | 0.97811 | 0.91146 | 0 |  | 6:54 | 0 | 0 | 0 | 6:54 | 0.90027 | 0.82754 | 0.072716 | 9.6583e-06 | 0
[13 empty] | 6:55 | 0.96585 | 0.91146 | 0 |  | 6:55 | 0 | 0 | 0 | 6:55 | 0.90085 | 0.82808 | 0.072764 | 9.6647e-06 | 0
[13 empty] | 6:55 | 0.95385 | 0.91146 | 0 |  | 6:55 | 0 | 0 | 0 | 6:55 | 0.90143 | 0.82861 | 0.07281 | 9.6708e-06 | 0
[13 empty] | 6:55 | 0.94209 | 0.91146 | 0 |  | 6:55 | 0 | 0 | 0 | 6:55 | 0.90199 | 0.82913 | 0.072855 | 9.6769e-06 | 0
[13 empty] | 6:55 | 0.93058 | 0.91146 | 0 |  | 6:55 | 0 | 0 | 0 | 6:55 | 0.90255 | 0.82964 | 0.072901 | 9.683e-06 | 0
[13 empty] | 6:56 | 0.9193 | 0.91146 | 0 |  | 6:56 | 0 | 0 | 0 | 6:56 | 0.90312 | 0.83016 | 0.072947 | 9.6889e-06 | 0
[13 empty] | 6:56 | 0.90825 | 0.91146 | 0 |  | 6:56 | 0 | 0 | 0 | 6:56 | 0.90367 | 0.83067 | 0.072991 | 9.6948e-06 | 0
[13 empty] | 6:56 | 0.89743 | 0.91146 | 0 |  | 6:56 | 0 | 0 | 0 | 6:56 | 0.90422 | 0.83117 | 0.073035 | 9.7007e-06 | 0
[13 empty] | 6:56 | 0.88683 | 0.91146 | 0 |  | 6:56 | 0 | 0 | 0 | 6:56 | 0.90476 | 0.83167 | 0.073079 | 9.7065e-06 | 0
[13 empty] | 6:57 | 0.87645 | 0.91146 | 0 |  | 6:57 | 0 | 0 | 0 | 6:57 | 0.90528 | 0.83214 | 0.073121 | 9.7122e-06 | 0
[13 empty] | 6:57 | 0.86628 | 0.91146 | 0 |  | 6:57 | 0 | 0 | 0 | 6:57 | 0.90579 | 0.83262 | 0.073163 | 9.7177e-06 | 0
[13 empty] | 6:57 | 0.85633 | 0.91146 | 0 |  | 6:57 | 0 | 0 | 0 | 6:57 | 0.90631 | 0.8331 | 0.073205 | 9.7233e-06 | 0
[13 empty] | 6:57 | 0.84657 | 0.91146 | 0 |  | 6:57 | 0 | 0 | 0 | 6:57 | 0.90683 | 0.83358 | 0.073247 | 9.7288e-06 | 0
[13 empty] | 6:58 | 0.83702 | 0.91146 | 0 |  | 6:58 | 0 | 0 | 0 | 6:58 | 0.90733 | 0.83404 | 0.073287 | 9.7342e-06 | 0
[13 empty] | 6:58 | 0.82766 | 0.91146 | 0 |  | 6:58 | 0 | 0 | 0 | 6:58 | 0.90785 | 0.83451 | 0.073329 | 9.7397e-06 | 0
[13 empty] | 6:58 | 0.8185 | 0.91146 | 0 |  | 6:58 | 0 | 0 | 0 | 6:58 | 0.90833 | 0.83495 | 0.073369 | 9.7449e-06 | 0
[13 empty] | 6:58 | 0.80952 | 0.91146 | 0 |  | 6:58 | 0 | 0 | 0 | 6:58 | 0.90883 | 0.83541 | 0.073407 | 9.7502e-06 | 0
[13 empty] | 6:59 | 0.80073 | 0.91146 | 0 |  | 6:59 | 0 | 0 | 0 | 6:59 | 0.90931 | 0.83585 | 0.073447 | 9.7554e-06 | 0
[13 empty] | 6:59 | 0.79211 | 0.91146 | 0 |  | 6:59 | 0 | 0 | 0 | 6:59 | 0.90978 | 0.83629 | 0.073486 | 9.7605e-06 | 0
[13 empty] | 6:59 | 0.78368 | 0.91146 | 0 |  | 6:59 | 0 | 0 | 0 | 6:59 | 0.91026 | 0.83673 | 0.073524 | 9.7657e-06 | 0
[13 empty] | 7:00 | 0.77542 | 0.91146 | 0 |  | 7:00 | 0 | 0 | 0 | 7:00 | 0.91074 | 0.83717 | 0.073562 | 9.7706e-06 | 0
[13 empty] | 7:00 | 0.76733 | 0.91146 | 0 |  | 7:00 | 0 | 0 | 0 | 7:00 | 0.9112 | 0.83759 | 0.0736 | 9.7756e-06 | 0
[13 empty] | 7:00 | 0.7594 | 0.91146 | 0.91784 |  | 7:00 | 0 | 0.15298 | 0 | 7:00 | 0.91165 | 0.83801 | 0.073637 | 9.7806e-06 | 0
[13 empty] | 7:00 | 0.75164 | 0.91146 | 0.91784 |  | 7:00 | 0.75552 | 0.15298 | 5.6664 | 7:00 | 0.91211 | 0.83843 | 0.073673 | 9.7855e-06 | 0
[13 empty] | 7:00 | 0.74403 | 0.91146 | 0.91784 |  | 7:00 | 0.74784 | 0.15298 | 16.9415 | 7:00 | 0.91257 | 0.83885 | 0.073709 | 9.7903e-06 | 0
[13 empty] | 7:01 | 0.73658 | 0.91146 | 0.91784 |  | 7:01 | 0.74031 | 0.15298 | 28.1026 | 7:01 | 0.913 | 0.83925 | 0.073745 | 9.7951e-06 | 0
[13 empty] | 7:01 | 0.72929 | 0.91146 | 0.91784 |  | 7:01 | 0.73294 | 0.15298 | 39.1519 | 7:01 | 0.91346 | 0.83967 | 0.073782 | 9.7999e-06 | 0
[13 empty] | 7:01 | 1.1629 | 0.91146 | 0.91784 |  | 7:01 | 0.94609 | 0.15298 | 51.7448 | 7:01 | 0.91415 | 0.8403 | 0.073839 | 9.8073e-06 | 0
[13 empty] | 7:02 | 1.1468 | 0.91146 | 0.91784 |  | 7:02 | 1.1549 | 0.15298 | 67.5021 | 7:02 | 0.91485 | 0.84095 | 0.073894 | 9.8148e-06 | 0
[13 empty] | 7:02 | 1.1311 | 0.91146 | 0.91784 |  | 7:02 | 1.139 | 0.15298 | 84.7059 | 7:02 | 0.91554 | 0.84158 | 0.07395 | 9.8222e-06 | 0
[13 empty] | 7:02 | 1.1157 | 0.91146 | 0.91784 |  | 7:02 | 1.1234 | 0.15298 | 101.674 | 7:02 | 0.91621 | 0.84219 | 0.074005 | 9.8295e-06 | 0
[13 empty] | 7:02 | 1.1006 | 0.91146 | 0.91784 |  | 7:02 | 1.1082 | 0.15298 | 118.4111 | 7:02 | 0.91687 | 0.8428 | 0.074059 | 9.8365e-06 | 0
[13 empty] | 7:02 | 1.0859 | 0.91146 | 0.91784 |  | 7:02 | 1.0933 | 0.15298 | 134.922 | 7:02 | 0.91753 | 0.84341 | 0.074112 | 9.8436e-06 | 0
[13 empty] | 7:03 | 1.0714 | 0.91146 | 0.91784 |  | 7:03 | 1.0786 | 0.15298 | 151.2112 | 7:03 | 0.91818 | 0.84401 | 0.074164 | 9.8507e-06 | 0
[13 empty] | 7:03 | 1.0572 | 0.91146 | 0.91784 |  | 7:03 | 1.0643 | 0.15298 | 167.2834 | 7:03 | 0.91882 | 0.8446 | 0.074215 | 9.8574e-06 | 0
[13 empty] | 7:03 | 1.0434 | 0.91146 | 0.91784 |  | 7:03 | 1.0503 | 0.15298 | 183.1431 | 7:03 | 0.91945 | 0.84517 | 0.074267 | 9.8642e-06 | 0
[13 empty] | 7:04 | 1.0298 | 0.91146 | 0.91784 |  | 7:04 | 1.0366 | 0.15298 | 198.7934 | 7:04 | 0.92007 | 0.84574 | 0.074316 | 9.8709e-06 | 0
[13 empty] | 7:04 | 1.0164 | 0.91146 | 0.91784 |  | 7:04 | 1.0231 | 0.15298 | 214.2423 | 7:04 | 0.92069 | 0.84632 | 0.074366 | 9.8776e-06 | 0
[13 empty] | 7:04 | 1.0034 | 0.91146 | 0.91784 |  | 7:04 | 1.0099 | 0.15298 | 229.4887 | 7:04 | 0.9213 | 0.84687 | 0.074416 | 9.8841e-06 | 0
[13 empty] | 7:04 | 0.99062 | 0.91146 | 0.91784 |  | 7:04 | 0.99701 | 0.15298 | 244.5422 | 7:04 | 0.9219 | 0.84742 | 0.074464 | 9.8904e-06 | 0
[13 empty] | 7:04 | 0.97811 | 0.91146 | 0.91784 |  | 7:04 | 0.98437 | 0.15298 | 259.4009 | 7:04 | 0.9225 | 0.84798 | 0.074511 | 9.8969e-06 | 0
[13 empty] | 7:05 | 0.96585 | 0.91146 | 0.91784 |  | 7:05 | 0.97198 | 0.15298 | 274.0744 | 7:05 | 0.92308 | 0.84851 | 0.074559 | 9.903e-06 | 0
[13 empty] | 7:05 | 0.95385 | 0.91146 | 0.91784 |  | 7:05 | 0.95985 | 0.15298 | 288.5625 | 7:05 | 0.92366 | 0.84905 | 0.074605 | 9.9093e-06 | 0
[13 empty] | 7:05 | 0.94209 | 0.91146 | 0.91784 |  | 7:05 | 0.94797 | 0.15298 | 302.8712 | 7:05 | 0.92423 | 0.84956 | 0.074653 | 9.9154e-06 | 0
[13 empty] | 7:06 | 0.93058 | 0.91146 | 0.91784 |  | 7:06 | 0.93634 | 0.15298 | 317.0042 | 7:06 | 0.92478 | 0.85008 | 0.074697 | 9.9215e-06 | 0
[13 empty] | 7:06 | 0.9193 | 0.91146 | 0.91784 |  | 7:06 | 0.92494 | 0.15298 | 330.9633 | 7:06 | 0.92535 | 0.85059 | 0.074742 | 9.9274e-06 | 0
[13 empty] | 7:06 | 0.90825 | 0.91146 | 0.91784 |  | 7:06 | 0.91377 | 0.15298 | 344.7544 | 7:06 | 0.92589 | 0.85109 | 0.074786 | 9.9334e-06 | 0
[13 empty] | 7:06 | 0.89743 | 0.91146 | 0.91784 |  | 7:06 | 0.90284 | 0.15298 | 358.3794 | 7:06 | 0.92645 | 0.85161 | 0.07483 | 9.9391e-06 | 0
[13 empty] | 7:06 | 0.88683 | 0.91146 | 0.91784 |  | 7:06 | 0.89213 | 0.15298 | 371.8401 | 7:06 | 0.92697 | 0.85208 | 0.074874 | 9.9448e-06 | 0
[13 empty] | 7:07 | 0.87645 | 0.91146 | 0.91784 |  | 7:07 | 0.88164 | 0.15298 | 385.1441 | 7:07 | 0.92751 | 0.85258 | 0.074916 | 9.9506e-06 | 0
[13 empty] | 7:07 | 0.86628 | 0.91146 | 0.91784 |  | 7:07 | 0.87137 | 0.15298 | 398.2916 | 7:07 | 0.92803 | 0.85306 | 0.074958 | 9.9563e-06 | 0
[13 empty] | 7:07 | 0.85633 | 0.91146 | 0.91784 |  | 7:07 | 0.8613 | 0.15298 | 411.2863 | 7:07 | 0.92855 | 0.85354 | 0.075 | 9.9618e-06 | 0
[13 empty] | 7:08 | 0.84657 | 0.91146 | 0.91784 |  | 7:08 | 0.85145 | 0.15298 | 424.132 | 7:08 | 0.92906 | 0.85401 | 0.075042 | 9.9674e-06 | 0
[13 empty] | 7:08 | 0.83702 | 0.91146 | 0.91784 |  | 7:08 | 0.8418 | 0.15298 | 436.8326 | 7:08 | 0.92957 | 0.85447 | 0.075084 | 9.9727e-06 | 0
[13 empty] | 7:08 | 0.82766 | 0.91146 | 0.91784 |  | 7:08 | 0.83234 | 0.15298 | 449.388 | 7:08 | 0.93006 | 0.85493 | 0.075124 | 9.9781e-06 | 0
[13 empty] | 7:08 | 0.8185 | 0.91146 | 0.91784 |  | 7:08 | 0.82308 | 0.15298 | 461.804 | 7:08 | 0.93056 | 0.85539 | 0.075164 | 9.9834e-06 | 0
[13 empty] | 7:08 | 0.80952 | 0.91146 | 0.91784 |  | 7:08 | 0.81401 | 0.15298 | 474.0825 | 7:08 | 0.93106 | 0.85585 | 0.075203 | 9.9888e-06 | 0
[13 empty] | 7:09 | 0.80073 | 0.91146 | 0.91784 |  | 7:09 | 0.80512 | 0.15298 | 486.2253 | 7:09 | 0.93154 | 0.85629 | 0.075243 | 9.9939e-06 | 0
[13 empty] | 7:09 | 0.79211 | 0.91146 | 0.91784 |  | 7:09 | 0.79642 | 0.15298 | 498.2364 | 7:09 | 0.93202 | 0.85672 | 0.075281 | 9.9991e-06 | 0
[13 empty] | 7:09 | 0.78368 | 0.91146 | 0.91784 |  | 7:09 | 0.7879 | 0.15298 | 510.1196 | 7:09 | 0.93249 | 0.85716 | 0.075319 | 1.0004e-05 | 0
[13 empty] | 7:10 | 0.77542 | 0.91146 | 0.91784 |  | 7:10 | 0.77955 | 0.15298 | 521.8748 | 7:10 | 0.93297 | 0.8576 | 0.075357 | 1.0009e-05 | 0
[13 empty] | 7:10 | 0.76733 | 0.91146 | 0.91784 |  | 7:10 | 0.77137 | 0.15298 | 533.5058 | 7:10 | 0.93343 | 0.85802 | 0.075396 | 1.0014e-05 | 0
[13 empty] | 7:10 | 0.7594 | 0.91146 | 0.91784 |  | 7:10 | 0.76336 | 0.15298 | 545.0165 | 7:10 | 0.93389 | 0.85844 | 0.075432 | 1.0019e-05 | 0
[13 empty] | 7:10 | 0.75164 | 0.91146 | 0.91784 |  | 7:10 | 0 | 0.15298 | 550.7423 | 7:10 | 0.93434 | 0.85886 | 0.075468 | 1.0024e-05 | 0
[13 empty] | 7:10 | 0.74403 | 0.91146 | 0.91784 |  | 7:10 | 0 | 0.15298 | 550.7423 | 7:10 | 0.9348 | 0.85928 | 0.075504 | 1.0029e-05 | 0
[13 empty] | 7:11 | 0.73658 | 0.91146 | 0.91784 |  | 7:11 | 0 | 0.15298 | 550.7423 | 7:11 | 0.93524 | 0.85968 | 0.075541 | 1.0034e-05 | 0
[13 empty] | 7:11 | 0.72929 | 0.91146 | 0.91784 |  | 7:11 | 0 | 0.15298 | 550.7423 | 7:11 | 0.93567 | 0.86009 | 0.075577 | 1.0038e-05 | 0
[13 empty] | 7:11 | 1.1629 | 0.91146 | 0.91784 |  | 7:11 | 0 | 0.15298 | 550.7423 | 7:11 | 0.93638 | 0.86074 | 0.075634 | 1.0046e-05 | 0
[13 empty] | 7:12 | 1.1468 | 0.91146 | 0.91784 |  | 7:12 | 0 | 0.15298 | 550.7423 | 7:12 | 0.93708 | 0.86138 | 0.07569 | 1.0053e-05 | 0
[13 empty] | 7:12 | 1.1311 | 0.91146 | 0.91784 |  | 7:12 | 0 | 0.15298 | 550.7423 | 7:12 | 0.93777 | 0.86201 | 0.075745 | 1.0061e-05 | 0
[13 empty] | 7:12 | 1.1157 | 0.91146 | 0.91784 |  | 7:12 | 0 | 0.15298 | 550.7423 | 7:12 | 0.93844 | 0.86263 | 0.0758 | 1.0068e-05 | 0
[13 empty] | 7:12 | 1.1006 | 0.91146 | 0.91784 |  | 7:12 | 0 | 0.15298 | 550.7423 | 7:12 | 0.9391 | 0.86324 | 0.075854 | 1.0075e-05 | 0
[13 empty] | 7:12 | 1.0859 | 0.91146 | 0.91784 |  | 7:12 | 0 | 0.15298 | 550.7423 | 7:12 | 0.93977 | 0.86385 | 0.075907 | 1.0082e-05 | 0
[13 empty] | 7:13 | 1.0714 | 0.91146 | 0.91784 |  | 7:13 | 0 | 0.15298 | 550.7423 | 7:13 | 0.94041 | 0.86444 | 0.075959 | 1.0089e-05 | 0
[13 empty] | 7:13 | 1.0572 | 0.91146 | 0.91784 |  | 7:13 | 0 | 0.15298 | 550.7423 | 7:13 | 0.94105 | 0.86503 | 0.07601 | 1.0096e-05 | 0
[13 empty] | 7:13 | 1.0434 | 0.91146 | 0.91784 |  | 7:13 | 0 | 0.15298 | 550.7423 | 7:13 | 0.94168 | 0.86561 | 0.076062 | 1.0103e-05 | 0
[13 empty] | 7:14 | 1.0298 | 0.91146 | 0.91784 |  | 7:14 | 0 | 0.15298 | 550.7423 | 7:14 | 0.9423 | 0.86618 | 0.076112 | 1.0109e-05 | 0
[13 empty] | 7:14 | 1.0164 | 0.91146 | 0.91784 |  | 7:14 | 0 | 0.15298 | 550.7423 | 7:14 | 0.94292 | 0.86675 | 0.076161 | 1.0116e-05 | 0
[13 empty] | 7:14 | 1.0034 | 0.91146 | 0.91784 |  | 7:14 | 0 | 0.15298 | 550.7423 | 7:14 | 0.94353 | 0.86731 | 0.076211 | 1.0122e-05 | 0
[13 empty] | 7:14 | 0.99062 | 0.91146 | 0.91784 |  | 7:14 | 0 | 0.15298 | 550.7423 | 7:14 | 0.94413 | 0.86786 | 0.076259 | 1.0129e-05 | 0
[13 empty] | 7:14 | 0.97811 | 0.91146 | 0.91784 |  | 7:14 | 0 | 0.15298 | 550.7423 | 7:14 | 0.94473 | 0.86841 | 0.076307 | 1.0135e-05 | 0
[13 empty] | 7:15 | 0.96585 | 0.91146 | 0.91784 |  | 7:15 | 0 | 0.15298 | 550.7423 | 7:15 | 0.94531 | 0.86895 | 0.076354 | 1.0142e-05 | 0
[13 empty] | 7:15 | 0.95385 | 0.91146 | 0.91784 |  | 7:15 | 0 | 0.15298 | 550.7423 | 7:15 | 0.94588 | 0.86946 | 0.076402 | 1.0148e-05 | 0
[13 empty] | 7:15 | 0.94209 | 0.91146 | 0.91784 |  | 7:15 | 0 | 0.15298 | 550.7423 | 7:15 | 0.94646 | 0.87 | 0.076448 | 1.0154e-05 | 0
[13 empty] | 7:16 | 0.93058 | 0.91146 | 0.91784 |  | 7:16 | 0 | 0.15298 | 550.7423 | 7:16 | 0.94702 | 0.87051 | 0.076492 | 1.016e-05 | 0
[13 empty] | 7:16 | 0.9193 | 0.91146 | 0.91784 |  | 7:16 | 0 | 0.15298 | 550.7423 | 7:16 | 0.94758 | 0.87103 | 0.076538 | 1.0166e-05 | 0
[13 empty] | 7:16 | 0.90825 | 0.91146 | 0.91784 |  | 7:16 | 0 | 0.15298 | 550.7423 | 7:16 | 0.94812 | 0.87153 | 0.076582 | 1.0172e-05 | 0
[13 empty] | 7:16 | 0.89743 | 0.91146 | 0.91784 |  | 7:16 | 0 | 0.15298 | 550.7423 | 7:16 | 0.94866 | 0.87202 | 0.076625 | 1.0178e-05 | 0
[13 empty] | 7:17 | 0.88683 | 0.91146 | 0.91784 |  | 7:17 | 0 | 0.15298 | 550.7423 | 7:17 | 0.9492 | 0.87252 | 0.076669 | 1.0183e-05 | 0
[13 empty] | 7:17 | 0.87645 | 0.91146 | 0.91784 |  | 7:17 | 0 | 0.15298 | 550.7423 | 7:17 | 0.94974 | 0.87302 | 0.076711 | 1.0189e-05 | 0
[13 empty] | 7:17 | 0.86628 | 0.91146 | 0.91784 |  | 7:17 | 0 | 0.15298 | 550.7423 | 7:17 | 0.95026 | 0.87349 | 0.076755 | 1.0195e-05 | 0
[13 empty] | 7:17 | 0.85633 | 0.91146 | 0.91784 |  | 7:17 | 0 | 0.15298 | 550.7423 | 7:17 | 0.95078 | 0.87397 | 0.076797 | 1.02e-05 | 0
[13 empty] | 7:18 | 0.84657 | 0.91146 | 0.91784 |  | 7:18 | 0 | 0.15298 | 550.7423 | 7:18 | 0.9513 | 0.87445 | 0.076837 | 1.0206e-05 | 0
[13 empty] | 7:18 | 0.83702 | 0.91146 | 0.91784 |  | 7:18 | 0 | 0.15298 | 550.7423 | 7:18 | 0.9518 | 0.87491 | 0.076879 | 1.0211e-05 | 0
[13 empty] | 7:18 | 0.82766 | 0.91146 | 0.91784 |  | 7:18 | 0 | 0.15298 | 550.7423 | 7:18 | 0.95229 | 0.87536 | 0.07692 | 1.0217e-05 | 0
[13 empty] | 7:18 | 0.8185 | 0.91146 | 0.91784 |  | 7:18 | 0 | 0.15298 | 550.7423 | 7:18 | 0.95279 | 0.87582 | 0.07696 | 1.0222e-05 | 0
[13 empty] | 7:19 | 0.80952 | 0.91146 | 0.91784 |  | 7:19 | 0 | 0.15298 | 550.7423 | 7:19 | 0.95329 | 0.87628 | 0.076998 | 1.0227e-05 | 0
[13 empty] | 7:19 | 0.80073 | 0.91146 | 0.91784 |  | 7:19 | 0 | 0.15298 | 550.7423 | 7:19 | 0.95377 | 0.87672 | 0.077038 | 1.0232e-05 | 0
[13 empty] | 7:19 | 0.79211 | 0.91146 | 0.91784 |  | 7:19 | 0 | 0.15298 | 550.7423 | 7:19 | 0.95425 | 0.87716 | 0.077076 | 1.0237e-05 | 0
[13 empty] | 7:19 | 0.78368 | 0.91146 | 0.91784 |  | 7:19 | 0 | 0.15298 | 550.7423 | 7:19 | 0.95472 | 0.8776 | 0.077114 | 1.0243e-05 | 0
[13 empty] | 7:20 | 0.77542 | 0.91146 | 0.91784 |  | 7:20 | 0 | 0.15298 | 550.7423 | 7:20 | 0.95518 | 0.87802 | 0.077153 | 1.0248e-05 | 0
[13 empty] | 7:20 | 0.76733 | 0.91146 | 0.91784 |  | 7:20 | 0 | 0.15298 | 550.7423 | 7:20 | 0.95566 | 0.87846 | 0.077191 | 1.0253e-05 | 0
[13 empty] | 7:20 | 0.7594 | 0.91146 | 0.91784 |  | 7:20 | 0 | 0.15298 | 550.7423 | 7:20 | 0.95612 | 0.87888 | 0.077227 | 1.0257e-05 | 0
[13 empty] | 7:20 | 0.75164 | 0.91146 | 0.91784 |  | 7:20 | 0 | 0.15298 | 550.7423 | 7:20 | 0.95657 | 0.8793 | 0.077265 | 1.0262e-05 | 0
[13 empty] | 7:21 | 0.74403 | 0.91146 | 0.91784 |  | 7:21 | 0 | 0.15298 | 550.7423 | 7:21 | 0.95703 | 0.87972 | 0.077302 | 1.0267e-05 | 0
[13 empty] | 7:21 | 0.73658 | 0.91146 | 0.91784 |  | 7:21 | 0 | 0.15298 | 550.7423 | 7:21 | 0.95747 | 0.88012 | 0.077336 | 1.0272e-05 | 0
[13 empty] | 7:21 | 0.72929 | 0.91146 | 0.91784 |  | 7:21 | 0 | 0.15298 | 550.7423 | 7:21 | 0.9579 | 0.88052 | 0.077372 | 1.0277e-05 | 0
[13 empty] | 7:21 | 1.1629 | 0.91146 | 0.91784 |  | 7:21 | 0 | 0.15298 | 550.7423 | 7:21 | 0.95861 | 0.88117 | 0.07743 | 1.0284e-05 | 0
[13 empty] | 7:22 | 1.1468 | 0.91146 | 0.91784 |  | 7:22 | 0 | 0.15298 | 550.7423 | 7:22 | 0.95932 | 0.88182 | 0.077485 | 1.0292e-05 | 0
[13 empty] | 7:22 | 1.1311 | 0.91146 | 0.91784 |  | 7:22 | 0 | 0.15298 | 550.7423 | 7:22 | 0.96 | 0.88245 | 0.07754 | 1.0299e-05 | 0
[13 empty] | 7:22 | 1.1157 | 0.91146 | 0.91784 |  | 7:22 | 0 | 0.15298 | 550.7423 | 7:22 | 0.96067 | 0.88306 | 0.077596 | 1.0306e-05 | 0
[13 empty] | 7:22 | 1.1006 | 0.91146 | 0.91784 |  | 7:22 | 0 | 0.15298 | 550.7423 | 7:22 | 0.96133 | 0.88367 | 0.077649 | 1.0313e-05 | 0
[13 empty] | 7:22 | 1.0859 | 0.91146 | 0.91784 |  | 7:22 | 0 | 0.15298 | 550.7423 | 7:22 | 0.962 | 0.88428 | 0.077703 | 1.032e-05 | 0
[13 empty] | 7:23 | 1.0714 | 0.91146 | 0.91784 |  | 7:23 | 0 | 0.15298 | 550.7423 | 7:23 | 0.96264 | 0.88488 | 0.077754 | 1.0328e-05 | 0
[13 empty] | 7:23 | 1.0572 | 0.91146 | 0.91784 |  | 7:23 | 0 | 0.15298 | 550.7423 | 7:23 | 0.96328 | 0.88547 | 0.077806 | 1.0334e-05 | 0
[13 empty] | 7:23 | 1.0434 | 0.91146 | 0.91784 |  | 7:23 | 0 | 0.15298 | 550.7423 | 7:23 | 0.96391 | 0.88604 | 0.077857 | 1.0341e-05 | 0
[13 empty] | 7:24 | 1.0298 | 0.91146 | 0.91784 |  | 7:24 | 0 | 0.15298 | 550.7423 | 7:24 | 0.96453 | 0.88661 | 0.077907 | 1.0348e-05 | 0
[13 empty] | 7:24 | 1.0164 | 0.91146 | 0.91784 |  | 7:24 | 0 | 0.15298 | 550.7423 | 7:24 | 0.96515 | 0.88719 | 0.077957 | 1.0354e-05 | 0
[13 empty] | 7:24 | 1.0034 | 0.91146 | 0.91784 |  | 7:24 | 0 | 0.15298 | 550.7423 | 7:24 | 0.96576 | 0.88774 | 0.078006 | 1.0361e-05 | 0
[13 empty] | 7:24 | 0.99062 | 0.91146 | 0.91784 |  | 7:24 | 0 | 0.15298 | 550.7423 | 7:24 | 0.96636 | 0.88829 | 0.078054 | 1.0367e-05 | 0
[13 empty] | 7:24 | 0.97811 | 0.91146 | 0.91784 |  | 7:24 | 0 | 0.15298 | 550.7423 | 7:24 | 0.96694 | 0.88883 | 0.078102 | 1.0374e-05 | 0
[13 empty] | 7:25 | 0.96585 | 0.91146 | 0.91784 |  | 7:25 | 0 | 0.15298 | 550.7423 | 7:25 | 0.96754 | 0.88938 | 0.07815 | 1.038e-05 | 0
[13 empty] | 7:25 | 0.95385 | 0.91146 | 0.91784 |  | 7:25 | 0 | 0.15298 | 550.7423 | 7:25 | 0.96811 | 0.8899 | 0.078197 | 1.0386e-05 | 0
[13 empty] | 7:25 | 0.94209 | 0.91146 | 0.91784 |  | 7:25 | 0 | 0.15298 | 550.7423 | 7:25 | 0.96869 | 0.89043 | 0.078243 | 1.0392e-05 | 0
[13 empty] | 7:26 | 0.93058 | 0.91146 | 0.91784 |  | 7:26 | 0 | 0.15298 | 550.7423 | 7:26 | 0.96925 | 0.89095 | 0.078289 | 1.0398e-05 | 0
[13 empty] | 7:26 | 0.9193 | 0.91146 | 0.91784 |  | 7:26 | 0 | 0.15298 | 550.7423 | 7:26 | 0.96981 | 0.89147 | 0.078333 | 1.0404e-05 | 0
[13 empty] | 7:26 | 0.90825 | 0.91146 | 0.91784 |  | 7:26 | 0 | 0.15298 | 550.7423 | 7:26 | 0.97035 | 0.89196 | 0.078377 | 1.041e-05 | 0
[13 empty] | 7:26 | 0.89743 | 0.91146 | 0.91784 |  | 7:26 | 0 | 0.15298 | 550.7423 | 7:26 | 0.97089 | 0.89246 | 0.078421 | 1.0416e-05 | 0
[13 empty] | 7:26 | 0.88683 | 0.91146 | 0.91784 |  | 7:26 | 0 | 0.15298 | 550.7423 | 7:26 | 0.97143 | 0.89295 | 0.078465 | 1.0422e-05 | 0
[13 empty] | 7:27 | 0.87645 | 0.91146 | 0.91784 |  | 7:27 | 0 | 0.15298 | 550.7423 | 7:27 | 0.97197 | 0.89345 | 0.078507 | 1.0427e-05 | 0
[13 empty] | 7:27 | 0.86628 | 0.91146 | 0.91784 |  | 7:27 | 0 | 0.15298 | 550.7423 | 7:27 | 0.97249 | 0.89393 | 0.078551 | 1.0433e-05 | 0
[13 empty] | 7:27 | 0.85633 | 0.91146 | 0.91784 |  | 7:27 | 0 | 0.15298 | 550.7423 | 7:27 | 0.97301 | 0.89441 | 0.078593 | 1.0439e-05 | 0
[13 empty] | 7:28 | 0.84657 | 0.91146 | 0.91784 |  | 7:28 | 0 | 0.15298 | 550.7423 | 7:28 | 0.97353 | 0.89488 | 0.078633 | 1.0444e-05 | 0
[13 empty] | 7:28 | 0.83702 | 0.91146 | 0.91784 |  | 7:28 | 0 | 0.15298 | 550.7423 | 7:28 | 0.97403 | 0.89534 | 0.078675 | 1.045e-05 | 0
[13 empty] | 7:28 | 0.82766 | 0.91146 | 0.91784 |  | 7:28 | 0 | 0.15298 | 550.7423 | 7:28 | 0.97453 | 0.8958 | 0.078715 | 1.0455e-05 | 0
[13 empty] | 7:28 | 0.8185 | 0.91146 | 0.91784 |  | 7:28 | 0 | 0.15298 | 550.7423 | 7:28 | 0.97502 | 0.89626 | 0.078755 | 1.046e-05 | 0
[13 empty] | 7:28 | 0.80952 | 0.91146 | 0.91784 |  | 7:28 | 0 | 0.15298 | 550.7423 | 7:28 | 0.9755 | 0.8967 | 0.078795 | 1.0466e-05 | 0
[13 empty] | 7:29 | 0.80073 | 0.91146 | 0.91784 |  | 7:29 | 0 | 0.15298 | 550.7423 | 7:29 | 0.976 | 0.89716 | 0.078833 | 1.0471e-05 | 0
[13 empty] | 7:29 | 0.79211 | 0.91146 | 0.91784 |  | 7:29 | 0 | 0.15298 | 550.7423 | 7:29 | 0.97648 | 0.8976 | 0.078871 | 1.0476e-05 | 0
[13 empty] | 7:29 | 0.78368 | 0.91146 | 0.91784 |  | 7:29 | 0 | 0.15298 | 550.7423 | 7:29 | 0.97696 | 0.89803 | 0.07891 | 1.0481e-05 | 0
[13 empty] | 7:30 | 0.77542 | 0.91146 | 0.91784 |  | 7:30 | 0 | 0.15298 | 550.7423 | 7:30 | 0.97741 | 0.89846 | 0.078948 | 1.0486e-05 | 0
[13 empty] | 7:30 | 0.76733 | 0.91146 | 0.91784 |  | 7:30 | 0 | 0.15298 | 550.7423 | 7:30 | 0.97789 | 0.89889 | 0.078986 | 1.0491e-05 | 0
[13 empty] | 7:30 | 0.7594 | 0.91146 | 0.91784 |  | 7:30 | 0 | 0.15298 | 550.7423 | 7:30 | 0.97835 | 0.89931 | 0.079022 | 1.0496e-05 | 0
[13 empty] | 7:30 | 0.75164 | 0.91146 | 0.91784 |  | 7:30 | 0 | 0.15298 | 550.7423 | 7:30 | 0.97881 | 0.89973 | 0.079061 | 1.0501e-05 | 0
[13 empty] | 7:30 | 0.74403 | 0.91146 | 0.91784 |  | 7:30 | 0 | 0.15298 | 550.7423 | 7:30 | 0.97924 | 0.90014 | 0.079097 | 1.0506e-05 | 0
[13 empty] | 7:31 | 0.73658 | 0.91146 | 0.91784 |  | 7:31 | 0 | 0.15298 | 550.7423 | 7:31 | 0.9797 | 0.90056 | 0.079133 | 1.0511e-05 | 0
[13 empty] | 7:31 | 0.72929 | 0.91146 | 0.91784 |  | 7:31 | 0 | 0.15298 | 550.7423 | 7:31 | 0.98014 | 0.90096 | 0.079167 | 1.0515e-05 | 0
[13 empty] | 7:31 | 1.1629 | 0.91146 | 0.91784 |  | 7:31 | 0 | 0.15298 | 550.7423 | 7:31 | 0.98084 | 0.90161 | 0.079225 | 1.0523e-05 | 0
[13 empty] | 7:32 | 1.1468 | 0.91146 | 0.91784 |  | 7:32 | 0 | 0.15298 | 550.7423 | 7:32 | 0.98153 | 0.90224 | 0.07928 | 1.053e-05 | 0
[13 empty] | 7:32 | 1.1311 | 0.91146 | 0.91784 |  | 7:32 | 0 | 0.15298 | 550.7423 | 7:32 | 0.98221 | 0.90287 | 0.079336 | 1.0538e-05 | 0
[13 empty] | 7:32 | 1.1157 | 0.91146 | 0.91784 |  | 7:32 | 0 | 0.15298 | 550.7423 | 7:32 | 0.9829 | 0.9035 | 0.079391 | 1.0545e-05 | 0
[13 empty] | 7:32 | 1.1006 | 0.91146 | 0.91784 |  | 7:32 | 0 | 0.15298 | 550.7423 | 7:32 | 0.98356 | 0.90411 | 0.079444 | 1.0552e-05 | 0
[13 empty] | 7:32 | 1.0859 | 0.91146 | 0.91784 |  | 7:32 | 0 | 0.15298 | 550.7423 | 7:32 | 0.98423 | 0.90472 | 0.079498 | 1.0559e-05 | 0
[13 empty] | 7:33 | 1.0714 | 0.91146 | 0.91784 |  | 7:33 | 0 | 0.15298 | 550.7423 | 7:33 | 0.98487 | 0.90531 | 0.079549 | 1.0566e-05 | 0
[13 empty] | 7:33 | 1.0572 | 0.91146 | 0.91784 |  | 7:33 | 0 | 0.15298 | 550.7423 | 7:33 | 0.98552 | 0.9059 | 0.079601 | 1.0573e-05 | 0
[13 empty] | 7:33 | 1.0434 | 0.91146 | 0.91784 |  | 7:33 | 0 | 0.15298 | 550.7423 | 7:33 | 0.98614 | 0.90648 | 0.079653 | 1.058e-05 | 0
[13 empty] | 7:34 | 1.0298 | 0.91146 | 0.91784 |  | 7:34 | 0 | 0.15298 | 550.7423 | 7:34 | 0.98676 | 0.90705 | 0.079702 | 1.0586e-05 | 0
[13 empty] | 7:34 | 1.0164 | 0.91146 | 0.91784 |  | 7:34 | 0 | 0.15298 | 550.7423 | 7:34 | 0.98738 | 0.90762 | 0.079752 | 1.0593e-05 | 0
[13 empty] | 7:34 | 1.0034 | 0.91146 | 0.91784 |  | 7:34 | 0 | 0.15298 | 550.7423 | 7:34 | 0.98799 | 0.90818 | 0.079802 | 1.06e-05 | 0
[13 empty] | 7:34 | 0.99062 | 0.91146 | 0.91784 |  | 7:34 | 0 | 0.15298 | 550.7423 | 7:34 | 0.98859 | 0.90873 | 0.079849 | 1.0606e-05 | 0
[13 empty] | 7:34 | 0.97811 | 0.91146 | 0.91784 |  | 7:34 | 0 | 0.15298 | 550.7423 | 7:34 | 0.98917 | 0.90926 | 0.079899 | 1.0612e-05 | 0
[13 empty] | 7:35 | 0.96585 | 0.91146 | 0.91784 |  | 7:35 | 0 | 0.15298 | 550.7423 | 7:35 | 0.98976 | 0.9098 | 0.079945 | 1.0618e-05 | 0
[13 empty] | 7:35 | 0.95385 | 0.91146 | 0.91784 |  | 7:35 | 0 | 0.15298 | 550.7423 | 7:35 | 0.99034 | 0.91033 | 0.079993 | 1.0625e-05 | 0
[13 empty] | 7:35 | 0.94209 | 0.91146 | 0.91784 |  | 7:35 | 0 | 0.15298 | 550.7423 | 7:35 | 0.99092 | 0.91087 | 0.080038 | 1.0631e-05 | 0
[13 empty] | 7:36 | 0.93058 | 0.91146 | 0.91784 |  | 7:36 | 0 | 0.15298 | 550.7423 | 7:36 | 0.99148 | 0.91138 | 0.080084 | 1.0637e-05 | 0
[13 empty] | 7:36 | 0.9193 | 0.91146 | 0.91784 |  | 7:36 | 0 | 0.15298 | 550.7423 | 7:36 | 0.99204 | 0.9119 | 0.080128 | 1.0643e-05 | 0
[13 empty] | 7:36 | 0.90825 | 0.91146 | 0.91784 |  | 7:36 | 0 | 0.15298 | 550.7423 | 7:36 | 0.99258 | 0.9124 | 0.080172 | 1.0649e-05 | 0
[13 empty] | 7:36 | 0.89743 | 0.91146 | 0.91784 |  | 7:36 | 0 | 0.15298 | 550.7423 | 7:36 | 0.99312 | 0.91289 | 0.080216 | 1.0655e-05 | 0
[13 empty] | 7:36 | 0.88683 | 0.91146 | 0.91784 |  | 7:36 | 0 | 0.15298 | 550.7423 | 7:36 | 0.99366 | 0.91339 | 0.08026 | 1.066e-05 | 0
[13 empty] | 7:37 | 0.87645 | 0.91146 | 0.91784 |  | 7:37 | 0 | 0.15298 | 550.7423 | 7:37 | 0.9942 | 0.91389 | 0.080304 | 1.0666e-05 | 0
[13 empty] | 7:37 | 0.86628 | 0.91146 | 0.91784 |  | 7:37 | 0 | 0.15298 | 550.7423 | 7:37 | 0.99472 | 0.91436 | 0.080346 | 1.0672e-05 | 0
[13 empty] | 7:37 | 0.85633 | 0.91146 | 0.91784 |  | 7:37 | 0 | 0.15298 | 550.7423 | 7:37 | 0.99524 | 0.91484 | 0.080388 | 1.0677e-05 | 0
[13 empty] | 7:38 | 0.84657 | 0.91146 | 0.91784 |  | 7:38 | 0 | 0.15298 | 550.7423 | 7:38 | 0.99574 | 0.9153 | 0.080428 | 1.0683e-05 | 0
[13 empty] | 7:38 | 0.83702 | 0.91146 | 0.91784 |  | 7:38 | 0 | 0.15298 | 550.7423 | 7:38 | 0.99626 | 0.91578 | 0.08047 | 1.0688e-05 | 0
[13 empty] | 7:38 | 0.82766 | 0.91146 | 0.91784 |  | 7:38 | 0 | 0.15298 | 550.7423 | 7:38 | 0.99676 | 0.91624 | 0.08051 | 1.0693e-05 | 0
[13 empty] | 7:38 | 0.8185 | 0.91146 | 0.91784 |  | 7:38 | 0 | 0.15298 | 550.7423 | 7:38 | 0.99726 | 0.91669 | 0.08055 | 1.0699e-05 | 0
[13 empty] | 7:38 | 0.80952 | 0.91146 | 0.91784 |  | 7:38 | 0 | 0.15298 | 550.7423 | 7:38 | 0.99773 | 0.91713 | 0.08059 | 1.0704e-05 | 0
[13 empty] | 7:39 | 0.80073 | 0.91146 | 0.91784 |  | 7:39 | 0 | 0.15298 | 550.7423 | 7:39 | 0.99823 | 0.91759 | 0.080629 | 1.0709e-05 | 0
[13 empty] | 7:39 | 0.79211 | 0.91146 | 0.91784 |  | 7:39 | 0 | 0.15298 | 550.7423 | 7:39 | 0.99871 | 0.91803 | 0.080667 | 1.0715e-05 | 0
[13 empty] | 7:39 | 0.78368 | 0.91146 | 0.91784 |  | 7:39 | 0 | 0.15298 | 550.7423 | 7:39 | 0.99919 | 0.91847 | 0.080705 | 1.0719e-05 | 0
[13 empty] | 7:39 | 0.77542 | 0.91146 | 0.91784 |  | 7:39 | 0 | 0.15298 | 550.7423 | 7:39 | 0.99964 | 0.91889 | 0.080743 | 1.0725e-05 | 0
[13 empty] | 7:40 | 0.76733 | 0.91146 | 0.91784 |  | 7:40 | 0 | 0.15298 | 550.7423 | 7:40 | 1.0001 | 0.91933 | 0.080781 | 1.073e-05 | 0
[13 empty] | 7:40 | 0.7594 | 0.91146 | 0.91784 |  | 7:40 | 0 | 0.15298 | 550.7423 | 7:40 | 1.0006 | 0.91975 | 0.080818 | 1.0735e-05 | 0
[13 empty] | 7:40 | 0.75164 | 0.91146 | 0.91784 |  | 7:40 | 0 | 0.15298 | 550.7423 | 7:40 | 1.001 | 0.92017 | 0.080856 | 1.0739e-05 | 0
[13 empty] | 7:40 | 0.74403 | 0.91146 | 0.91784 |  | 7:40 | 0 | 0.15298 | 550.7423 | 7:40 | 1.0015 | 0.92057 | 0.080892 | 1.0744e-05 | 0
[13 empty] | 7:41 | 0.73658 | 0.91146 | 0.91784 |  | 7:41 | 0 | 0.15298 | 550.7423 | 7:41 | 1.0019 | 0.92099 | 0.080928 | 1.0749e-05 | 0
[13 empty] | 7:41 | 0.72929 | 0.91146 | 0.91784 |  | 7:41 | 0 | 0.15298 | 550.7423 | 7:41 | 1.0024 | 0.92139 | 0.080963 | 1.0754e-05 | 0
[13 empty] | 7:41 | 1.1629 | 0.91146 | 0.91784 |  | 7:41 | 0 | 0.15298 | 550.7423 | 7:41 | 1.0031 | 0.92204 | 0.08102 | 1.0761e-05 | 0
[13 empty] | 7:41 | 1.1468 | 0.91146 | 0.91784 |  | 7:41 | 0 | 0.15298 | 550.7423 | 7:41 | 1.0038 | 0.92267 | 0.081075 | 1.0769e-05 | 0
[13 empty] | 7:42 | 1.1311 | 0.91146 | 0.91784 |  | 7:42 | 0 | 0.15298 | 550.7423 | 7:42 | 1.0044 | 0.9233 | 0.081131 | 1.0776e-05 | 0
[13 empty] | 7:42 | 1.1157 | 0.91146 | 0.91784 |  | 7:42 | 0 | 0.15298 | 550.7423 | 7:42 | 1.0051 | 0.92393 | 0.081186 | 1.0783e-05 | 0
[13 empty] | 7:42 | 1.1006 | 0.91146 | 0.91784 |  | 7:42 | 0 | 0.15298 | 550.7423 | 7:42 | 1.0058 | 0.92454 | 0.08124 | 1.0791e-05 | 0
[13 empty] | 7:42 | 1.0859 | 0.91146 | 0.91784 |  | 7:42 | 0 | 0.15298 | 550.7423 | 7:42 | 1.0064 | 0.92514 | 0.081293 | 1.0798e-05 | 0
[13 empty] | 7:43 | 1.0714 | 0.91146 | 0.91784 |  | 7:43 | 0 | 0.15298 | 550.7423 | 7:43 | 1.0071 | 0.92575 | 0.081345 | 1.0804e-05 | 0
[13 empty] | 7:43 | 1.0572 | 0.91146 | 0.91784 |  | 7:43 | 0 | 0.15298 | 550.7423 | 7:43 | 1.0077 | 0.92632 | 0.081396 | 1.0811e-05 | 0
[13 empty] | 7:43 | 1.0434 | 0.91146 | 0.91784 |  | 7:43 | 0 | 0.15298 | 550.7423 | 7:43 | 1.0084 | 0.92691 | 0.081448 | 1.0818e-05 | 0
[13 empty] | 7:43 | 1.0298 | 0.91146 | 0.91784 |  | 7:43 | 0 | 0.15298 | 550.7423 | 7:43 | 1.009 | 0.92748 | 0.081498 | 1.0825e-05 | 0
[13 empty] | 7:44 | 1.0164 | 0.91146 | 0.91784 |  | 7:44 | 0 | 0.15298 | 550.7423 | 7:44 | 1.0096 | 0.92804 | 0.081549 | 1.0831e-05 | 0
[13 empty] | 7:44 | 1.0034 | 0.91146 | 0.91784 |  | 7:44 | 0 | 0.15298 | 550.7423 | 7:44 | 1.0102 | 0.92861 | 0.081597 | 1.0838e-05 | 0
[13 empty] | 7:44 | 0.99062 | 0.91146 | 0.91784 |  | 7:44 | 0 | 0.15298 | 550.7423 | 7:44 | 1.0108 | 0.92917 | 0.081646 | 1.0844e-05 | 0
[13 empty] | 7:44 | 0.97811 | 0.91146 | 0.91784 |  | 7:44 | 0 | 0.15298 | 550.7423 | 7:44 | 1.0114 | 0.9297 | 0.081694 | 1.0851e-05 | 0
[13 empty] | 7:45 | 0.96585 | 0.91146 | 0.91784 |  | 7:45 | 0 | 0.15298 | 550.7423 | 7:45 | 1.012 | 0.93024 | 0.08174 | 1.0857e-05 | 0
[13 empty] | 7:45 | 0.95385 | 0.91146 | 0.91784 |  | 7:45 | 0 | 0.15298 | 550.7423 | 7:45 | 1.0126 | 0.93077 | 0.081788 | 1.0863e-05 | 0
[13 empty] | 7:45 | 0.94209 | 0.91146 | 0.91784 |  | 7:45 | 0 | 0.15298 | 550.7423 | 7:45 | 1.0131 | 0.93129 | 0.081834 | 1.0869e-05 | 0
[13 empty] | 7:45 | 0.93058 | 0.91146 | 0.91784 |  | 7:45 | 0 | 0.15298 | 550.7423 | 7:45 | 1.0137 | 0.93182 | 0.081879 | 1.0875e-05 | 0
[13 empty] | 7:46 | 0.9193 | 0.91146 | 0.91784 |  | 7:46 | 0 | 0.15298 | 550.7423 | 7:46 | 1.0143 | 0.93232 | 0.081923 | 1.0881e-05 | 0
[13 empty] | 7:46 | 0.90825 | 0.91146 | 0.91784 |  | 7:46 | 0 | 0.15298 | 550.7423 | 7:46 | 1.0148 | 0.93283 | 0.081969 | 1.0887e-05 | 0
[13 empty] | 7:46 | 0.89743 | 0.91146 | 0.91784 |  | 7:46 | 0 | 0.15298 | 550.7423 | 7:46 | 1.0154 | 0.93333 | 0.082011 | 1.0893e-05 | 0
[13 empty] | 7:46 | 0.88683 | 0.91146 | 0.91784 |  | 7:46 | 0 | 0.15298 | 550.7423 | 7:46 | 1.0159 | 0.93383 | 0.082055 | 1.0899e-05 | 0
[13 empty] | 7:47 | 0.87645 | 0.91146 | 0.91784 |  | 7:47 | 0 | 0.15298 | 550.7423 | 7:47 | 1.0164 | 0.9343 | 0.082099 | 1.0905e-05 | 0
[13 empty] | 7:47 | 0.86628 | 0.91146 | 0.91784 |  | 7:47 | 0 | 0.15298 | 550.7423 | 7:47 | 1.017 | 0.9348 | 0.082141 | 1.091e-05 | 0
[13 empty] | 7:47 | 0.85633 | 0.91146 | 0.91784 |  | 7:47 | 0 | 0.15298 | 550.7423 | 7:47 | 1.0175 | 0.93528 | 0.082183 | 1.0916e-05 | 0
[13 empty] | 7:48 | 0.84657 | 0.91146 | 0.91784 |  | 7:48 | 0 | 0.15298 | 550.7423 | 7:48 | 1.018 | 0.93574 | 0.082223 | 1.0921e-05 | 0
[13 empty] | 7:48 | 0.83702 | 0.91146 | 0.91784 |  | 7:48 | 0 | 0.15298 | 550.7423 | 7:48 | 1.0185 | 0.93621 | 0.082265 | 1.0927e-05 | 0
[13 empty] | 7:48 | 0.82766 | 0.91146 | 0.91784 |  | 7:48 | 0 | 0.15298 | 550.7423 | 7:48 | 1.019 | 0.93667 | 0.082305 | 1.0932e-05 | 0
[13 empty] | 7:48 | 0.8185 | 0.91146 | 0.91784 |  | 7:48 | 0 | 0.15298 | 550.7423 | 7:48 | 1.0195 | 0.93713 | 0.082345 | 1.0937e-05 | 0
[13 empty] | 7:48 | 0.80952 | 0.91146 | 0.91784 |  | 7:48 | 0 | 0.15298 | 550.7423 | 7:48 | 1.02 | 0.93757 | 0.082386 | 1.0943e-05 | 0
[13 empty] | 7:49 | 0.80073 | 0.91146 | 0.91784 |  | 7:49 | 0 | 0.15298 | 550.7423 | 7:49 | 1.0205 | 0.93803 | 0.082424 | 1.0948e-05 | 0
[13 empty] | 7:49 | 0.79211 | 0.91146 | 0.91784 |  | 7:49 | 0 | 0.15298 | 550.7423 | 7:49 | 1.0209 | 0.93847 | 0.082464 | 1.0953e-05 | 0
[13 empty] | 7:49 | 0.78368 | 0.91146 | 0.91784 |  | 7:49 | 0 | 0.15298 | 550.7423 | 7:49 | 1.0214 | 0.93889 | 0.082502 | 1.0958e-05 | 0
[13 empty] | 7:50 | 0.77542 | 0.91146 | 0.91784 |  | 7:50 | 0 | 0.15298 | 550.7423 | 7:50 | 1.0219 | 0.93933 | 0.082538 | 1.0963e-05 | 0
[13 empty] | 7:50 | 0.76733 | 0.91146 | 0.91784 |  | 7:50 | 0 | 0.15298 | 550.7423 | 7:50 | 1.0223 | 0.93975 | 0.082577 | 1.0968e-05 | 0
[13 empty] | 7:50 | 0.7594 | 0.91146 | 0.91784 |  | 7:50 | 0 | 0.15298 | 550.7423 | 7:50 | 1.0228 | 0.94017 | 0.082615 | 1.0973e-05 | 0
[13 empty] | 7:50 | 0.75164 | 0.91146 | 0.91784 |  | 7:50 | 0 | 0.15298 | 550.7423 | 7:50 | 1.0232 | 0.94059 | 0.082651 | 1.0978e-05 | 0
[13 empty] | 7:50 | 0.74403 | 0.91146 | 0.91784 |  | 7:50 | 0 | 0.15298 | 550.7423 | 7:50 | 1.0237 | 0.94101 | 0.082687 | 1.0983e-05 | 0
[13 empty] | 7:51 | 0.73658 | 0.91146 | 0.91784 |  | 7:51 | 0 | 0.15298 | 550.7423 | 7:51 | 1.0242 | 0.94143 | 0.082724 | 1.0987e-05 | 0
[13 empty] | 7:51 | 0.72929 | 0.91146 | 0.91784 |  | 7:51 | 0 | 0.15298 | 550.7423 | 7:51 | 1.0246 | 0.94183 | 0.082758 | 1.0992e-05 | 0
[13 empty] | 7:51 | 1.1629 | 0.91146 | 0.91784 |  | 7:51 | 0 | 0.15298 | 550.7423 | 7:51 | 1.0253 | 0.94248 | 0.082815 | 1.1e-05 | 0
[13 empty] | 7:52 | 1.1468 | 0.91146 | 0.91784 |  | 7:52 | 0 | 0.15298 | 550.7423 | 7:52 | 1.026 | 0.94311 | 0.082871 | 1.1007e-05 | 0
[13 empty] | 7:52 | 1.1311 | 0.91146 | 0.91784 |  | 7:52 | 0 | 0.15298 | 550.7423 | 7:52 | 1.0267 | 0.94374 | 0.082926 | 1.1015e-05 | 0
[13 empty] | 7:52 | 1.1157 | 0.91146 | 0.91784 |  | 7:52 | 0 | 0.15298 | 550.7423 | 7:52 | 1.0274 | 0.94437 | 0.082981 | 1.1022e-05 | 0
[13 empty] | 7:52 | 1.1006 | 0.91146 | 0.91784 |  | 7:52 | 0 | 0.15298 | 550.7423 | 7:52 | 1.028 | 0.94498 | 0.083035 | 1.1029e-05 | 0
[13 empty] | 7:52 | 1.0859 | 0.91146 | 0.91784 |  | 7:52 | 0 | 0.15298 | 550.7423 | 7:52 | 1.0287 | 0.94557 | 0.083088 | 1.1036e-05 | 0
[13 empty] | 7:53 | 1.0714 | 0.91146 | 0.91784 |  | 7:53 | 0 | 0.15298 | 550.7423 | 7:53 | 1.0293 | 0.94616 | 0.08314 | 1.1043e-05 | 0
[13 empty] | 7:53 | 1.0572 | 0.91146 | 0.91784 |  | 7:53 | 0 | 0.15298 | 550.7423 | 7:53 | 1.03 | 0.94676 | 0.083192 | 1.105e-05 | 0
[13 empty] | 7:53 | 1.0434 | 0.91146 | 0.91784 |  | 7:53 | 0 | 0.15298 | 550.7423 | 7:53 | 1.0306 | 0.94735 | 0.083243 | 1.1057e-05 | 0
[13 empty] | 7:54 | 1.0298 | 0.91146 | 0.91784 |  | 7:54 | 0 | 0.15298 | 550.7423 | 7:54 | 1.0312 | 0.94792 | 0.083295 | 1.1063e-05 | 0
[13 empty] | 7:54 | 1.0164 | 0.91146 | 0.91784 |  | 7:54 | 0 | 0.15298 | 550.7423 | 7:54 | 1.0318 | 0.94847 | 0.083344 | 1.107e-05 | 0
[13 empty] | 7:54 | 1.0034 | 0.91146 | 0.91784 |  | 7:54 | 0 | 0.15298 | 550.7423 | 7:54 | 1.0325 | 0.94905 | 0.083392 | 1.1076e-05 | 0
[13 empty] | 7:54 | 0.99062 | 0.91146 | 0.91784 |  | 7:54 | 0 | 0.15298 | 550.7423 | 7:54 | 1.033 | 0.94958 | 0.083442 | 1.1083e-05 | 0
[13 empty] | 7:54 | 0.97811 | 0.91146 | 0.91784 |  | 7:54 | 0 | 0.15298 | 550.7423 | 7:54 | 1.0336 | 0.95014 | 0.083489 | 1.1089e-05 | 0
[13 empty] | 7:55 | 0.96585 | 0.91146 | 0.91784 |  | 7:55 | 0 | 0.15298 | 550.7423 | 7:55 | 1.0342 | 0.95067 | 0.083535 | 1.1096e-05 | 0
[13 empty] | 7:55 | 0.95385 | 0.91146 | 0.91784 |  | 7:55 | 0 | 0.15298 | 550.7423 | 7:55 | 1.0348 | 0.95121 | 0.083583 | 1.1102e-05 | 0
[13 empty] | 7:55 | 0.94209 | 0.91146 | 0.91784 |  | 7:55 | 0 | 0.15298 | 550.7423 | 7:55 | 1.0354 | 0.95172 | 0.083629 | 1.1108e-05 | 0
[13 empty] | 7:56 | 0.93058 | 0.91146 | 0.91784 |  | 7:56 | 0 | 0.15298 | 550.7423 | 7:56 | 1.0359 | 0.95224 | 0.083675 | 1.1114e-05 | 0
[13 empty] | 7:56 | 0.9193 | 0.91146 | 0.91784 |  | 7:56 | 0 | 0.15298 | 550.7423 | 7:56 | 1.0365 | 0.95275 | 0.083719 | 1.112e-05 | 0
[13 empty] | 7:56 | 0.90825 | 0.91146 | 0.91784 |  | 7:56 | 0 | 0.15298 | 550.7423 | 7:56 | 1.037 | 0.95327 | 0.083765 | 1.1126e-05 | 0
[13 empty] | 7:56 | 0.89743 | 0.91146 | 0.91784 |  | 7:56 | 0 | 0.15298 | 550.7423 | 7:56 | 1.0376 | 0.95376 | 0.083808 | 1.1131e-05 | 0
[13 empty] | 7:56 | 0.88683 | 0.91146 | 0.91784 |  | 7:56 | 0 | 0.15298 | 550.7423 | 7:56 | 1.0381 | 0.95426 | 0.08385 | 1.1137e-05 | 0
[13 empty] | 7:57 | 0.87645 | 0.91146 | 0.91784 |  | 7:57 | 0 | 0.15298 | 550.7423 | 7:57 | 1.0386 | 0.95474 | 0.083894 | 1.1143e-05 | 0
[13 empty] | 7:57 | 0.86628 | 0.91146 | 0.91784 |  | 7:57 | 0 | 0.15298 | 550.7423 | 7:57 | 1.0392 | 0.95522 | 0.083936 | 1.1149e-05 | 0
[13 empty] | 7:57 | 0.85633 | 0.91146 | 0.91784 |  | 7:57 | 0 | 0.15298 | 550.7423 | 7:57 | 1.0397 | 0.95569 | 0.083978 | 1.1154e-05 | 0
[13 empty] | 7:58 | 0.84657 | 0.91146 | 0.91784 |  | 7:58 | 0 | 0.15298 | 550.7423 | 7:58 | 1.0402 | 0.95617 | 0.084019 | 1.116e-05 | 0
[13 empty] | 7:58 | 0.83702 | 0.91146 | 0.91784 |  | 7:58 | 0 | 0.15298 | 550.7423 | 7:58 | 1.0407 | 0.95663 | 0.084061 | 1.1165e-05 | 0
[13 empty] | 7:58 | 0.82766 | 0.91146 | 0.91784 |  | 7:58 | 0 | 0.15298 | 550.7423 | 7:58 | 1.0412 | 0.95711 | 0.084101 | 1.117e-05 | 0
[13 empty] | 7:58 | 0.8185 | 0.91146 | 0.91784 |  | 7:58 | 0 | 0.15298 | 550.7423 | 7:58 | 1.0417 | 0.95755 | 0.084141 | 1.1176e-05 | 0
[13 empty] | 7:58 | 0.80952 | 0.91146 | 0.91784 |  | 7:58 | 0 | 0.15298 | 550.7423 | 7:58 | 1.0422 | 0.958 | 0.084181 | 1.1181e-05 | 0
[13 empty] | 7:59 | 0.80073 | 0.91146 | 0.91784 |  | 7:59 | 0 | 0.15298 | 550.7423 | 7:59 | 1.0427 | 0.95844 | 0.084219 | 1.1186e-05 | 0
[13 empty] | 7:59 | 0.79211 | 0.91146 | 0.91784 |  | 7:59 | 0 | 0.15298 | 550.7423 | 7:59 | 1.0432 | 0.95888 | 0.084259 | 1.1191e-05 | 0
[13 empty] | 7:59 | 0.78368 | 0.91146 | 0.91784 |  | 7:59 | 0 | 0.15298 | 550.7423 | 7:59 | 1.0436 | 0.95932 | 0.084297 | 1.1197e-05 | 0
[13 empty] | 8:00 | 0.77542 | 0.91146 | 0.91784 |  | 8:00 | 0 | 0.15298 | 550.7423 | 8:00 | 1.0441 | 0.95976 | 0.084334 | 1.1202e-05 | 0
[13 empty] | 8:00 | 0.76733 | 0.91146 | 0.91784 |  | 8:00 | 0 | 0.15298 | 550.7423 | 8:00 | 1.0446 | 0.96018 | 0.084372 | 1.1206e-05 | 0
[13 empty] | 8:00 | 0.7594 | 0.91146 | 0.91784 |  | 8:00 | 0 | 0.15298 | 550.7423 | 8:00 | 1.045 | 0.9606 | 0.08441 | 1.1211e-05 | 0
[13 empty] | 8:00 | 0.75164 | 0.91146 | 0.91784 |  | 8:00 | 0.75552 | 0.15298 | 556.4089 | 8:00 | 1.0455 | 0.96102 | 0.084446 | 1.1216e-05 | 0
[13 empty] | 8:00 | 0.74403 | 0.91146 | 0.91784 |  | 8:00 | 0.74784 | 0.15298 | 567.6847 | 8:00 | 1.0459 | 0.96144 | 0.084483 | 1.1221e-05 | 0
[13 empty] | 8:01 | 0.73658 | 0.91146 | 0.91784 |  | 8:01 | 0.74031 | 0.15298 | 578.8459 | 8:01 | 1.0464 | 0.96184 | 0.084519 | 1.1226e-05 | 0
[13 empty] | 8:01 | 0.72929 | 0.91146 | 0.91784 |  | 8:01 | 0.73294 | 0.15298 | 589.8944 | 8:01 | 1.0468 | 0.96226 | 0.084553 | 1.1231e-05 | 0
[13 empty] | 8:01 | 1.1629 | 0.91146 | 0.91784 |  | 8:01 | 0.94609 | 0.15298 | 602.488 | 8:01 | 1.0475 | 0.96291 | 0.084611 | 1.1238e-05 | 0
[13 empty] | 8:02 | 1.1468 | 0.91146 | 0.91784 |  | 8:02 | 1.1549 | 0.15298 | 618.2444 | 8:02 | 1.0482 | 0.96354 | 0.084668 | 1.1246e-05 | 0
[13 empty] | 8:02 | 1.1311 | 0.91146 | 0.91784 |  | 8:02 | 1.139 | 0.15298 | 635.4484 | 8:02 | 1.0489 | 0.96417 | 0.084723 | 1.1253e-05 | 0
[13 empty] | 8:02 | 1.1157 | 0.91146 | 0.91784 |  | 8:02 | 1.1234 | 0.15298 | 652.4156 | 8:02 | 1.0496 | 0.96478 | 0.084777 | 1.126e-05 | 0
[13 empty] | 8:02 | 1.1006 | 0.91146 | 0.91784 |  | 8:02 | 1.1082 | 0.15298 | 669.1536 | 8:02 | 1.0502 | 0.9654 | 0.08483 | 1.1267e-05 | 0
[13 empty] | 8:02 | 1.0859 | 0.91146 | 0.91784 |  | 8:02 | 1.0933 | 0.15298 | 685.6643 | 8:02 | 1.0509 | 0.96601 | 0.084884 | 1.1274e-05 | 0
[13 empty] | 8:03 | 1.0714 | 0.91146 | 0.91784 |  | 8:03 | 1.0786 | 0.15298 | 701.9535 | 8:03 | 1.0515 | 0.9666 | 0.084935 | 1.1281e-05 | 0
[13 empty] | 8:03 | 1.0572 | 0.91146 | 0.91784 |  | 8:03 | 1.0643 | 0.15298 | 718.025 | 8:03 | 1.0522 | 0.96719 | 0.084989 | 1.1288e-05 | 0
[13 empty] | 8:03 | 1.0434 | 0.91146 | 0.91784 |  | 8:03 | 1.0503 | 0.15298 | 733.8863 | 8:03 | 1.0528 | 0.96778 | 0.085038 | 1.1295e-05 | 0
[13 empty] | 8:04 | 1.0298 | 0.91146 | 0.91784 |  | 8:04 | 1.0366 | 0.15298 | 749.5376 | 8:04 | 1.0535 | 0.96836 | 0.08509 | 1.1302e-05 | 0
[13 empty] | 8:04 | 1.0164 | 0.91146 | 0.91784 |  | 8:04 | 1.0231 | 0.15298 | 764.9846 | 8:04 | 1.0541 | 0.96891 | 0.08514 | 1.1308e-05 | 0
[13 empty] | 8:04 | 1.0034 | 0.91146 | 0.91784 |  | 8:04 | 1.0099 | 0.15298 | 780.231 | 8:04 | 1.0547 | 0.96946 | 0.085187 | 1.1315e-05 | 0
[13 empty] | 8:04 | 0.99062 | 0.91146 | 0.91784 |  | 8:04 | 0.99701 | 0.15298 | 795.2845 | 8:04 | 1.0553 | 0.97002 | 0.085237 | 1.1321e-05 | 0
[13 empty] | 8:04 | 0.97811 | 0.91146 | 0.91784 |  | 8:04 | 0.98437 | 0.15298 | 810.1432 | 8:04 | 1.0559 | 0.97057 | 0.085285 | 1.1328e-05 | 0
[13 empty] | 8:05 | 0.96585 | 0.91146 | 0.91784 |  | 8:05 | 0.97198 | 0.15298 | 824.8167 | 8:05 | 1.0564 | 0.97111 | 0.085331 | 1.1334e-05 | 0
[13 empty] | 8:05 | 0.95385 | 0.91146 | 0.91784 |  | 8:05 | 0.95985 | 0.15298 | 839.3048 | 8:05 | 1.057 | 0.97164 | 0.085378 | 1.134e-05 | 0
[13 empty] | 8:05 | 0.94209 | 0.91146 | 0.91784 |  | 8:05 | 0.94797 | 0.15298 | 853.6135 | 8:05 | 1.0576 | 0.97216 | 0.085424 | 1.1346e-05 | 0
[13 empty] | 8:06 | 0.93058 | 0.91146 | 0.91784 |  | 8:06 | 0.93634 | 0.15298 | 867.7465 | 8:06 | 1.0582 | 0.97267 | 0.08547 | 1.1352e-05 | 0
[13 empty] | 8:06 | 0.9193 | 0.91146 | 0.91784 |  | 8:06 | 0.92494 | 0.15298 | 881.7056 | 8:06 | 1.0587 | 0.97319 | 0.085514 | 1.1358e-05 | 0
[13 empty] | 8:06 | 0.90825 | 0.91146 | 0.91784 |  | 8:06 | 0.91377 | 0.15298 | 895.4967 | 8:06 | 1.0593 | 0.9737 | 0.08556 | 1.1364e-05 | 0
[13 empty] | 8:06 | 0.89743 | 0.91146 | 0.91784 |  | 8:06 | 0.90284 | 0.15298 | 909.1217 | 8:06 | 1.0598 | 0.9742 | 0.085604 | 1.137e-05 | 0
[13 empty] | 8:06 | 0.88683 | 0.91146 | 0.91784 |  | 8:06 | 0.89213 | 0.15298 | 922.5824 | 8:06 | 1.0604 | 0.9747 | 0.085646 | 1.1376e-05 | 0
[13 empty] | 8:07 | 0.87645 | 0.91146 | 0.91784 |  | 8:07 | 0.88164 | 0.15298 | 935.8864 | 8:07 | 1.0609 | 0.97517 | 0.08569 | 1.1381e-05 | 0
[13 empty] | 8:07 | 0.86628 | 0.91146 | 0.91784 |  | 8:07 | 0.87137 | 0.15298 | 949.0339 | 8:07 | 1.0614 | 0.97565 | 0.085732 | 1.1387e-05 | 0
[13 empty] | 8:07 | 0.85633 | 0.91146 | 0.91784 |  | 8:07 | 0.8613 | 0.15298 | 962.0286 | 8:07 | 1.0619 | 0.97613 | 0.085774 | 1.1393e-05 | 0
[13 empty] | 8:08 | 0.84657 | 0.91146 | 0.91784 |  | 8:08 | 0.85145 | 0.15298 | 974.8743 | 8:08 | 1.0624 | 0.97661 | 0.085816 | 1.1398e-05 | 0
[13 empty] | 8:08 | 0.83702 | 0.91146 | 0.91784 |  | 8:08 | 0.8418 | 0.15298 | 987.5749 | 8:08 | 1.0629 | 0.97706 | 0.085856 | 1.1404e-05 | 0
[13 empty] | 8:08 | 0.82766 | 0.91146 | 0.91784 |  | 8:08 | 0.83234 | 0.15298 | 1000.1303 | 8:08 | 1.0634 | 0.97752 | 0.085896 | 1.1409e-05 | 0
[13 empty] | 8:08 | 0.8185 | 0.91146 | 0.91784 |  | 8:08 | 0.82308 | 0.15298 | 1012.5463 | 8:08 | 1.0639 | 0.97798 | 0.085936 | 1.1414e-05 | 0
[13 empty] | 8:08 | 0.80952 | 0.91146 | 0.91784 |  | 8:08 | 0.81401 | 0.15298 | 1024.8248 | 8:08 | 1.0644 | 0.97844 | 0.085976 | 1.1419e-05 | 0
[13 empty] | 8:09 | 0.80073 | 0.91146 | 0.91784 |  | 8:09 | 0.80512 | 0.15298 | 1036.9676 | 8:09 | 1.0649 | 0.97888 | 0.086014 | 1.1425e-05 | 0
[13 empty] | 8:09 | 0.79211 | 0.91146 | 0.91784 |  | 8:09 | 0.79642 | 0.15298 | 1048.9787 | 8:09 | 1.0654 | 0.97932 | 0.086054 | 1.143e-05 | 0
[13 empty] | 8:09 | 0.78368 | 0.91146 | 0.91784 |  | 8:09 | 0.7879 | 0.15298 | 1060.8619 | 8:09 | 1.0659 | 0.97976 | 0.086093 | 1.1435e-05 | 0
[13 empty] | 8:10 | 0.77542 | 0.91146 | 0.91784 |  | 8:10 | 0.77955 | 0.15298 | 1072.6171 | 8:10 | 1.0663 | 0.9802 | 0.086131 | 1.144e-05 | 0
[13 empty] | 8:10 | 0.76733 | 0.91146 | 0.91784 |  | 8:10 | 0.77137 | 0.15298 | 1084.25 | 8:10 | 1.0668 | 0.98062 | 0.086167 | 1.1445e-05 | 0
[13 empty] | 8:10 | 0.7594 | 0.91146 | 0.91784 |  | 8:10 | 0.76336 | 0.15298 | 1095.7588 | 8:10 | 1.0673 | 0.98104 | 0.086205 | 1.145e-05 | 0
[13 empty] | 8:10 | 0.75164 | 0.91146 | 0.91784 |  | 8:10 | 0 | 0.15298 | 1101.4846 | 8:10 | 1.0677 | 0.98146 | 0.086242 | 1.1455e-05 | 0
[13 empty] | 8:10 | 0.74403 | 0.91146 | 0.91784 |  | 8:10 | 0 | 0.15298 | 1101.4846 | 8:10 | 1.0682 | 0.98188 | 0.086278 | 1.146e-05 | 0
[13 empty] | 8:11 | 0.73658 | 0.91146 | 0.91784 |  | 8:11 | 0 | 0.15298 | 1101.4846 | 8:11 | 1.0686 | 0.98228 | 0.086314 | 1.1464e-05 | 0
[13 empty] | 8:11 | 0.72929 | 0.91146 | 0.91784 |  | 8:11 | 0 | 0.15298 | 1101.4846 | 8:11 | 1.069 | 0.98268 | 0.086349 | 1.1469e-05 | 0
[13 empty] | 8:11 | 1.1629 | 0.91146 | 0.91784 |  | 8:11 | 0 | 0.15298 | 1101.4846 | 8:11 | 1.0697 | 0.98333 | 0.086406 | 1.1477e-05 | 0
[13 empty] | 8:12 | 1.1468 | 0.91146 | 0.91784 |  | 8:12 | 0 | 0.15298 | 1101.4846 | 8:12 | 1.0705 | 0.98398 | 0.086463 | 1.1484e-05 | 0
[13 empty] | 8:12 | 1.1311 | 0.91146 | 0.91784 |  | 8:12 | 0 | 0.15298 | 1101.4846 | 8:12 | 1.0711 | 0.98461 | 0.086519 | 1.1491e-05 | 0
[13 empty] | 8:12 | 1.1157 | 0.91146 | 0.91784 |  | 8:12 | 0 | 0.15298 | 1101.4846 | 8:12 | 1.0718 | 0.98522 | 0.086572 | 1.1499e-05 | 0
[13 empty] | 8:12 | 1.1006 | 0.91146 | 0.91784 |  | 8:12 | 0 | 0.15298 | 1101.4846 | 8:12 | 1.0725 | 0.98583 | 0.086625 | 1.1506e-05 | 0
[13 empty] | 8:12 | 1.0859 | 0.91146 | 0.91784 |  | 8:12 | 0 | 0.15298 | 1101.4846 | 8:12 | 1.0731 | 0.98644 | 0.086679 | 1.1513e-05 | 0
[13 empty] | 8:13 | 1.0714 | 0.91146 | 0.91784 |  | 8:13 | 0 | 0.15298 | 1101.4846 | 8:13 | 1.0738 | 0.98703 | 0.086732 | 1.152e-05 | 0
[13 empty] | 8:13 | 1.0572 | 0.91146 | 0.91784 |  | 8:13 | 0 | 0.15298 | 1101.4846 | 8:13 | 1.0744 | 0.98763 | 0.086784 | 1.1527e-05 | 0
[13 empty] | 8:13 | 1.0434 | 0.91146 | 0.91784 |  | 8:13 | 0 | 0.15298 | 1101.4846 | 8:13 | 1.075 | 0.9882 | 0.086834 | 1.1533e-05 | 0
[13 empty] | 8:14 | 1.0298 | 0.91146 | 0.91784 |  | 8:14 | 0 | 0.15298 | 1101.4846 | 8:14 | 1.0757 | 0.98877 | 0.086885 | 1.154e-05 | 0
[13 empty] | 8:14 | 1.0164 | 0.91146 | 0.91784 |  | 8:14 | 0 | 0.15298 | 1101.4846 | 8:14 | 1.0763 | 0.98935 | 0.086935 | 1.1547e-05 | 0
[13 empty] | 8:14 | 1.0034 | 0.91146 | 0.91784 |  | 8:14 | 0 | 0.15298 | 1101.4846 | 8:14 | 1.0769 | 0.9899 | 0.086983 | 1.1553e-05 | 0
[13 empty] | 8:14 | 0.99062 | 0.91146 | 0.91784 |  | 8:14 | 0 | 0.15298 | 1101.4846 | 8:14 | 1.0775 | 0.99045 | 0.087032 | 1.156e-05 | 0
[13 empty] | 8:14 | 0.97811 | 0.91146 | 0.91784 |  | 8:14 | 0 | 0.15298 | 1101.4846 | 8:14 | 1.0781 | 0.99101 | 0.08708 | 1.1566e-05 | 0
[13 empty] | 8:15 | 0.96585 | 0.91146 | 0.91784 |  | 8:15 | 0 | 0.15298 | 1101.4846 | 8:15 | 1.0787 | 0.99154 | 0.087128 | 1.1572e-05 | 0
[13 empty] | 8:15 | 0.95385 | 0.91146 | 0.91784 |  | 8:15 | 0 | 0.15298 | 1101.4846 | 8:15 | 1.0793 | 0.99208 | 0.087174 | 1.1579e-05 | 0
[13 empty] | 8:15 | 0.94209 | 0.91146 | 0.91784 |  | 8:15 | 0 | 0.15298 | 1101.4846 | 8:15 | 1.0798 | 0.99259 | 0.087219 | 1.1585e-05 | 0
[13 empty] | 8:16 | 0.93058 | 0.91146 | 0.91784 |  | 8:16 | 0 | 0.15298 | 1101.4846 | 8:16 | 1.0804 | 0.99311 | 0.087265 | 1.1591e-05 | 0
[13 empty] | 8:16 | 0.9193 | 0.91146 | 0.91784 |  | 8:16 | 0 | 0.15298 | 1101.4846 | 8:16 | 1.0809 | 0.99362 | 0.087309 | 1.1597e-05 | 0
[13 empty] | 8:16 | 0.90825 | 0.91146 | 0.91784 |  | 8:16 | 0 | 0.15298 | 1101.4846 | 8:16 | 1.0815 | 0.99412 | 0.087355 | 1.1603e-05 | 0
[13 empty] | 8:16 | 0.89743 | 0.91146 | 0.91784 |  | 8:16 | 0 | 0.15298 | 1101.4846 | 8:16 | 1.082 | 0.99464 | 0.087399 | 1.1609e-05 | 0
[13 empty] | 8:16 | 0.88683 | 0.91146 | 0.91784 |  | 8:16 | 0 | 0.15298 | 1101.4846 | 8:16 | 1.0826 | 0.99511 | 0.087441 | 1.1614e-05 | 0
[13 empty] | 8:17 | 0.87645 | 0.91146 | 0.91784 |  | 8:17 | 0 | 0.15298 | 1101.4846 | 8:17 | 1.0831 | 0.99561 | 0.087485 | 1.162e-05 | 0
[13 empty] | 8:17 | 0.86628 | 0.91146 | 0.91784 |  | 8:17 | 0 | 0.15298 | 1101.4846 | 8:17 | 1.0836 | 0.99609 | 0.087527 | 1.1626e-05 | 0
[13 empty] | 8:17 | 0.85633 | 0.91146 | 0.91784 |  | 8:17 | 0 | 0.15298 | 1101.4846 | 8:17 | 1.0841 | 0.99656 | 0.087569 | 1.1631e-05 | 0
[13 empty] | 8:18 | 0.84657 | 0.91146 | 0.91784 |  | 8:18 | 0 | 0.15298 | 1101.4846 | 8:18 | 1.0847 | 0.99704 | 0.087611 | 1.1637e-05 | 0
[13 empty] | 8:18 | 0.83702 | 0.91146 | 0.91784 |  | 8:18 | 0 | 0.15298 | 1101.4846 | 8:18 | 1.0852 | 0.9975 | 0.087651 | 1.1642e-05 | 0
[13 empty] | 8:18 | 0.82766 | 0.91146 | 0.91784 |  | 8:18 | 0 | 0.15298 | 1101.4846 | 8:18 | 1.0857 | 0.99796 | 0.087691 | 1.1647e-05 | 0
[13 empty] | 8:18 | 0.8185 | 0.91146 | 0.91784 |  | 8:18 | 0 | 0.15298 | 1101.4846 | 8:18 | 1.0862 | 0.99842 | 0.087731 | 1.1653e-05 | 0
[13 empty] | 8:18 | 0.80952 | 0.91146 | 0.91784 |  | 8:18 | 0 | 0.15298 | 1101.4846 | 8:18 | 1.0867 | 0.99888 | 0.087771 | 1.1658e-05 | 0
[13 empty] | 8:19 | 0.80073 | 0.91146 | 0.91784 |  | 8:19 | 0 | 0.15298 | 1101.4846 | 8:19 | 1.0871 | 0.99931 | 0.08781 | 1.1663e-05 | 0
[13 empty] | 8:19 | 0.79211 | 0.91146 | 0.91784 |  | 8:19 | 0 | 0.15298 | 1101.4846 | 8:19 | 1.0876 | 0.99975 | 0.08785 | 1.1668e-05 | 0
[13 empty] | 8:19 | 0.78368 | 0.91146 | 0.91784 |  | 8:19 | 0 | 0.15298 | 1101.4846 | 8:19 | 1.0881 | 1.0002 | 0.087888 | 1.1673e-05 | 0
[13 empty] | 8:20 | 0.77542 | 0.91146 | 0.91784 |  | 8:20 | 0 | 0.15298 | 1101.4846 | 8:20 | 1.0886 | 1.0006 | 0.087926 | 1.1678e-05 | 0
[13 empty] | 8:20 | 0.76733 | 0.91146 | 0.91784 |  | 8:20 | 0 | 0.15298 | 1101.4846 | 8:20 | 1.089 | 1.0011 | 0.087962 | 1.1683e-05 | 0
[13 empty] | 8:20 | 0.7594 | 0.91146 | 0.91784 |  | 8:20 | 0 | 0.15298 | 1101.4846 | 8:20 | 1.0895 | 1.0015 | 0.088001 | 1.1688e-05 | 0
[13 empty] | 8:20 | 0.75164 | 0.91146 | 0.91784 |  | 8:20 | 0 | 0.15298 | 1101.4846 | 8:20 | 1.0899 | 1.0019 | 0.088037 | 1.1693e-05 | 0
[13 empty] | 8:20 | 0.74403 | 0.91146 | 0.91784 |  | 8:20 | 0 | 0.15298 | 1101.4846 | 8:20 | 1.0904 | 1.0023 | 0.088073 | 1.1698e-05 | 0
[13 empty] | 8:21 | 0.73658 | 0.91146 | 0.91784 |  | 8:21 | 0 | 0.15298 | 1101.4846 | 8:21 | 1.0908 | 1.0027 | 0.088109 | 1.1703e-05 | 0
[13 empty] | 8:21 | 0.72929 | 0.91146 | 0.91784 |  | 8:21 | 0 | 0.15298 | 1101.4846 | 8:21 | 1.0913 | 1.0031 | 0.088146 | 1.1708e-05 | 0
[13 empty] | 8:21 | 1.1629 | 0.91146 | 0.91784 |  | 8:21 | 0 | 0.15298 | 1101.4846 | 8:21 | 1.092 | 1.0038 | 0.088201 | 1.1715e-05 | 0
[13 empty] | 8:22 | 1.1468 | 0.91146 | 0.91784 |  | 8:22 | 0 | 0.15298 | 1101.4846 | 8:22 | 1.0927 | 1.0044 | 0.088258 | 1.1723e-05 | 0
[13 empty] | 8:22 | 1.1311 | 0.91146 | 0.91784 |  | 8:22 | 0 | 0.15298 | 1101.4846 | 8:22 | 1.0934 | 1.005 | 0.088314 | 1.173e-05 | 0
[13 empty] | 8:22 | 1.1157 | 0.91146 | 0.91784 |  | 8:22 | 0 | 0.15298 | 1101.4846 | 8:22 | 1.094 | 1.0057 | 0.088367 | 1.1737e-05 | 0
[13 empty] | 8:22 | 1.1006 | 0.91146 | 0.91784 |  | 8:22 | 0 | 0.15298 | 1101.4846 | 8:22 | 1.0947 | 1.0063 | 0.088421 | 1.1744e-05 | 0
[13 empty] | 8:22 | 1.0859 | 0.91146 | 0.91784 |  | 8:22 | 0 | 0.15298 | 1101.4846 | 8:22 | 1.0954 | 1.0069 | 0.088474 | 1.1751e-05 | 0
[13 empty] | 8:23 | 1.0714 | 0.91146 | 0.91784 |  | 8:23 | 0 | 0.15298 | 1101.4846 | 8:23 | 1.096 | 1.0075 | 0.088528 | 1.1758e-05 | 0
[13 empty] | 8:23 | 1.0572 | 0.91146 | 0.91784 |  | 8:23 | 0 | 0.15298 | 1101.4846 | 8:23 | 1.0967 | 1.0081 | 0.088579 | 1.1765e-05 | 0
[13 empty] | 8:23 | 1.0434 | 0.91146 | 0.91784 |  | 8:23 | 0 | 0.15298 | 1101.4846 | 8:23 | 1.0973 | 1.0086 | 0.088629 | 1.1772e-05 | 0
[13 empty] | 8:24 | 1.0298 | 0.91146 | 0.91784 |  | 8:24 | 0 | 0.15298 | 1101.4846 | 8:24 | 1.0979 | 1.0092 | 0.08868 | 1.1779e-05 | 0
[13 empty] | 8:24 | 1.0164 | 0.91146 | 0.91784 |  | 8:24 | 0 | 0.15298 | 1101.4846 | 8:24 | 1.0985 | 1.0098 | 0.08873 | 1.1785e-05 | 0
[13 empty] | 8:24 | 1.0034 | 0.91146 | 0.91784 |  | 8:24 | 0 | 0.15298 | 1101.4846 | 8:24 | 1.0991 | 1.0103 | 0.08878 | 1.1792e-05 | 0
[13 empty] | 8:24 | 0.99062 | 0.91146 | 0.91784 |  | 8:24 | 0 | 0.15298 | 1101.4846 | 8:24 | 1.0997 | 1.0109 | 0.088828 | 1.1798e-05 | 0
[13 empty] | 8:24 | 0.97811 | 0.91146 | 0.91784 |  | 8:24 | 0 | 0.15298 | 1101.4846 | 8:24 | 1.1003 | 1.0114 | 0.088875 | 1.1805e-05 | 0
[13 empty] | 8:25 | 0.96585 | 0.91146 | 0.91784 |  | 8:25 | 0 | 0.15298 | 1101.4846 | 8:25 | 1.1009 | 1.012 | 0.088923 | 1.1811e-05 | 0
[13 empty] | 8:25 | 0.95385 | 0.91146 | 0.91784 |  | 8:25 | 0 | 0.15298 | 1101.4846 | 8:25 | 1.1015 | 1.0125 | 0.088969 | 1.1817e-05 | 0
[13 empty] | 8:25 | 0.94209 | 0.91146 | 0.91784 |  | 8:25 | 0 | 0.15298 | 1101.4846 | 8:25 | 1.1021 | 1.013 | 0.089015 | 1.1823e-05 | 0
[13 empty] | 8:26 | 0.93058 | 0.91146 | 0.91784 |  | 8:26 | 0 | 0.15298 | 1101.4846 | 8:26 | 1.1026 | 1.0135 | 0.089061 | 1.1829e-05 | 0
[13 empty] | 8:26 | 0.9193 | 0.91146 | 0.91784 |  | 8:26 | 0 | 0.15298 | 1101.4846 | 8:26 | 1.1032 | 1.0141 | 0.089106 | 1.1835e-05 | 0
[13 empty] | 8:26 | 0.90825 | 0.91146 | 0.91784 |  | 8:26 | 0 | 0.15298 | 1101.4846 | 8:26 | 1.1037 | 1.0146 | 0.08915 | 1.1841e-05 | 0
[13 empty] | 8:26 | 0.89743 | 0.91146 | 0.91784 |  | 8:26 | 0 | 0.15298 | 1101.4846 | 8:26 | 1.1043 | 1.0151 | 0.089194 | 1.1847e-05 | 0
[13 empty] | 8:26 | 0.88683 | 0.91146 | 0.91784 |  | 8:26 | 0 | 0.15298 | 1101.4846 | 8:26 | 1.1048 | 1.0155 | 0.089238 | 1.1853e-05 | 0
[13 empty] | 8:27 | 0.87645 | 0.91146 | 0.91784 |  | 8:27 | 0 | 0.15298 | 1101.4846 | 8:27 | 1.1053 | 1.016 | 0.08928 | 1.1858e-05 | 0
[13 empty] | 8:27 | 0.86628 | 0.91146 | 0.91784 |  | 8:27 | 0 | 0.15298 | 1101.4846 | 8:27 | 1.1059 | 1.0165 | 0.089322 | 1.1864e-05 | 0
[13 empty] | 8:27 | 0.85633 | 0.91146 | 0.91784 |  | 8:27 | 0 | 0.15298 | 1101.4846 | 8:27 | 1.1064 | 1.017 | 0.089364 | 1.187e-05 | 0
[13 empty] | 8:28 | 0.84657 | 0.91146 | 0.91784 |  | 8:28 | 0 | 0.15298 | 1101.4846 | 8:28 | 1.1069 | 1.0175 | 0.089406 | 1.1875e-05 | 0
[13 empty] | 8:28 | 0.83702 | 0.91146 | 0.91784 |  | 8:28 | 0 | 0.15298 | 1101.4846 | 8:28 | 1.1074 | 1.0179 | 0.089446 | 1.188e-05 | 0
[13 empty] | 8:28 | 0.82766 | 0.91146 | 0.91784 |  | 8:28 | 0 | 0.15298 | 1101.4846 | 8:28 | 1.1079 | 1.0184 | 0.089486 | 1.1886e-05 | 0
[13 empty] | 8:28 | 0.8185 | 0.91146 | 0.91784 |  | 8:28 | 0 | 0.15298 | 1101.4846 | 8:28 | 1.1084 | 1.0189 | 0.089527 | 1.1891e-05 | 0
[13 empty] | 8:28 | 0.80952 | 0.91146 | 0.91784 |  | 8:28 | 0 | 0.15298 | 1101.4846 | 8:28 | 1.1089 | 1.0193 | 0.089567 | 1.1897e-05 | 0
[13 empty] | 8:29 | 0.80073 | 0.91146 | 0.91784 |  | 8:29 | 0 | 0.15298 | 1101.4846 | 8:29 | 1.1094 | 1.0198 | 0.089607 | 1.1902e-05 | 0
[13 empty] | 8:29 | 0.79211 | 0.91146 | 0.91784 |  | 8:29 | 0 | 0.15298 | 1101.4846 | 8:29 | 1.1098 | 1.0202 | 0.089645 | 1.1907e-05 | 0
[13 empty] | 8:29 | 0.78368 | 0.91146 | 0.91784 |  | 8:29 | 0 | 0.15298 | 1101.4846 | 8:29 | 1.1103 | 1.0206 | 0.089683 | 1.1912e-05 | 0
[13 empty] | 8:30 | 0.77542 | 0.91146 | 0.91784 |  | 8:30 | 0 | 0.15298 | 1101.4846 | 8:30 | 1.1108 | 1.021 | 0.089721 | 1.1917e-05 | 0
[13 empty] | 8:30 | 0.76733 | 0.91146 | 0.91784 |  | 8:30 | 0 | 0.15298 | 1101.4846 | 8:30 | 1.1113 | 1.0215 | 0.089758 | 1.1922e-05 | 0
[13 empty] | 8:30 | 0.7594 | 0.91146 | 0.91784 |  | 8:30 | 0 | 0.15298 | 1101.4846 | 8:30 | 1.1117 | 1.0219 | 0.089796 | 1.1927e-05 | 0
[13 empty] | 8:30 | 0.75164 | 0.91146 | 0.91784 |  | 8:30 | 0 | 0.15298 | 1101.4846 | 8:30 | 1.1122 | 1.0223 | 0.089832 | 1.1932e-05 | 0
[13 empty] | 8:30 | 0.74403 | 0.91146 | 0.91784 |  | 8:30 | 0 | 0.15298 | 1101.4846 | 8:30 | 1.1126 | 1.0227 | 0.089868 | 1.1937e-05 | 0
[13 empty] | 8:31 | 0.73658 | 0.91146 | 0.91784 |  | 8:31 | 0 | 0.15298 | 1101.4846 | 8:31 | 1.1131 | 1.0231 | 0.089905 | 1.1941e-05 | 0
[13 empty] | 8:31 | 0.72929 | 0.91146 | 0.91784 |  | 8:31 | 0 | 0.15298 | 1101.4846 | 8:31 | 1.1135 | 1.0236 | 0.089941 | 1.1946e-05 | 0
[13 empty] | 8:31 | 1.1629 | 0.91146 | 0.91784 |  | 8:31 | 0 | 0.15298 | 1101.4846 | 8:31 | 1.1142 | 1.0242 | 0.089996 | 1.1954e-05 | 0
[13 empty] | 8:32 | 1.1468 | 0.91146 | 0.91784 |  | 8:32 | 0 | 0.15298 | 1101.4846 | 8:32 | 1.1149 | 1.0248 | 0.090054 | 1.1961e-05 | 0
[13 empty] | 8:32 | 1.1311 | 0.91146 | 0.91784 |  | 8:32 | 0 | 0.15298 | 1101.4846 | 8:32 | 1.1156 | 1.0255 | 0.090109 | 1.1968e-05 | 0
[13 empty] | 8:32 | 1.1157 | 0.91146 | 0.91784 |  | 8:32 | 0 | 0.15298 | 1101.4846 | 8:32 | 1.1163 | 1.0261 | 0.090163 | 1.1976e-05 | 0
[13 empty] | 8:32 | 1.1006 | 0.91146 | 0.91784 |  | 8:32 | 0 | 0.15298 | 1101.4846 | 8:32 | 1.1169 | 1.0267 | 0.090216 | 1.1983e-05 | 0
[13 empty] | 8:32 | 1.0859 | 0.91146 | 0.91784 |  | 8:32 | 0 | 0.15298 | 1101.4846 | 8:32 | 1.1176 | 1.0273 | 0.090269 | 1.199e-05 | 0
[13 empty] | 8:33 | 1.0714 | 0.91146 | 0.91784 |  | 8:33 | 0 | 0.15298 | 1101.4846 | 8:33 | 1.1182 | 1.0279 | 0.090323 | 1.1997e-05 | 0
[13 empty] | 8:33 | 1.0572 | 0.91146 | 0.91784 |  | 8:33 | 0 | 0.15298 | 1101.4846 | 8:33 | 1.1189 | 1.0285 | 0.090375 | 1.2004e-05 | 0
[13 empty] | 8:33 | 1.0434 | 0.91146 | 0.91784 |  | 8:33 | 0 | 0.15298 | 1101.4846 | 8:33 | 1.1195 | 1.0291 | 0.090426 | 1.2011e-05 | 0
[13 empty] | 8:34 | 1.0298 | 0.91146 | 0.91784 |  | 8:34 | 0 | 0.15298 | 1101.4846 | 8:34 | 1.1201 | 1.0296 | 0.090476 | 1.2017e-05 | 0
[13 empty] | 8:34 | 1.0164 | 0.91146 | 0.91784 |  | 8:34 | 0 | 0.15298 | 1101.4846 | 8:34 | 1.1208 | 1.0302 | 0.090525 | 1.2024e-05 | 0
[13 empty] | 8:34 | 1.0034 | 0.91146 | 0.91784 |  | 8:34 | 0 | 0.15298 | 1101.4846 | 8:34 | 1.1214 | 1.0308 | 0.090575 | 1.203e-05 | 0
[13 empty] | 8:34 | 0.99062 | 0.91146 | 0.91784 |  | 8:34 | 0 | 0.15298 | 1101.4846 | 8:34 | 1.122 | 1.0313 | 0.090623 | 1.2037e-05 | 0
[13 empty] | 8:34 | 0.97811 | 0.91146 | 0.91784 |  | 8:34 | 0 | 0.15298 | 1101.4846 | 8:34 | 1.1225 | 1.0319 | 0.090671 | 1.2043e-05 | 0
[13 empty] | 8:35 | 0.96585 | 0.91146 | 0.91784 |  | 8:35 | 0 | 0.15298 | 1101.4846 | 8:35 | 1.1231 | 1.0324 | 0.090718 | 1.2049e-05 | 0
[13 empty] | 8:35 | 0.95385 | 0.91146 | 0.91784 |  | 8:35 | 0 | 0.15298 | 1101.4846 | 8:35 | 1.1237 | 1.0329 | 0.090764 | 1.2056e-05 | 0
[13 empty] | 8:35 | 0.94209 | 0.91146 | 0.91784 |  | 8:35 | 0 | 0.15298 | 1101.4846 | 8:35 | 1.1243 | 1.0335 | 0.09081 | 1.2062e-05 | 0
[13 empty] | 8:36 | 0.93058 | 0.91146 | 0.91784 |  | 8:36 | 0 | 0.15298 | 1101.4846 | 8:36 | 1.1248 | 1.034 | 0.090856 | 1.2068e-05 | 0
[13 empty] | 8:36 | 0.9193 | 0.91146 | 0.91784 |  | 8:36 | 0 | 0.15298 | 1101.4846 | 8:36 | 1.1254 | 1.0345 | 0.090902 | 1.2074e-05 | 0
[13 empty] | 8:36 | 0.90825 | 0.91146 | 0.91784 |  | 8:36 | 0 | 0.15298 | 1101.4846 | 8:36 | 1.1259 | 1.035 | 0.090946 | 1.2079e-05 | 0
[13 empty] | 8:36 | 0.89743 | 0.91146 | 0.91784 |  | 8:36 | 0 | 0.15298 | 1101.4846 | 8:36 | 1.1265 | 1.0355 | 0.09099 | 1.2085e-05 | 0
[13 empty] | 8:36 | 0.88683 | 0.91146 | 0.91784 |  | 8:36 | 0 | 0.15298 | 1101.4846 | 8:36 | 1.127 | 1.036 | 0.091033 | 1.2091e-05 | 0
[13 empty] | 8:37 | 0.87645 | 0.91146 | 0.91784 |  | 8:37 | 0 | 0.15298 | 1101.4846 | 8:37 | 1.1276 | 1.0365 | 0.091075 | 1.2097e-05 | 0
[13 empty] | 8:37 | 0.86628 | 0.91146 | 0.91784 |  | 8:37 | 0 | 0.15298 | 1101.4846 | 8:37 | 1.1281 | 1.037 | 0.091117 | 1.2102e-05 | 0
[13 empty] | 8:37 | 0.85633 | 0.91146 | 0.91784 |  | 8:37 | 0 | 0.15298 | 1101.4846 | 8:37 | 1.1286 | 1.0374 | 0.091159 | 1.2108e-05 | 0
[13 empty] | 8:38 | 0.84657 | 0.91146 | 0.91784 |  | 8:38 | 0 | 0.15298 | 1101.4846 | 8:38 | 1.1291 | 1.0379 | 0.091202 | 1.2113e-05 | 0
[13 empty] | 8:38 | 0.83702 | 0.91146 | 0.91784 |  | 8:38 | 0 | 0.15298 | 1101.4846 | 8:38 | 1.1296 | 1.0384 | 0.091242 | 1.2119e-05 | 0
[13 empty] | 8:38 | 0.82766 | 0.91146 | 0.91784 |  | 8:38 | 0 | 0.15298 | 1101.4846 | 8:38 | 1.1301 | 1.0388 | 0.091282 | 1.2124e-05 | 0
[13 empty] | 8:38 | 0.8185 | 0.91146 | 0.91784 |  | 8:38 | 0 | 0.15298 | 1101.4846 | 8:38 | 1.1306 | 1.0393 | 0.091322 | 1.213e-05 | 0
[13 empty] | 8:39 | 0.80952 | 0.91146 | 0.91784 |  | 8:39 | 0 | 0.15298 | 1101.4846 | 8:39 | 1.1311 | 1.0397 | 0.091362 | 1.2135e-05 | 0
[13 empty] | 8:39 | 0.80073 | 0.91146 | 0.91784 |  | 8:39 | 0 | 0.15298 | 1101.4846 | 8:39 | 1.1316 | 1.0402 | 0.091402 | 1.214e-05 | 0
[13 empty] | 8:39 | 0.79211 | 0.91146 | 0.91784 |  | 8:39 | 0 | 0.15298 | 1101.4846 | 8:39 | 1.1321 | 1.0406 | 0.09144 | 1.2145e-05 | 0
[13 empty] | 8:39 | 0.78368 | 0.91146 | 0.91784 |  | 8:39 | 0 | 0.15298 | 1101.4846 | 8:39 | 1.1326 | 1.0411 | 0.091478 | 1.215e-05 | 0
[13 empty] | 8:40 | 0.77542 | 0.91146 | 0.91784 |  | 8:40 | 0 | 0.15298 | 1101.4846 | 8:40 | 1.133 | 1.0415 | 0.091517 | 1.2155e-05 | 0
[13 empty] | 8:40 | 0.76733 | 0.91146 | 0.91784 |  | 8:40 | 0 | 0.15298 | 1101.4846 | 8:40 | 1.1335 | 1.0419 | 0.091553 | 1.216e-05 | 0
[13 empty] | 8:40 | 0.7594 | 0.91146 | 0.91784 |  | 8:40 | 0 | 0.15298 | 1101.4846 | 8:40 | 1.1339 | 1.0423 | 0.091591 | 1.2165e-05 | 0
[13 empty] | 8:40 | 0.75164 | 0.91146 | 0.91784 |  | 8:40 | 0 | 0.15298 | 1101.4846 | 8:40 | 1.1344 | 1.0428 | 0.091627 | 1.217e-05 | 0
[13 empty] | 8:41 | 0.74403 | 0.91146 | 0.91784 |  | 8:41 | 0 | 0.15298 | 1101.4846 | 8:41 | 1.1348 | 1.0432 | 0.091664 | 1.2175e-05 | 0
[13 empty] | 8:41 | 0.73658 | 0.91146 | 0.91784 |  | 8:41 | 0 | 0.15298 | 1101.4846 | 8:41 | 1.1353 | 1.0436 | 0.0917 | 1.218e-05 | 0
[13 empty] | 8:41 | 0.72929 | 0.91146 | 0.91784 |  | 8:41 | 0 | 0.15298 | 1101.4846 | 8:41 | 1.1357 | 1.044 | 0.091736 | 1.2185e-05 | 0
[13 empty] | 8:41 | 1.1629 | 0.91146 | 0.91784 |  | 8:41 | 0 | 0.15298 | 1101.4846 | 8:41 | 1.1364 | 1.0446 | 0.091794 | 1.2192e-05 | 0
[13 empty] | 8:42 | 1.1468 | 0.91146 | 0.91784 |  | 8:42 | 0 | 0.15298 | 1101.4846 | 8:42 | 1.1371 | 1.0453 | 0.091849 | 1.22e-05 | 0
[13 empty] | 8:42 | 1.1311 | 0.91146 | 0.91784 |  | 8:42 | 0 | 0.15298 | 1101.4846 | 8:42 | 1.1378 | 1.0459 | 0.091904 | 1.2207e-05 | 0
[13 empty] | 8:42 | 1.1157 | 0.91146 | 0.91784 |  | 8:42 | 0 | 0.15298 | 1101.4846 | 8:42 | 1.1385 | 1.0465 | 0.091958 | 1.2214e-05 | 0
[13 empty] | 8:42 | 1.1006 | 0.91146 | 0.91784 |  | 8:42 | 0 | 0.15298 | 1101.4846 | 8:42 | 1.1392 | 1.0471 | 0.092013 | 1.2221e-05 | 0
[13 empty] | 8:43 | 1.0859 | 0.91146 | 0.91784 |  | 8:43 | 0 | 0.15298 | 1101.4846 | 8:43 | 1.1398 | 1.0477 | 0.092065 | 1.2228e-05 | 0
[13 empty] | 8:43 | 1.0714 | 0.91146 | 0.91784 |  | 8:43 | 0 | 0.15298 | 1101.4846 | 8:43 | 1.1405 | 1.0483 | 0.092118 | 1.2235e-05 | 0
[13 empty] | 8:43 | 1.0572 | 0.91146 | 0.91784 |  | 8:43 | 0 | 0.15298 | 1101.4846 | 8:43 | 1.1411 | 1.0489 | 0.09217 | 1.2242e-05 | 0
[13 empty] | 8:43 | 1.0434 | 0.91146 | 0.91784 |  | 8:43 | 0 | 0.15298 | 1101.4846 | 8:43 | 1.1417 | 1.0495 | 0.092221 | 1.2249e-05 | 0
[13 empty] | 8:44 | 1.0298 | 0.91146 | 0.91784 |  | 8:44 | 0 | 0.15298 | 1101.4846 | 8:44 | 1.1424 | 1.0501 | 0.092271 | 1.2256e-05 | 0
[13 empty] | 8:44 | 1.0164 | 0.91146 | 0.91784 |  | 8:44 | 0 | 0.15298 | 1101.4846 | 8:44 | 1.143 | 1.0507 | 0.092321 | 1.2262e-05 | 0
[13 empty] | 8:44 | 1.0034 | 0.91146 | 0.91784 |  | 8:44 | 0 | 0.15298 | 1101.4846 | 8:44 | 1.1436 | 1.0512 | 0.09237 | 1.2269e-05 | 0
[13 empty] | 8:44 | 0.99062 | 0.91146 | 0.91784 |  | 8:44 | 0 | 0.15298 | 1101.4846 | 8:44 | 1.1442 | 1.0518 | 0.092418 | 1.2275e-05 | 0
[13 empty] | 8:44 | 0.97811 | 0.91146 | 0.91784 |  | 8:44 | 0 | 0.15298 | 1101.4846 | 8:44 | 1.1448 | 1.0523 | 0.092466 | 1.2282e-05 | 0
[13 empty] | 8:45 | 0.96585 | 0.91146 | 0.91784 |  | 8:45 | 0 | 0.15298 | 1101.4846 | 8:45 | 1.1454 | 1.0528 | 0.092514 | 1.2288e-05 | 0
[13 empty] | 8:45 | 0.95385 | 0.91146 | 0.91784 |  | 8:45 | 0 | 0.15298 | 1101.4846 | 8:45 | 1.1459 | 1.0534 | 0.092559 | 1.2294e-05 | 0
[13 empty] | 8:45 | 0.94209 | 0.91146 | 0.91784 |  | 8:45 | 0 | 0.15298 | 1101.4846 | 8:45 | 1.1465 | 1.0539 | 0.092605 | 1.23e-05 | 0
[13 empty] | 8:46 | 0.93058 | 0.91146 | 0.91784 |  | 8:46 | 0 | 0.15298 | 1101.4846 | 8:46 | 1.1471 | 1.0544 | 0.092651 | 1.2306e-05 | 0
[13 empty] | 8:46 | 0.9193 | 0.91146 | 0.91784 |  | 8:46 | 0 | 0.15298 | 1101.4846 | 8:46 | 1.1476 | 1.0549 | 0.092697 | 1.2312e-05 | 0
[13 empty] | 8:46 | 0.90825 | 0.91146 | 0.91784 |  | 8:46 | 0 | 0.15298 | 1101.4846 | 8:46 | 1.1482 | 1.0554 | 0.092741 | 1.2318e-05 | 0
[13 empty] | 8:46 | 0.89743 | 0.91146 | 0.91784 |  | 8:46 | 0 | 0.15298 | 1101.4846 | 8:46 | 1.1487 | 1.0559 | 0.092785 | 1.2324e-05 | 0
[13 empty] | 8:46 | 0.88683 | 0.91146 | 0.91784 |  | 8:46 | 0 | 0.15298 | 1101.4846 | 8:46 | 1.1493 | 1.0564 | 0.092829 | 1.233e-05 | 0
[13 empty] | 8:47 | 0.87645 | 0.91146 | 0.91784 |  | 8:47 | 0 | 0.15298 | 1101.4846 | 8:47 | 1.1498 | 1.0569 | 0.092871 | 1.2335e-05 | 0
[13 empty] | 8:47 | 0.86628 | 0.91146 | 0.91784 |  | 8:47 | 0 | 0.15298 | 1101.4846 | 8:47 | 1.1503 | 1.0574 | 0.092913 | 1.2341e-05 | 0
[13 empty] | 8:47 | 0.85633 | 0.91146 | 0.91784 |  | 8:47 | 0 | 0.15298 | 1101.4846 | 8:47 | 1.1508 | 1.0579 | 0.092955 | 1.2346e-05 | 0
[13 empty] | 8:48 | 0.84657 | 0.91146 | 0.91784 |  | 8:48 | 0 | 0.15298 | 1101.4846 | 8:48 | 1.1513 | 1.0583 | 0.092997 | 1.2352e-05 | 0
[13 empty] | 8:48 | 0.83702 | 0.91146 | 0.91784 |  | 8:48 | 0 | 0.15298 | 1101.4846 | 8:48 | 1.1519 | 1.0588 | 0.093037 | 1.2357e-05 | 0
[13 empty] | 8:48 | 0.82766 | 0.91146 | 0.91784 |  | 8:48 | 0 | 0.15298 | 1101.4846 | 8:48 | 1.1524 | 1.0593 | 0.093079 | 1.2363e-05 | 0
[13 empty] | 8:48 | 0.8185 | 0.91146 | 0.91784 |  | 8:48 | 0 | 0.15298 | 1101.4846 | 8:48 | 1.1529 | 1.0597 | 0.093117 | 1.2368e-05 | 0
[13 empty] | 8:48 | 0.80952 | 0.91146 | 0.91784 |  | 8:48 | 0 | 0.15298 | 1101.4846 | 8:48 | 1.1533 | 1.0602 | 0.093157 | 1.2373e-05 | 0
[13 empty] | 8:49 | 0.80073 | 0.91146 | 0.91784 |  | 8:49 | 0 | 0.15298 | 1101.4846 | 8:49 | 1.1538 | 1.0606 | 0.093197 | 1.2379e-05 | 0
[13 empty] | 8:49 | 0.79211 | 0.91146 | 0.91784 |  | 8:49 | 0 | 0.15298 | 1101.4846 | 8:49 | 1.1543 | 1.0611 | 0.093236 | 1.2384e-05 | 0
[13 empty] | 8:49 | 0.78368 | 0.91146 | 0.91784 |  | 8:49 | 0 | 0.15298 | 1101.4846 | 8:49 | 1.1548 | 1.0615 | 0.093274 | 1.2389e-05 | 0
[13 empty] | 8:50 | 0.77542 | 0.91146 | 0.91784 |  | 8:50 | 0 | 0.15298 | 1101.4846 | 8:50 | 1.1552 | 1.0619 | 0.093312 | 1.2394e-05 | 0
[13 empty] | 8:50 | 0.76733 | 0.91146 | 0.91784 |  | 8:50 | 0 | 0.15298 | 1101.4846 | 8:50 | 1.1557 | 1.0623 | 0.09335 | 1.2399e-05 | 0
[13 empty] | 8:50 | 0.7594 | 0.91146 | 0.91784 |  | 8:50 | 0 | 0.15298 | 1101.4846 | 8:50 | 1.1562 | 1.0628 | 0.093386 | 1.2404e-05 | 0
[13 empty] | 8:50 | 0.75164 | 0.91146 | 0.91784 |  | 8:50 | 0 | 0.15298 | 1101.4846 | 8:50 | 1.1566 | 1.0632 | 0.093423 | 1.2409e-05 | 0
[13 empty] | 8:50 | 0.74403 | 0.91146 | 0.91784 |  | 8:50 | 0 | 0.15298 | 1101.4846 | 8:50 | 1.1571 | 1.0636 | 0.093459 | 1.2414e-05 | 0
[13 empty] | 8:51 | 0.73658 | 0.91146 | 0.91784 |  | 8:51 | 0 | 0.15298 | 1101.4846 | 8:51 | 1.1575 | 1.064 | 0.093495 | 1.2418e-05 | 0
[13 empty] | 8:51 | 0.72929 | 0.91146 | 0.91784 |  | 8:51 | 0 | 0.15298 | 1101.4846 | 8:51 | 1.158 | 1.0644 | 0.093532 | 1.2423e-05 | 0
[13 empty] | 8:51 | 1.1629 | 0.91146 | 0.91784 |  | 8:51 | 0 | 0.15298 | 1101.4846 | 8:51 | 1.1587 | 1.0651 | 0.093589 | 1.2431e-05 | 0
[13 empty] | 8:52 | 1.1468 | 0.91146 | 0.91784 |  | 8:52 | 0 | 0.15298 | 1101.4846 | 8:52 | 1.1594 | 1.0657 | 0.093644 | 1.2438e-05 | 0
[13 empty] | 8:52 | 1.1311 | 0.91146 | 0.91784 |  | 8:52 | 0 | 0.15298 | 1101.4846 | 8:52 | 1.16 | 1.0663 | 0.0937 | 1.2445e-05 | 0
[13 empty] | 8:52 | 1.1157 | 0.91146 | 0.91784 |  | 8:52 | 0 | 0.15298 | 1101.4846 | 8:52 | 1.1607 | 1.067 | 0.093753 | 1.2453e-05 | 0
[13 empty] | 8:52 | 1.1006 | 0.91146 | 0.91784 |  | 8:52 | 0 | 0.15298 | 1101.4846 | 8:52 | 1.1614 | 1.0676 | 0.093808 | 1.246e-05 | 0
[13 empty] | 8:52 | 1.0859 | 0.91146 | 0.91784 |  | 8:52 | 0 | 0.15298 | 1101.4846 | 8:52 | 1.162 | 1.0682 | 0.09386 | 1.2467e-05 | 0
[13 empty] | 8:53 | 1.0714 | 0.91146 | 0.91784 |  | 8:53 | 0 | 0.15298 | 1101.4846 | 8:53 | 1.1627 | 1.0688 | 0.093914 | 1.2474e-05 | 0
[13 empty] | 8:53 | 1.0572 | 0.91146 | 0.91784 |  | 8:53 | 0 | 0.15298 | 1101.4846 | 8:53 | 1.1633 | 1.0693 | 0.093965 | 1.2481e-05 | 0
[13 empty] | 8:53 | 1.0434 | 0.91146 | 0.91784 |  | 8:53 | 0 | 0.15298 | 1101.4846 | 8:53 | 1.164 | 1.0699 | 0.094017 | 1.2487e-05 | 0
[13 empty] | 8:54 | 1.0298 | 0.91146 | 0.91784 |  | 8:54 | 0 | 0.15298 | 1101.4846 | 8:54 | 1.1646 | 1.0705 | 0.094066 | 1.2494e-05 | 0
[13 empty] | 8:54 | 1.0164 | 0.91146 | 0.91784 |  | 8:54 | 0 | 0.15298 | 1101.4846 | 8:54 | 1.1652 | 1.0711 | 0.094116 | 1.2501e-05 | 0
[13 empty] | 8:54 | 1.0034 | 0.91146 | 0.91784 |  | 8:54 | 0 | 0.15298 | 1101.4846 | 8:54 | 1.1658 | 1.0716 | 0.094166 | 1.2507e-05 | 0
[13 empty] | 8:54 | 0.99062 | 0.91146 | 0.91784 |  | 8:54 | 0 | 0.15298 | 1101.4846 | 8:54 | 1.1664 | 1.0722 | 0.094213 | 1.2514e-05 | 0
[13 empty] | 8:54 | 0.97811 | 0.91146 | 0.91784 |  | 8:54 | 0 | 0.15298 | 1101.4846 | 8:54 | 1.167 | 1.0727 | 0.094261 | 1.252e-05 | 0
[13 empty] | 8:55 | 0.96585 | 0.91146 | 0.91784 |  | 8:55 | 0 | 0.15298 | 1101.4846 | 8:55 | 1.1676 | 1.0733 | 0.094309 | 1.2526e-05 | 0
[13 empty] | 8:55 | 0.95385 | 0.91146 | 0.91784 |  | 8:55 | 0 | 0.15298 | 1101.4846 | 8:55 | 1.1682 | 1.0738 | 0.094355 | 1.2532e-05 | 0
[13 empty] | 8:55 | 0.94209 | 0.91146 | 0.91784 |  | 8:55 | 0 | 0.15298 | 1101.4846 | 8:55 | 1.1687 | 1.0743 | 0.094401 | 1.2539e-05 | 0
[13 empty] | 8:56 | 0.93058 | 0.91146 | 0.91784 |  | 8:56 | 0 | 0.15298 | 1101.4846 | 8:56 | 1.1693 | 1.0748 | 0.094446 | 1.2545e-05 | 0
[13 empty] | 8:56 | 0.9193 | 0.91146 | 0.91784 |  | 8:56 | 0 | 0.15298 | 1101.4846 | 8:56 | 1.1699 | 1.0753 | 0.094492 | 1.2551e-05 | 0
[13 empty] | 8:56 | 0.90825 | 0.91146 | 0.91784 |  | 8:56 | 0 | 0.15298 | 1101.4846 | 8:56 | 1.1704 | 1.0759 | 0.094536 | 1.2557e-05 | 0
[13 empty] | 8:56 | 0.89743 | 0.91146 | 0.91784 |  | 8:56 | 0 | 0.15298 | 1101.4846 | 8:56 | 1.171 | 1.0764 | 0.09458 | 1.2562e-05 | 0
[13 empty] | 8:56 | 0.88683 | 0.91146 | 0.91784 |  | 8:56 | 0 | 0.15298 | 1101.4846 | 8:56 | 1.1715 | 1.0769 | 0.094624 | 1.2568e-05 | 0
[13 empty] | 8:57 | 0.87645 | 0.91146 | 0.91784 |  | 8:57 | 0 | 0.15298 | 1101.4846 | 8:57 | 1.172 | 1.0773 | 0.094666 | 1.2574e-05 | 0
[13 empty] | 8:57 | 0.86628 | 0.91146 | 0.91784 |  | 8:57 | 0 | 0.15298 | 1101.4846 | 8:57 | 1.1725 | 1.0778 | 0.094708 | 1.2579e-05 | 0
[13 empty] | 8:57 | 0.85633 | 0.91146 | 0.91784 |  | 8:57 | 0 | 0.15298 | 1101.4846 | 8:57 | 1.1731 | 1.0783 | 0.09475 | 1.2585e-05 | 0
[13 empty] | 8:58 | 0.84657 | 0.91146 | 0.91784 |  | 8:58 | 0 | 0.15298 | 1101.4846 | 8:58 | 1.1736 | 1.0788 | 0.094792 | 1.2591e-05 | 0
[13 empty] | 8:58 | 0.83702 | 0.91146 | 0.91784 |  | 8:58 | 0 | 0.15298 | 1101.4846 | 8:58 | 1.1741 | 1.0792 | 0.094832 | 1.2596e-05 | 0
[13 empty] | 8:58 | 0.82766 | 0.91146 | 0.91784 |  | 8:58 | 0 | 0.15298 | 1101.4846 | 8:58 | 1.1746 | 1.0797 | 0.094874 | 1.2601e-05 | 0
[13 empty] | 8:58 | 0.8185 | 0.91146 | 0.91784 |  | 8:58 | 0 | 0.15298 | 1101.4846 | 8:58 | 1.1751 | 1.0801 | 0.094914 | 1.2607e-05 | 0
[13 empty] | 8:58 | 0.80952 | 0.91146 | 0.91784 |  | 8:58 | 0 | 0.15298 | 1101.4846 | 8:58 | 1.1756 | 1.0806 | 0.094952 | 1.2612e-05 | 0
[13 empty] | 8:59 | 0.80073 | 0.91146 | 0.91784 |  | 8:59 | 0 | 0.15298 | 1101.4846 | 8:59 | 1.176 | 1.081 | 0.094993 | 1.2617e-05 | 0
[13 empty] | 8:59 | 0.79211 | 0.91146 | 0.91784 |  | 8:59 | 0 | 0.15298 | 1101.4846 | 8:59 | 1.1765 | 1.0815 | 0.095031 | 1.2622e-05 | 0
[13 empty] | 8:59 | 0.78368 | 0.91146 | 0.91784 |  | 8:59 | 0 | 0.15298 | 1101.4846 | 8:59 | 1.177 | 1.0819 | 0.095069 | 1.2627e-05 | 0
[13 empty] | 9:00 | 0.77542 | 0.91146 | 0.91784 |  | 9:00 | 0 | 0.15298 | 1101.4846 | 9:00 | 1.1775 | 1.0824 | 0.095107 | 1.2632e-05 | 0
[13 empty] | 9:00 | 0.76733 | 0.91146 | 0.91784 |  | 9:00 | 0 | 0.15298 | 1101.4846 | 9:00 | 1.1779 | 1.0828 | 0.095145 | 1.2637e-05 | 0
[13 empty] | 9:00 | 0.7594 | 0.91146 | 0.91784 |  | 9:00 | 0 | 0.15298 | 1101.4846 | 9:00 | 1.1784 | 1.0832 | 0.095182 | 1.2642e-05 | 0
[13 empty] | 9:00 | 0.75164 | 0.91146 | 0.91784 |  | 9:00 | 0.75552 | 0.15298 | 1107.1512 | 9:00 | 1.1788 | 1.0836 | 0.095218 | 1.2647e-05 | 0
[13 empty] | 9:00 | 0.74403 | 0.91146 | 0.91784 |  | 9:00 | 0.74784 | 0.15298 | 1118.427 | 9:00 | 1.1793 | 1.084 | 0.095254 | 1.2652e-05 | 0
[13 empty] | 9:01 | 0.73658 | 0.91146 | 0.91784 |  | 9:01 | 0.74031 | 0.15298 | 1129.5882 | 9:01 | 1.1797 | 1.0844 | 0.095291 | 1.2657e-05 | 0
[13 empty] | 9:01 | 0.72929 | 0.91146 | 0.91784 |  | 9:01 | 0.73294 | 0.15298 | 1140.6367 | 9:01 | 1.1802 | 1.0849 | 0.095327 | 1.2661e-05 | 0
[13 empty] | 9:01 | 1.1629 | 0.91146 | 0.91784 |  | 9:01 | 0.94609 | 0.15298 | 1153.2303 | 9:01 | 1.1809 | 1.0855 | 0.095384 | 1.2669e-05 | 0
[13 empty] | 9:02 | 1.1468 | 0.91146 | 0.91784 |  | 9:02 | 1.1549 | 0.15298 | 1168.9867 | 9:02 | 1.1816 | 1.0861 | 0.095439 | 1.2676e-05 | 0
[13 empty] | 9:02 | 1.1311 | 0.91146 | 0.91784 |  | 9:02 | 1.139 | 0.15298 | 1186.1907 | 9:02 | 1.1823 | 1.0868 | 0.095495 | 1.2684e-05 | 0
[13 empty] | 9:02 | 1.1157 | 0.91146 | 0.91784 |  | 9:02 | 1.1234 | 0.15298 | 1203.1598 | 9:02 | 1.1829 | 1.0874 | 0.09555 | 1.2691e-05 | 0
[13 empty] | 9:02 | 1.1006 | 0.91146 | 0.91784 |  | 9:02 | 1.1082 | 0.15298 | 1219.8959 | 9:02 | 1.1836 | 1.088 | 0.095604 | 1.2698e-05 | 0
[13 empty] | 9:02 | 1.0859 | 0.91146 | 0.91784 |  | 9:02 | 1.0933 | 0.15298 | 1236.4066 | 9:02 | 1.1843 | 1.0886 | 0.095657 | 1.2705e-05 | 0
[13 empty] | 9:03 | 1.0714 | 0.91146 | 0.91784 |  | 9:03 | 1.0786 | 0.15298 | 1252.6958 | 9:03 | 1.1849 | 1.0892 | 0.095709 | 1.2712e-05 | 0
[13 empty] | 9:03 | 1.0572 | 0.91146 | 0.91784 |  | 9:03 | 1.0643 | 0.15298 | 1268.7692 | 9:03 | 1.1856 | 1.0898 | 0.09576 | 1.2719e-05 | 0
[13 empty] | 9:03 | 1.0434 | 0.91146 | 0.91784 |  | 9:03 | 1.0503 | 0.15298 | 1284.6286 | 9:03 | 1.1862 | 1.0904 | 0.095812 | 1.2726e-05 | 0
[13 empty] | 9:04 | 1.0298 | 0.91146 | 0.91784 |  | 9:04 | 1.0366 | 0.15298 | 1300.2799 | 9:04 | 1.1868 | 1.0909 | 0.095862 | 1.2733e-05 | 0
[13 empty] | 9:04 | 1.0164 | 0.91146 | 0.91784 |  | 9:04 | 1.0231 | 0.15298 | 1315.7269 | 9:04 | 1.1874 | 1.0915 | 0.095911 | 1.2739e-05 | 0
[13 empty] | 9:04 | 1.0034 | 0.91146 | 0.91784 |  | 9:04 | 1.0099 | 0.15298 | 1330.9752 | 9:04 | 1.188 | 1.0921 | 0.095961 | 1.2746e-05 | 0
[13 empty] | 9:04 | 0.99062 | 0.91146 | 0.91784 |  | 9:04 | 0.99701 | 0.15298 | 1346.0268 | 9:04 | 1.1886 | 1.0926 | 0.096009 | 1.2752e-05 | 0
[13 empty] | 9:04 | 0.97811 | 0.91146 | 0.91784 |  | 9:04 | 0.98437 | 0.15298 | 1360.8874 | 9:04 | 1.1892 | 1.0932 | 0.096056 | 1.2758e-05 | 0
[13 empty] | 9:05 | 0.96585 | 0.91146 | 0.91784 |  | 9:05 | 0.97198 | 0.15298 | 1375.559 | 9:05 | 1.1898 | 1.0937 | 0.096104 | 1.2765e-05 | 0
[13 empty] | 9:05 | 0.95385 | 0.91146 | 0.91784 |  | 9:05 | 0.95985 | 0.15298 | 1390.0471 | 9:05 | 1.1904 | 1.0942 | 0.09615 | 1.2771e-05 | 0
[13 empty] | 9:05 | 0.94209 | 0.91146 | 0.91784 |  | 9:05 | 0.94797 | 0.15298 | 1404.3558 | 9:05 | 1.191 | 1.0948 | 0.096198 | 1.2777e-05 | 0
[13 empty] | 9:06 | 0.93058 | 0.91146 | 0.91784 |  | 9:06 | 0.93634 | 0.15298 | 1418.4888 | 9:06 | 1.1915 | 1.0953 | 0.096242 | 1.2783e-05 | 0
[13 empty] | 9:06 | 0.9193 | 0.91146 | 0.91784 |  | 9:06 | 0.92494 | 0.15298 | 1432.4479 | 9:06 | 1.1921 | 1.0958 | 0.096287 | 1.2789e-05 | 0
[13 empty] | 9:06 | 0.90825 | 0.91146 | 0.91784 |  | 9:06 | 0.91377 | 0.15298 | 1446.239 | 9:06 | 1.1926 | 1.0963 | 0.096331 | 1.2795e-05 | 0
[13 empty] | 9:06 | 0.89743 | 0.91146 | 0.91784 |  | 9:06 | 0.90284 | 0.15298 | 1459.864 | 9:06 | 1.1932 | 1.0968 | 0.096375 | 1.2801e-05 | 0
[13 empty] | 9:06 | 0.88683 | 0.91146 | 0.91784 |  | 9:06 | 0.89213 | 0.15298 | 1473.3266 | 9:06 | 1.1937 | 1.0973 | 0.096419 | 1.2807e-05 | 0
[13 empty] | 9:07 | 0.87645 | 0.91146 | 0.91784 |  | 9:07 | 0.88164 | 0.15298 | 1486.6287 | 9:07 | 1.1942 | 1.0978 | 0.096461 | 1.2812e-05 | 0
[13 empty] | 9:07 | 0.86628 | 0.91146 | 0.91784 |  | 9:07 | 0.87137 | 0.15298 | 1499.7762 | 9:07 | 1.1948 | 1.0982 | 0.096503 | 1.2818e-05 | 0
[13 empty] | 9:07 | 0.85633 | 0.91146 | 0.91784 |  | 9:07 | 0.8613 | 0.15298 | 1512.7709 | 9:07 | 1.1953 | 1.0987 | 0.096545 | 1.2823e-05 | 0
[13 empty] | 9:08 | 0.84657 | 0.91146 | 0.91784 |  | 9:08 | 0.85145 | 0.15298 | 1525.6166 | 9:08 | 1.1958 | 1.0992 | 0.096587 | 1.2829e-05 | 0
[13 empty] | 9:08 | 0.83702 | 0.91146 | 0.91784 |  | 9:08 | 0.8418 | 0.15298 | 1538.3172 | 9:08 | 1.1963 | 1.0997 | 0.096627 | 1.2834e-05 | 0
[13 empty] | 9:08 | 0.82766 | 0.91146 | 0.91784 |  | 9:08 | 0.83234 | 0.15298 | 1550.8726 | 9:08 | 1.1968 | 1.1001 | 0.096669 | 1.284e-05 | 0
[13 empty] | 9:08 | 0.8185 | 0.91146 | 0.91784 |  | 9:08 | 0.82308 | 0.15298 | 1563.2886 | 9:08 | 1.1973 | 1.1006 | 0.09671 | 1.2845e-05 | 0
[13 empty] | 9:08 | 0.80952 | 0.91146 | 0.91784 |  | 9:08 | 0.81401 | 0.15298 | 1575.5671 | 9:08 | 1.1978 | 1.101 | 0.096748 | 1.285e-05 | 0
[13 empty] | 9:09 | 0.80073 | 0.91146 | 0.91784 |  | 9:09 | 0.80512 | 0.15298 | 1587.7099 | 9:09 | 1.1983 | 1.1015 | 0.096788 | 1.2855e-05 | 0
[13 empty] | 9:09 | 0.79211 | 0.91146 | 0.91784 |  | 9:09 | 0.79642 | 0.15298 | 1599.7211 | 9:09 | 1.1988 | 1.1019 | 0.096826 | 1.2861e-05 | 0
[13 empty] | 9:09 | 0.78368 | 0.91146 | 0.91784 |  | 9:09 | 0.7879 | 0.15298 | 1611.6042 | 9:09 | 1.1992 | 1.1024 | 0.096864 | 1.2866e-05 | 0
[13 empty] | 9:10 | 0.77542 | 0.91146 | 0.91784 |  | 9:10 | 0.77955 | 0.15298 | 1623.3594 | 9:10 | 1.1997 | 1.1028 | 0.096902 | 1.2871e-05 | 0
[13 empty] | 9:10 | 0.76733 | 0.91146 | 0.91784 |  | 9:10 | 0.77137 | 0.15298 | 1634.9923 | 9:10 | 1.2002 | 1.1032 | 0.096941 | 1.2876e-05 | 0
[13 empty] | 9:10 | 0.7594 | 0.91146 | 0.91784 |  | 9:10 | 0.76336 | 0.15298 | 1646.5031 | 9:10 | 1.2006 | 1.1036 | 0.096977 | 1.2881e-05 | 0
[13 empty] | 9:10 | 0.75164 | 0.91146 | 0.91784 |  | 9:10 | 0 | 0.15298 | 1652.2269 | 9:10 | 1.2011 | 1.1041 | 0.097013 | 1.2886e-05 | 0
[13 empty] | 9:10 | 0.74403 | 0.91146 | 0.91784 |  | 9:10 | 0 | 0.15298 | 1652.2269 | 9:10 | 1.2015 | 1.1045 | 0.097049 | 1.289e-05 | 0
[13 empty] | 9:11 | 0.73658 | 0.91146 | 0.91784 |  | 9:11 | 0 | 0.15298 | 1652.2269 | 9:11 | 1.202 | 1.1049 | 0.097086 | 1.2895e-05 | 0
[13 empty] | 9:11 | 0.72929 | 0.91146 | 0.91784 |  | 9:11 | 0 | 0.15298 | 1652.2269 | 9:11 | 1.2024 | 1.1053 | 0.097122 | 1.29e-05 | 0
[13 empty] | 9:11 | 1.1629 | 0.91146 | 0.91784 |  | 9:11 | 0 | 0.15298 | 1652.2269 | 9:11 | 1.2031 | 1.1059 | 0.097179 | 1.2908e-05 | 0
[13 empty] | 9:12 | 1.1468 | 0.91146 | 0.91784 |  | 9:12 | 0 | 0.15298 | 1652.2269 | 9:12 | 1.2038 | 1.1066 | 0.097235 | 1.2915e-05 | 0
[13 empty] | 9:12 | 1.1311 | 0.91146 | 0.91784 |  | 9:12 | 0 | 0.15298 | 1652.2269 | 9:12 | 1.2045 | 1.1072 | 0.09729 | 1.2922e-05 | 0
[13 empty] | 9:12 | 1.1157 | 0.91146 | 0.91784 |  | 9:12 | 0 | 0.15298 | 1652.2269 | 9:12 | 1.2052 | 1.1078 | 0.097346 | 1.293e-05 | 0
[13 empty] | 9:12 | 1.1006 | 0.91146 | 0.91784 |  | 9:12 | 0 | 0.15298 | 1652.2269 | 9:12 | 1.2058 | 1.1084 | 0.097399 | 1.2937e-05 | 0
[13 empty] | 9:12 | 1.0859 | 0.91146 | 0.91784 |  | 9:12 | 0 | 0.15298 | 1652.2269 | 9:12 | 1.2065 | 1.109 | 0.097452 | 1.2944e-05 | 0
[13 empty] | 9:13 | 1.0714 | 0.91146 | 0.91784 |  | 9:13 | 0 | 0.15298 | 1652.2269 | 9:13 | 1.2071 | 1.1096 | 0.097504 | 1.2951e-05 | 0
[13 empty] | 9:13 | 1.0572 | 0.91146 | 0.91784 |  | 9:13 | 0 | 0.15298 | 1652.2269 | 9:13 | 1.2078 | 1.1102 | 0.097556 | 1.2958e-05 | 0
[13 empty] | 9:13 | 1.0434 | 0.91146 | 0.91784 |  | 9:13 | 0 | 0.15298 | 1652.2269 | 9:13 | 1.2084 | 1.1108 | 0.097607 | 1.2964e-05 | 0
[13 empty] | 9:14 | 1.0298 | 0.91146 | 0.91784 |  | 9:14 | 0 | 0.15298 | 1652.2269 | 9:14 | 1.209 | 1.1114 | 0.097657 | 1.2971e-05 | 0
[13 empty] | 9:14 | 1.0164 | 0.91146 | 0.91784 |  | 9:14 | 0 | 0.15298 | 1652.2269 | 9:14 | 1.2097 | 1.1119 | 0.097706 | 1.2978e-05 | 0
[13 empty] | 9:14 | 1.0034 | 0.91146 | 0.91784 |  | 9:14 | 0 | 0.15298 | 1652.2269 | 9:14 | 1.2103 | 1.1125 | 0.097756 | 1.2984e-05 | 0
[13 empty] | 9:14 | 0.99062 | 0.91146 | 0.91784 |  | 9:14 | 0 | 0.15298 | 1652.2269 | 9:14 | 1.2109 | 1.113 | 0.097804 | 1.2991e-05 | 0
[13 empty] | 9:14 | 0.97811 | 0.91146 | 0.91784 |  | 9:14 | 0 | 0.15298 | 1652.2269 | 9:14 | 1.2115 | 1.1136 | 0.097852 | 1.2997e-05 | 0
[13 empty] | 9:15 | 0.96585 | 0.91146 | 0.91784 |  | 9:15 | 0 | 0.15298 | 1652.2269 | 9:15 | 1.212 | 1.1141 | 0.097899 | 1.3003e-05 | 0
[13 empty] | 9:15 | 0.95385 | 0.91146 | 0.91784 |  | 9:15 | 0 | 0.15298 | 1652.2269 | 9:15 | 1.2126 | 1.1147 | 0.097945 | 1.3009e-05 | 0
[13 empty] | 9:15 | 0.94209 | 0.91146 | 0.91784 |  | 9:15 | 0 | 0.15298 | 1652.2269 | 9:15 | 1.2132 | 1.1152 | 0.097993 | 1.3015e-05 | 0
[13 empty] | 9:16 | 0.93058 | 0.91146 | 0.91784 |  | 9:16 | 0 | 0.15298 | 1652.2269 | 9:16 | 1.2138 | 1.1157 | 0.098037 | 1.3022e-05 | 0
[13 empty] | 9:16 | 0.9193 | 0.91146 | 0.91784 |  | 9:16 | 0 | 0.15298 | 1652.2269 | 9:16 | 1.2143 | 1.1162 | 0.098083 | 1.3028e-05 | 0
[13 empty] | 9:16 | 0.90825 | 0.91146 | 0.91784 |  | 9:16 | 0 | 0.15298 | 1652.2269 | 9:16 | 1.2149 | 1.1167 | 0.098127 | 1.3033e-05 | 0
[13 empty] | 9:16 | 0.89743 | 0.91146 | 0.91784 |  | 9:16 | 0 | 0.15298 | 1652.2269 | 9:16 | 1.2154 | 1.1172 | 0.098171 | 1.3039e-05 | 0
[13 empty] | 9:16 | 0.88683 | 0.91146 | 0.91784 |  | 9:16 | 0 | 0.15298 | 1652.2269 | 9:16 | 1.2159 | 1.1177 | 0.098215 | 1.3045e-05 | 0
[13 empty] | 9:17 | 0.87645 | 0.91146 | 0.91784 |  | 9:17 | 0 | 0.15298 | 1652.2269 | 9:17 | 1.2165 | 1.1182 | 0.098257 | 1.3051e-05 | 0
[13 empty] | 9:17 | 0.86628 | 0.91146 | 0.91784 |  | 9:17 | 0 | 0.15298 | 1652.2269 | 9:17 | 1.217 | 1.1187 | 0.0983 | 1.3056e-05 | 0
[13 empty] | 9:17 | 0.85633 | 0.91146 | 0.91784 |  | 9:17 | 0 | 0.15298 | 1652.2269 | 9:17 | 1.2175 | 1.1192 | 0.098341 | 1.3062e-05 | 0
[13 empty] | 9:17 | 0.84657 | 0.91146 | 0.91784 |  | 9:17 | 0 | 0.15298 | 1652.2269 | 9:17 | 1.218 | 1.1196 | 0.098383 | 1.3067e-05 | 0
[13 empty] | 9:18 | 0.83702 | 0.91146 | 0.91784 |  | 9:18 | 0 | 0.15298 | 1652.2269 | 9:18 | 1.2185 | 1.1201 | 0.098425 | 1.3073e-05 | 0
[13 empty] | 9:18 | 0.82766 | 0.91146 | 0.91784 |  | 9:18 | 0 | 0.15298 | 1652.2269 | 9:18 | 1.219 | 1.1206 | 0.098465 | 1.3078e-05 | 0
[13 empty] | 9:18 | 0.8185 | 0.91146 | 0.91784 |  | 9:18 | 0 | 0.15298 | 1652.2269 | 9:18 | 1.2195 | 1.121 | 0.098505 | 1.3083e-05 | 0
[13 empty] | 9:18 | 0.80952 | 0.91146 | 0.91784 |  | 9:18 | 0 | 0.15298 | 1652.2269 | 9:18 | 1.22 | 1.1215 | 0.098543 | 1.3089e-05 | 0
[13 empty] | 9:19 | 0.80073 | 0.91146 | 0.91784 |  | 9:19 | 0 | 0.15298 | 1652.2269 | 9:19 | 1.2205 | 1.1219 | 0.098583 | 1.3094e-05 | 0
[13 empty] | 9:19 | 0.79211 | 0.91146 | 0.91784 |  | 9:19 | 0 | 0.15298 | 1652.2269 | 9:19 | 1.221 | 1.1223 | 0.098621 | 1.3099e-05 | 0
[13 empty] | 9:19 | 0.78368 | 0.91146 | 0.91784 |  | 9:19 | 0 | 0.15298 | 1652.2269 | 9:19 | 1.2215 | 1.1228 | 0.09866 | 1.3104e-05 | 0
[13 empty] | 9:19 | 0.77542 | 0.91146 | 0.91784 |  | 9:19 | 0 | 0.15298 | 1652.2269 | 9:19 | 1.2219 | 1.1232 | 0.098698 | 1.3109e-05 | 0
[13 empty] | 9:20 | 0.76733 | 0.91146 | 0.91784 |  | 9:20 | 0 | 0.15298 | 1652.2269 | 9:20 | 1.2224 | 1.1236 | 0.098736 | 1.3114e-05 | 0
[13 empty] | 9:20 | 0.7594 | 0.91146 | 0.91784 |  | 9:20 | 0 | 0.15298 | 1652.2269 | 9:20 | 1.2229 | 1.1241 | 0.098772 | 1.3119e-05 | 0
[13 empty] | 9:20 | 0.75164 | 0.91146 | 0.91784 |  | 9:20 | 0 | 0.15298 | 1652.2269 | 9:20 | 1.2233 | 1.1245 | 0.098808 | 1.3124e-05 | 0
[13 empty] | 9:20 | 0.74403 | 0.91146 | 0.91784 |  | 9:20 | 0 | 0.15298 | 1652.2269 | 9:20 | 1.2238 | 1.1249 | 0.098847 | 1.3129e-05 | 0
[13 empty] | 9:21 | 0.73658 | 0.91146 | 0.91784 |  | 9:21 | 0 | 0.15298 | 1652.2269 | 9:21 | 1.2242 | 1.1253 | 0.098881 | 1.3134e-05 | 0
[13 empty] | 9:21 | 0.72929 | 0.91146 | 0.91784 |  | 9:21 | 0 | 0.15298 | 1652.2269 | 9:21 | 1.2246 | 1.1257 | 0.098917 | 1.3138e-05 | 0
[13 empty] | 9:21 | 1.1629 | 0.91146 | 0.91784 |  | 9:21 | 0 | 0.15298 | 1652.2269 | 9:21 | 1.2253 | 1.1264 | 0.098975 | 1.3146e-05 | 0
[13 empty] | 9:21 | 1.1468 | 0.91146 | 0.91784 |  | 9:21 | 0 | 0.15298 | 1652.2269 | 9:21 | 1.2261 | 1.127 | 0.09903 | 1.3153e-05 | 0
[13 empty] | 9:22 | 1.1311 | 0.91146 | 0.91784 |  | 9:22 | 0 | 0.15298 | 1652.2269 | 9:22 | 1.2267 | 1.1276 | 0.099085 | 1.3161e-05 | 0
[13 empty] | 9:22 | 1.1157 | 0.91146 | 0.91784 |  | 9:22 | 0 | 0.15298 | 1652.2269 | 9:22 | 1.2274 | 1.1282 | 0.099141 | 1.3168e-05 | 0
[13 empty] | 9:22 | 1.1006 | 0.91146 | 0.91784 |  | 9:22 | 0 | 0.15298 | 1652.2269 | 9:22 | 1.2281 | 1.1289 | 0.099194 | 1.3175e-05 | 0
[13 empty] | 9:22 | 1.0859 | 0.91146 | 0.91784 |  | 9:22 | 0 | 0.15298 | 1652.2269 | 9:22 | 1.2287 | 1.1295 | 0.099248 | 1.3182e-05 | 0
[13 empty] | 9:23 | 1.0714 | 0.91146 | 0.91784 |  | 9:23 | 0 | 0.15298 | 1652.2269 | 9:23 | 1.2294 | 1.1301 | 0.099299 | 1.3189e-05 | 0
[13 empty] | 9:23 | 1.0572 | 0.91146 | 0.91784 |  | 9:23 | 0 | 0.15298 | 1652.2269 | 9:23 | 1.23 | 1.1307 | 0.099351 | 1.3196e-05 | 0
[13 empty] | 9:23 | 1.0434 | 0.91146 | 0.91784 |  | 9:23 | 0 | 0.15298 | 1652.2269 | 9:23 | 1.2306 | 1.1312 | 0.099402 | 1.3203e-05 | 0
[13 empty] | 9:24 | 1.0298 | 0.91146 | 0.91784 |  | 9:24 | 0 | 0.15298 | 1652.2269 | 9:24 | 1.2313 | 1.1318 | 0.099452 | 1.321e-05 | 0
[13 empty] | 9:24 | 1.0164 | 0.91146 | 0.91784 |  | 9:24 | 0 | 0.15298 | 1652.2269 | 9:24 | 1.2319 | 1.1324 | 0.099502 | 1.3216e-05 | 0
[13 empty] | 9:24 | 1.0034 | 0.91146 | 0.91784 |  | 9:24 | 0 | 0.15298 | 1652.2269 | 9:24 | 1.2325 | 1.1329 | 0.099551 | 1.3223e-05 | 0
[13 empty] | 9:24 | 0.99062 | 0.91146 | 0.91784 |  | 9:24 | 0 | 0.15298 | 1652.2269 | 9:24 | 1.2331 | 1.1335 | 0.099599 | 1.3229e-05 | 0
[13 empty] | 9:24 | 0.97811 | 0.91146 | 0.91784 |  | 9:24 | 0 | 0.15298 | 1652.2269 | 9:24 | 1.2337 | 1.134 | 0.099647 | 1.3235e-05 | 0
[13 empty] | 9:25 | 0.96585 | 0.91146 | 0.91784 |  | 9:25 | 0 | 0.15298 | 1652.2269 | 9:25 | 1.2343 | 1.1346 | 0.099695 | 1.3242e-05 | 0
[13 empty] | 9:25 | 0.95385 | 0.91146 | 0.91784 |  | 9:25 | 0 | 0.15298 | 1652.2269 | 9:25 | 1.2348 | 1.1351 | 0.099742 | 1.3248e-05 | 0
[13 empty] | 9:25 | 0.94209 | 0.91146 | 0.91784 |  | 9:25 | 0 | 0.15298 | 1652.2269 | 9:25 | 1.2354 | 1.1356 | 0.099788 | 1.3254e-05 | 0
[13 empty] | 9:26 | 0.93058 | 0.91146 | 0.91784 |  | 9:26 | 0 | 0.15298 | 1652.2269 | 9:26 | 1.236 | 1.1361 | 0.099832 | 1.326e-05 | 0
[13 empty] | 9:26 | 0.9193 | 0.91146 | 0.91784 |  | 9:26 | 0 | 0.15298 | 1652.2269 | 9:26 | 1.2365 | 1.1367 | 0.099878 | 1.3266e-05 | 0
[13 empty] | 9:26 | 0.90825 | 0.91146 | 0.91784 |  | 9:26 | 0 | 0.15298 | 1652.2269 | 9:26 | 1.2371 | 1.1371 | 0.099922 | 1.3272e-05 | 0
[13 empty] | 9:26 | 0.89743 | 0.91146 | 0.91784 |  | 9:26 | 0 | 0.15298 | 1652.2269 | 9:26 | 1.2376 | 1.1376 | 0.099966 | 1.3278e-05 | 0
[13 empty] | 9:26 | 0.88683 | 0.91146 | 0.91784 |  | 9:26 | 0 | 0.15298 | 1652.2269 | 9:26 | 1.2382 | 1.1381 | 0.10001 | 1.3283e-05 | 0
[13 empty] | 9:27 | 0.87645 | 0.91146 | 0.91784 |  | 9:27 | 0 | 0.15298 | 1652.2269 | 9:27 | 1.2387 | 1.1386 | 0.10005 | 1.3289e-05 | 0
[13 empty] | 9:27 | 0.86628 | 0.91146 | 0.91784 |  | 9:27 | 0 | 0.15298 | 1652.2269 | 9:27 | 1.2392 | 1.1391 | 0.1001 | 1.3295e-05 | 0
[13 empty] | 9:27 | 0.85633 | 0.91146 | 0.91784 |  | 9:27 | 0 | 0.15298 | 1652.2269 | 9:27 | 1.2397 | 1.1396 | 0.10014 | 1.33e-05 | 0
[13 empty] | 9:28 | 0.84657 | 0.91146 | 0.91784 |  | 9:28 | 0 | 0.15298 | 1652.2269 | 9:28 | 1.2403 | 1.1401 | 0.10018 | 1.3306e-05 | 0
[13 empty] | 9:28 | 0.83702 | 0.91146 | 0.91784 |  | 9:28 | 0 | 0.15298 | 1652.2269 | 9:28 | 1.2408 | 1.1405 | 0.10022 | 1.3311e-05 | 0
[13 empty] | 9:28 | 0.82766 | 0.91146 | 0.91784 |  | 9:28 | 0 | 0.15298 | 1652.2269 | 9:28 | 1.2413 | 1.141 | 0.10026 | 1.3317e-05 | 0
[13 empty] | 9:28 | 0.8185 | 0.91146 | 0.91784 |  | 9:28 | 0 | 0.15298 | 1652.2269 | 9:28 | 1.2418 | 1.1414 | 0.1003 | 1.3322e-05 | 0
[13 empty] | 9:28 | 0.80952 | 0.91146 | 0.91784 |  | 9:28 | 0 | 0.15298 | 1652.2269 | 9:28 | 1.2423 | 1.1419 | 0.10034 | 1.3327e-05 | 0
[13 empty] | 9:29 | 0.80073 | 0.91146 | 0.91784 |  | 9:29 | 0 | 0.15298 | 1652.2269 | 9:29 | 1.2427 | 1.1423 | 0.10038 | 1.3333e-05 | 0
[13 empty] | 9:29 | 0.79211 | 0.91146 | 0.91784 |  | 9:29 | 0 | 0.15298 | 1652.2269 | 9:29 | 1.2432 | 1.1428 | 0.10042 | 1.3338e-05 | 0
[13 empty] | 9:29 | 0.78368 | 0.91146 | 0.91784 |  | 9:29 | 0 | 0.15298 | 1652.2269 | 9:29 | 1.2437 | 1.1432 | 0.10045 | 1.3343e-05 | 0
[13 empty] | 9:30 | 0.77542 | 0.91146 | 0.91784 |  | 9:30 | 0 | 0.15298 | 1652.2269 | 9:30 | 1.2441 | 1.1436 | 0.10049 | 1.3348e-05 | 0
[13 empty] | 9:30 | 0.76733 | 0.91146 | 0.91784 |  | 9:30 | 0 | 0.15298 | 1652.2269 | 9:30 | 1.2446 | 1.1441 | 0.10053 | 1.3353e-05 | 0
[13 empty] | 9:30 | 0.7594 | 0.91146 | 0.91784 |  | 9:30 | 0 | 0.15298 | 1652.2269 | 9:30 | 1.2451 | 1.1445 | 0.10057 | 1.3358e-05 | 0
[13 empty] | 9:30 | 0.75164 | 0.91146 | 0.91784 |  | 9:30 | 0 | 0.15298 | 1652.2269 | 9:30 | 1.2455 | 1.1449 | 0.10061 | 1.3363e-05 | 0
[13 empty] | 9:30 | 0.74403 | 0.91146 | 0.91784 |  | 9:30 | 0 | 0.15298 | 1652.2269 | 9:30 | 1.246 | 1.1453 | 0.10064 | 1.3367e-05 | 0
[13 empty] | 9:31 | 0.73658 | 0.91146 | 0.91784 |  | 9:31 | 0 | 0.15298 | 1652.2269 | 9:31 | 1.2464 | 1.1457 | 0.10068 | 1.3372e-05 | 0
[13 empty] | 9:31 | 0.72929 | 0.91146 | 0.91784 |  | 9:31 | 0 | 0.15298 | 1652.2269 | 9:31 | 1.2469 | 1.1461 | 0.10071 | 1.3377e-05 | 0
[13 empty] | 9:31 | 1.1629 | 0.91146 | 0.91784 |  | 9:31 | 0 | 0.15298 | 1652.2269 | 9:31 | 1.2476 | 1.1468 | 0.10077 | 1.3384e-05 | 0
[13 empty] | 9:32 | 1.1468 | 0.91146 | 0.91784 |  | 9:32 | 0 | 0.15298 | 1652.2269 | 9:32 | 1.2483 | 1.1474 | 0.10083 | 1.3392e-05 | 0
[13 empty] | 9:32 | 1.1311 | 0.91146 | 0.91784 |  | 9:32 | 0 | 0.15298 | 1652.2269 | 9:32 | 1.2489 | 1.1481 | 0.10088 | 1.3399e-05 | 0
[13 empty] | 9:32 | 1.1157 | 0.91146 | 0.91784 |  | 9:32 | 0 | 0.15298 | 1652.2269 | 9:32 | 1.2496 | 1.1487 | 0.10094 | 1.3406e-05 | 0
[13 empty] | 9:32 | 1.1006 | 0.91146 | 0.91784 |  | 9:32 | 0 | 0.15298 | 1652.2269 | 9:32 | 1.2503 | 1.1493 | 0.10099 | 1.3414e-05 | 0
[13 empty] | 9:32 | 1.0859 | 0.91146 | 0.91784 |  | 9:32 | 0 | 0.15298 | 1652.2269 | 9:32 | 1.251 | 1.1499 | 0.10104 | 1.3421e-05 | 0
[13 empty] | 9:33 | 1.0714 | 0.91146 | 0.91784 |  | 9:33 | 0 | 0.15298 | 1652.2269 | 9:33 | 1.2516 | 1.1505 | 0.10109 | 1.3428e-05 | 0
[13 empty] | 9:33 | 1.0572 | 0.91146 | 0.91784 |  | 9:33 | 0 | 0.15298 | 1652.2269 | 9:33 | 1.2523 | 1.1511 | 0.10115 | 1.3435e-05 | 0
[13 empty] | 9:33 | 1.0434 | 0.91146 | 0.91784 |  | 9:33 | 0 | 0.15298 | 1652.2269 | 9:33 | 1.2529 | 1.1517 | 0.1012 | 1.3441e-05 | 0
[13 empty] | 9:34 | 1.0298 | 0.91146 | 0.91784 |  | 9:34 | 0 | 0.15298 | 1652.2269 | 9:34 | 1.2535 | 1.1522 | 0.10125 | 1.3448e-05 | 0
[13 empty] | 9:34 | 1.0164 | 0.91146 | 0.91784 |  | 9:34 | 0 | 0.15298 | 1652.2269 | 9:34 | 1.2541 | 1.1528 | 0.1013 | 1.3455e-05 | 0
[13 empty] | 9:34 | 1.0034 | 0.91146 | 0.91784 |  | 9:34 | 0 | 0.15298 | 1652.2269 | 9:34 | 1.2547 | 1.1534 | 0.10135 | 1.3461e-05 | 0
[13 empty] | 9:34 | 0.99062 | 0.91146 | 0.91784 |  | 9:34 | 0 | 0.15298 | 1652.2269 | 9:34 | 1.2553 | 1.1539 | 0.10139 | 1.3468e-05 | 0
[13 empty] | 9:34 | 0.97811 | 0.91146 | 0.91784 |  | 9:34 | 0 | 0.15298 | 1652.2269 | 9:34 | 1.2559 | 1.1545 | 0.10144 | 1.3474e-05 | 0
[13 empty] | 9:35 | 0.96585 | 0.91146 | 0.91784 |  | 9:35 | 0 | 0.15298 | 1652.2269 | 9:35 | 1.2565 | 1.155 | 0.10149 | 1.348e-05 | 0
[13 empty] | 9:35 | 0.95385 | 0.91146 | 0.91784 |  | 9:35 | 0 | 0.15298 | 1652.2269 | 9:35 | 1.2571 | 1.1555 | 0.10154 | 1.3486e-05 | 0
[13 empty] | 9:35 | 0.94209 | 0.91146 | 0.91784 |  | 9:35 | 0 | 0.15298 | 1652.2269 | 9:35 | 1.2577 | 1.1561 | 0.10158 | 1.3492e-05 | 0
[13 empty] | 9:36 | 0.93058 | 0.91146 | 0.91784 |  | 9:36 | 0 | 0.15298 | 1652.2269 | 9:36 | 1.2582 | 1.1566 | 0.10163 | 1.3499e-05 | 0
[13 empty] | 9:36 | 0.9193 | 0.91146 | 0.91784 |  | 9:36 | 0 | 0.15298 | 1652.2269 | 9:36 | 1.2588 | 1.1571 | 0.10167 | 1.3504e-05 | 0
[13 empty] | 9:36 | 0.90825 | 0.91146 | 0.91784 |  | 9:36 | 0 | 0.15298 | 1652.2269 | 9:36 | 1.2593 | 1.1576 | 0.10172 | 1.351e-05 | 0
[13 empty] | 9:36 | 0.89743 | 0.91146 | 0.91784 |  | 9:36 | 0 | 0.15298 | 1652.2269 | 9:36 | 1.2599 | 1.1581 | 0.10176 | 1.3516e-05 | 0
[13 empty] | 9:36 | 0.88683 | 0.91146 | 0.91784 |  | 9:36 | 0 | 0.15298 | 1652.2269 | 9:36 | 1.2604 | 1.1586 | 0.10181 | 1.3522e-05 | 0
[13 empty] | 9:37 | 0.87645 | 0.91146 | 0.91784 |  | 9:37 | 0 | 0.15298 | 1652.2269 | 9:37 | 1.2609 | 1.1591 | 0.10185 | 1.3528e-05 | 0
[13 empty] | 9:37 | 0.86628 | 0.91146 | 0.91784 |  | 9:37 | 0 | 0.15298 | 1652.2269 | 9:37 | 1.2615 | 1.1596 | 0.10189 | 1.3533e-05 | 0
[13 empty] | 9:37 | 0.85633 | 0.91146 | 0.91784 |  | 9:37 | 0 | 0.15298 | 1652.2269 | 9:37 | 1.262 | 1.16 | 0.10193 | 1.3539e-05 | 0
[13 empty] | 9:38 | 0.84657 | 0.91146 | 0.91784 |  | 9:38 | 0 | 0.15298 | 1652.2269 | 9:38 | 1.2625 | 1.1605 | 0.10197 | 1.3544e-05 | 0
[13 empty] | 9:38 | 0.83702 | 0.91146 | 0.91784 |  | 9:38 | 0 | 0.15298 | 1652.2269 | 9:38 | 1.263 | 1.161 | 0.10202 | 1.355e-05 | 0
[13 empty] | 9:38 | 0.82766 | 0.91146 | 0.91784 |  | 9:38 | 0 | 0.15298 | 1652.2269 | 9:38 | 1.2635 | 1.1614 | 0.10206 | 1.3555e-05 | 0
[13 empty] | 9:38 | 0.8185 | 0.91146 | 0.91784 |  | 9:38 | 0 | 0.15298 | 1652.2269 | 9:38 | 1.264 | 1.1619 | 0.1021 | 1.356e-05 | 0
[13 empty] | 9:38 | 0.80952 | 0.91146 | 0.91784 |  | 9:38 | 0 | 0.15298 | 1652.2269 | 9:38 | 1.2645 | 1.1623 | 0.10214 | 1.3566e-05 | 0
[13 empty] | 9:39 | 0.80073 | 0.91146 | 0.91784 |  | 9:39 | 0 | 0.15298 | 1652.2269 | 9:39 | 1.265 | 1.1628 | 0.10217 | 1.3571e-05 | 0
[13 empty] | 9:39 | 0.79211 | 0.91146 | 0.91784 |  | 9:39 | 0 | 0.15298 | 1652.2269 | 9:39 | 1.2654 | 1.1632 | 0.10221 | 1.3576e-05 | 0
[13 empty] | 9:39 | 0.78368 | 0.91146 | 0.91784 |  | 9:39 | 0 | 0.15298 | 1652.2269 | 9:39 | 1.2659 | 1.1637 | 0.10225 | 1.3581e-05 | 0
[13 empty] | 9:40 | 0.77542 | 0.91146 | 0.91784 |  | 9:40 | 0 | 0.15298 | 1652.2269 | 9:40 | 1.2664 | 1.1641 | 0.10229 | 1.3586e-05 | 0
[13 empty] | 9:40 | 0.76733 | 0.91146 | 0.91784 |  | 9:40 | 0 | 0.15298 | 1652.2269 | 9:40 | 1.2669 | 1.1645 | 0.10233 | 1.3591e-05 | 0
[13 empty] | 9:40 | 0.7594 | 0.91146 | 0.91784 |  | 9:40 | 0 | 0.15298 | 1652.2269 | 9:40 | 1.2673 | 1.1649 | 0.10236 | 1.3596e-05 | 0
[13 empty] | 9:40 | 0.75164 | 0.91146 | 0.91784 |  | 9:40 | 0 | 0.15298 | 1652.2269 | 9:40 | 1.2678 | 1.1654 | 0.1024 | 1.3601e-05 | 0
[13 empty] | 9:40 | 0.74403 | 0.91146 | 0.91784 |  | 9:40 | 0 | 0.15298 | 1652.2269 | 9:40 | 1.2682 | 1.1658 | 0.10244 | 1.3606e-05 | 0
[13 empty] | 9:41 | 0.73658 | 0.91146 | 0.91784 |  | 9:41 | 0 | 0.15298 | 1652.2269 | 9:41 | 1.2687 | 1.1662 | 0.10247 | 1.3611e-05 | 0
[13 empty] | 9:41 | 0.72929 | 0.91146 | 0.91784 |  | 9:41 | 0 | 0.15298 | 1652.2269 | 9:41 | 1.2691 | 1.1666 | 0.10251 | 1.3615e-05 | 0
[13 empty] | 9:41 | 1.1629 | 0.91146 | 0.91784 |  | 9:41 | 0 | 0.15298 | 1652.2269 | 9:41 | 1.2698 | 1.1672 | 0.10257 | 1.3623e-05 | 0
[13 empty] | 9:42 | 1.1468 | 0.91146 | 0.91784 |  | 9:42 | 0 | 0.15298 | 1652.2269 | 9:42 | 1.2705 | 1.1679 | 0.10262 | 1.363e-05 | 0
[13 empty] | 9:42 | 1.1311 | 0.91146 | 0.91784 |  | 9:42 | 0 | 0.15298 | 1652.2269 | 9:42 | 1.2712 | 1.1685 | 0.10268 | 1.3638e-05 | 0
[13 empty] | 9:42 | 1.1157 | 0.91146 | 0.91784 |  | 9:42 | 0 | 0.15298 | 1652.2269 | 9:42 | 1.2719 | 1.1691 | 0.10273 | 1.3645e-05 | 0
[13 empty] | 9:42 | 1.1006 | 0.91146 | 0.91784 |  | 9:42 | 0 | 0.15298 | 1652.2269 | 9:42 | 1.2725 | 1.1697 | 0.10278 | 1.3652e-05 | 0
[13 empty] | 9:42 | 1.0859 | 0.91146 | 0.91784 |  | 9:42 | 0 | 0.15298 | 1652.2269 | 9:42 | 1.2732 | 1.1703 | 0.10284 | 1.3659e-05 | 0
[13 empty] | 9:43 | 1.0714 | 0.91146 | 0.91784 |  | 9:43 | 0 | 0.15298 | 1652.2269 | 9:43 | 1.2738 | 1.1709 | 0.10289 | 1.3666e-05 | 0
[13 empty] | 9:43 | 1.0572 | 0.91146 | 0.91784 |  | 9:43 | 0 | 0.15298 | 1652.2269 | 9:43 | 1.2745 | 1.1715 | 0.10294 | 1.3673e-05 | 0
[13 empty] | 9:43 | 1.0434 | 0.91146 | 0.91784 |  | 9:43 | 0 | 0.15298 | 1652.2269 | 9:43 | 1.2751 | 1.1721 | 0.10299 | 1.368e-05 | 0
[13 empty] | 9:44 | 1.0298 | 0.91146 | 0.91784 |  | 9:44 | 0 | 0.15298 | 1652.2269 | 9:44 | 1.2757 | 1.1727 | 0.10304 | 1.3686e-05 | 0
[13 empty] | 9:44 | 1.0164 | 0.91146 | 0.91784 |  | 9:44 | 0 | 0.15298 | 1652.2269 | 9:44 | 1.2764 | 1.1732 | 0.10309 | 1.3693e-05 | 0
[13 empty] | 9:44 | 1.0034 | 0.91146 | 0.91784 |  | 9:44 | 0 | 0.15298 | 1652.2269 | 9:44 | 1.277 | 1.1738 | 0.10314 | 1.37e-05 | 0
[13 empty] | 9:44 | 0.99062 | 0.91146 | 0.91784 |  | 9:44 | 0 | 0.15298 | 1652.2269 | 9:44 | 1.2776 | 1.1744 | 0.10319 | 1.3706e-05 | 0
[13 empty] | 9:44 | 0.97811 | 0.91146 | 0.91784 |  | 9:44 | 0 | 0.15298 | 1652.2269 | 9:44 | 1.2781 | 1.1749 | 0.10324 | 1.3712e-05 | 0
[13 empty] | 9:45 | 0.96585 | 0.91146 | 0.91784 |  | 9:45 | 0 | 0.15298 | 1652.2269 | 9:45 | 1.2787 | 1.1754 | 0.10329 | 1.3719e-05 | 0
[13 empty] | 9:45 | 0.95385 | 0.91146 | 0.91784 |  | 9:45 | 0 | 0.15298 | 1652.2269 | 9:45 | 1.2793 | 1.176 | 0.10333 | 1.3725e-05 | 0
[13 empty] | 9:45 | 0.94209 | 0.91146 | 0.91784 |  | 9:45 | 0 | 0.15298 | 1652.2269 | 9:45 | 1.2799 | 1.1765 | 0.10338 | 1.3731e-05 | 0
[13 empty] | 9:46 | 0.93058 | 0.91146 | 0.91784 |  | 9:46 | 0 | 0.15298 | 1652.2269 | 9:46 | 1.2804 | 1.177 | 0.10342 | 1.3737e-05 | 0
[13 empty] | 9:46 | 0.9193 | 0.91146 | 0.91784 |  | 9:46 | 0 | 0.15298 | 1652.2269 | 9:46 | 1.281 | 1.1775 | 0.10347 | 1.3743e-05 | 0
[13 empty] | 9:46 | 0.90825 | 0.91146 | 0.91784 |  | 9:46 | 0 | 0.15298 | 1652.2269 | 9:46 | 1.2815 | 1.178 | 0.10351 | 1.3749e-05 | 0
[13 empty] | 9:46 | 0.89743 | 0.91146 | 0.91784 |  | 9:46 | 0 | 0.15298 | 1652.2269 | 9:46 | 1.2821 | 1.1785 | 0.10356 | 1.3755e-05 | 0
[13 empty] | 9:46 | 0.88683 | 0.91146 | 0.91784 |  | 9:46 | 0 | 0.15298 | 1652.2269 | 9:46 | 1.2826 | 1.179 | 0.1036 | 1.3761e-05 | 0
[13 empty] | 9:47 | 0.87645 | 0.91146 | 0.91784 |  | 9:47 | 0 | 0.15298 | 1652.2269 | 9:47 | 1.2831 | 1.1795 | 0.10364 | 1.3766e-05 | 0
[13 empty] | 9:47 | 0.86628 | 0.91146 | 0.91784 |  | 9:47 | 0 | 0.15298 | 1652.2269 | 9:47 | 1.2837 | 1.18 | 0.10369 | 1.3772e-05 | 0
[13 empty] | 9:47 | 0.85633 | 0.91146 | 0.91784 |  | 9:47 | 0 | 0.15298 | 1652.2269 | 9:47 | 1.2842 | 1.1805 | 0.10373 | 1.3777e-05 | 0
[13 empty] | 9:48 | 0.84657 | 0.91146 | 0.91784 |  | 9:48 | 0 | 0.15298 | 1652.2269 | 9:48 | 1.2847 | 1.1809 | 0.10377 | 1.3783e-05 | 0
[13 empty] | 9:48 | 0.83702 | 0.91146 | 0.91784 |  | 9:48 | 0 | 0.15298 | 1652.2269 | 9:48 | 1.2852 | 1.1814 | 0.10381 | 1.3788e-05 | 0
[13 empty] | 9:48 | 0.82766 | 0.91146 | 0.91784 |  | 9:48 | 0 | 0.15298 | 1652.2269 | 9:48 | 1.2857 | 1.1819 | 0.10385 | 1.3794e-05 | 0
[13 empty] | 9:48 | 0.8185 | 0.91146 | 0.91784 |  | 9:48 | 0 | 0.15298 | 1652.2269 | 9:48 | 1.2862 | 1.1823 | 0.10389 | 1.3799e-05 | 0
[13 empty] | 9:48 | 0.80952 | 0.91146 | 0.91784 |  | 9:48 | 0 | 0.15298 | 1652.2269 | 9:48 | 1.2867 | 1.1828 | 0.10393 | 1.3804e-05 | 0
[13 empty] | 9:49 | 0.80073 | 0.91146 | 0.91784 |  | 9:49 | 0 | 0.15298 | 1652.2269 | 9:49 | 1.2872 | 1.1832 | 0.10397 | 1.3809e-05 | 0
[13 empty] | 9:49 | 0.79211 | 0.91146 | 0.91784 |  | 9:49 | 0 | 0.15298 | 1652.2269 | 9:49 | 1.2877 | 1.1837 | 0.10401 | 1.3815e-05 | 0
[13 empty] | 9:49 | 0.78368 | 0.91146 | 0.91784 |  | 9:49 | 0 | 0.15298 | 1652.2269 | 9:49 | 1.2882 | 1.1841 | 0.10405 | 1.382e-05 | 0
[13 empty] | 9:50 | 0.77542 | 0.91146 | 0.91784 |  | 9:50 | 0 | 0.15298 | 1652.2269 | 9:50 | 1.2886 | 1.1845 | 0.10408 | 1.3825e-05 | 0
[13 empty] | 9:50 | 0.76733 | 0.91146 | 0.91784 |  | 9:50 | 0 | 0.15298 | 1652.2269 | 9:50 | 1.2891 | 1.1849 | 0.10412 | 1.383e-05 | 0
[13 empty] | 9:50 | 0.7594 | 0.91146 | 0.91784 |  | 9:50 | 0 | 0.15298 | 1652.2269 | 9:50 | 1.2895 | 1.1854 | 0.10416 | 1.3835e-05 | 0
[13 empty] | 9:50 | 0.75164 | 0.91146 | 0.91784 |  | 9:50 | 0 | 0.15298 | 1652.2269 | 9:50 | 1.29 | 1.1858 | 0.1042 | 1.3839e-05 | 0
[13 empty] | 9:50 | 0.74403 | 0.91146 | 0.91784 |  | 9:50 | 0 | 0.15298 | 1652.2269 | 9:50 | 1.2904 | 1.1862 | 0.10423 | 1.3844e-05 | 0
[13 empty] | 9:51 | 0.73658 | 0.91146 | 0.91784 |  | 9:51 | 0 | 0.15298 | 1652.2269 | 9:51 | 1.2909 | 1.1866 | 0.10427 | 1.3849e-05 | 0
[13 empty] | 9:51 | 0.72929 | 0.91146 | 0.91784 |  | 9:51 | 0 | 0.15298 | 1652.2269 | 9:51 | 1.2913 | 1.187 | 0.1043 | 1.3854e-05 | 0
[13 empty] | 9:51 | 1.1629 | 0.91146 | 0.91784 |  | 9:51 | 0 | 0.15298 | 1652.2269 | 9:51 | 1.292 | 1.1877 | 0.10436 | 1.3861e-05 | 0
[13 empty] | 9:52 | 1.1468 | 0.91146 | 0.91784 |  | 9:52 | 0 | 0.15298 | 1652.2269 | 9:52 | 1.2927 | 1.1883 | 0.10442 | 1.3869e-05 | 0
[13 empty] | 9:52 | 1.1311 | 0.91146 | 0.91784 |  | 9:52 | 0 | 0.15298 | 1652.2269 | 9:52 | 1.2934 | 1.1889 | 0.10447 | 1.3876e-05 | 0
[13 empty] | 9:52 | 1.1157 | 0.91146 | 0.91784 |  | 9:52 | 0 | 0.15298 | 1652.2269 | 9:52 | 1.2941 | 1.1896 | 0.10453 | 1.3883e-05 | 0
[13 empty] | 9:52 | 1.1006 | 0.91146 | 0.91784 |  | 9:52 | 0 | 0.15298 | 1652.2269 | 9:52 | 1.2948 | 1.1902 | 0.10458 | 1.3891e-05 | 0
[13 empty] | 9:52 | 1.0859 | 0.91146 | 0.91784 |  | 9:52 | 0 | 0.15298 | 1652.2269 | 9:52 | 1.2954 | 1.1908 | 0.10463 | 1.3898e-05 | 0
[13 empty] | 9:53 | 1.0714 | 0.91146 | 0.91784 |  | 9:53 | 0 | 0.15298 | 1652.2269 | 9:53 | 1.2961 | 1.1914 | 0.10469 | 1.3905e-05 | 0
[13 empty] | 9:53 | 1.0572 | 0.91146 | 0.91784 |  | 9:53 | 0 | 0.15298 | 1652.2269 | 9:53 | 1.2967 | 1.1919 | 0.10474 | 1.3911e-05 | 0
[13 empty] | 9:53 | 1.0434 | 0.91146 | 0.91784 |  | 9:53 | 0 | 0.15298 | 1652.2269 | 9:53 | 1.2973 | 1.1925 | 0.10479 | 1.3918e-05 | 0
[13 empty] | 9:54 | 1.0298 | 0.91146 | 0.91784 |  | 9:54 | 0 | 0.15298 | 1652.2269 | 9:54 | 1.298 | 1.1931 | 0.10484 | 1.3925e-05 | 0
[13 empty] | 9:54 | 1.0164 | 0.91146 | 0.91784 |  | 9:54 | 0 | 0.15298 | 1652.2269 | 9:54 | 1.2986 | 1.1937 | 0.10489 | 1.3931e-05 | 0
[13 empty] | 9:54 | 1.0034 | 0.91146 | 0.91784 |  | 9:54 | 0 | 0.15298 | 1652.2269 | 9:54 | 1.2992 | 1.1942 | 0.10494 | 1.3938e-05 | 0
[13 empty] | 9:54 | 0.99062 | 0.91146 | 0.91784 |  | 9:54 | 0 | 0.15298 | 1652.2269 | 9:54 | 1.2998 | 1.1948 | 0.10499 | 1.3944e-05 | 0
[13 empty] | 9:54 | 0.97811 | 0.91146 | 0.91784 |  | 9:54 | 0 | 0.15298 | 1652.2269 | 9:54 | 1.3004 | 1.1953 | 0.10503 | 1.3951e-05 | 0
[13 empty] | 9:55 | 0.96585 | 0.91146 | 0.91784 |  | 9:55 | 0 | 0.15298 | 1652.2269 | 9:55 | 1.301 | 1.1959 | 0.10508 | 1.3957e-05 | 0
[13 empty] | 9:55 | 0.95385 | 0.91146 | 0.91784 |  | 9:55 | 0 | 0.15298 | 1652.2269 | 9:55 | 1.3015 | 1.1964 | 0.10513 | 1.3963e-05 | 0
[13 empty] | 9:55 | 0.94209 | 0.91146 | 0.91784 |  | 9:55 | 0 | 0.15298 | 1652.2269 | 9:55 | 1.3021 | 1.1969 | 0.10517 | 1.3969e-05 | 0
[13 empty] | 9:56 | 0.93058 | 0.91146 | 0.91784 |  | 9:56 | 0 | 0.15298 | 1652.2269 | 9:56 | 1.3027 | 1.1974 | 0.10522 | 1.3975e-05 | 0
[13 empty] | 9:56 | 0.9193 | 0.91146 | 0.91784 |  | 9:56 | 0 | 0.15298 | 1652.2269 | 9:56 | 1.3032 | 1.1979 | 0.10526 | 1.3982e-05 | 0
[13 empty] | 9:56 | 0.90825 | 0.91146 | 0.91784 |  | 9:56 | 0 | 0.15298 | 1652.2269 | 9:56 | 1.3038 | 1.1985 | 0.10531 | 1.3987e-05 | 0
[13 empty] | 9:56 | 0.89743 | 0.91146 | 0.91784 |  | 9:56 | 0 | 0.15298 | 1652.2269 | 9:56 | 1.3043 | 1.199 | 0.10535 | 1.3993e-05 | 0
[13 empty] | 9:56 | 0.88683 | 0.91146 | 0.91784 |  | 9:56 | 0 | 0.15298 | 1652.2269 | 9:56 | 1.3049 | 1.1994 | 0.1054 | 1.3999e-05 | 0
[13 empty] | 9:57 | 0.87645 | 0.91146 | 0.91784 |  | 9:57 | 0 | 0.15298 | 1652.2269 | 9:57 | 1.3054 | 1.1999 | 0.10544 | 1.4005e-05 | 0
[13 empty] | 9:57 | 0.86628 | 0.91146 | 0.91784 |  | 9:57 | 0 | 0.15298 | 1652.2269 | 9:57 | 1.3059 | 1.2004 | 0.10548 | 1.401e-05 | 0
[13 empty] | 9:57 | 0.85633 | 0.91146 | 0.91784 |  | 9:57 | 0 | 0.15298 | 1652.2269 | 9:57 | 1.3064 | 1.2009 | 0.10552 | 1.4016e-05 | 0
[13 empty] | 9:58 | 0.84657 | 0.91146 | 0.91784 |  | 9:58 | 0 | 0.15298 | 1652.2269 | 9:58 | 1.3069 | 1.2014 | 0.10556 | 1.4021e-05 | 0
[13 empty] | 9:58 | 0.83702 | 0.91146 | 0.91784 |  | 9:58 | 0 | 0.15298 | 1652.2269 | 9:58 | 1.3075 | 1.2018 | 0.10561 | 1.4027e-05 | 0
[13 empty] | 9:58 | 0.82766 | 0.91146 | 0.91784 |  | 9:58 | 0 | 0.15298 | 1652.2269 | 9:58 | 1.308 | 1.2023 | 0.10565 | 1.4032e-05 | 0
[13 empty] | 9:58 | 0.8185 | 0.91146 | 0.91784 |  | 9:58 | 0 | 0.15298 | 1652.2269 | 9:58 | 1.3085 | 1.2028 | 0.10569 | 1.4037e-05 | 0
[13 empty] | 9:58 | 0.80952 | 0.91146 | 0.91784 |  | 9:58 | 0 | 0.15298 | 1652.2269 | 9:58 | 1.3089 | 1.2032 | 0.10573 | 1.4043e-05 | 0
[13 empty] | 9:59 | 0.80073 | 0.91146 | 0.91784 |  | 9:59 | 0 | 0.15298 | 1652.2269 | 9:59 | 1.3094 | 1.2036 | 0.10576 | 1.4048e-05 | 0
[13 empty] | 9:59 | 0.79211 | 0.91146 | 0.91784 |  | 9:59 | 0 | 0.15298 | 1652.2269 | 9:59 | 1.3099 | 1.2041 | 0.1058 | 1.4053e-05 | 0
[13 empty] | 9:59 | 0.78368 | 0.91146 | 0.91784 |  | 9:59 | 0 | 0.15298 | 1652.2269 | 9:59 | 1.3104 | 1.2045 | 0.10584 | 1.4058e-05 | 0
[13 empty] | 10:00 | 0.77542 | 0.91146 | 0.91784 |  | 10:00 | 0 | 0.15298 | 1652.2269 | 10:00 | 1.3108 | 1.2049 | 0.10588 | 1.4063e-05 | 0
[13 empty] | 10:00 | 0.76733 | 0.91146 | 0.91784 |  | 10:00 | 0 | 0.15298 | 1652.2269 | 10:00 | 1.3113 | 1.2054 | 0.10592 | 1.4068e-05 | 0
[13 empty] | 10:00 | 0.7594 | 0.91146 | 0.91784 |  | 10:00 | 0 | 0.15298 | 1652.2269 | 10:00 | 1.3118 | 1.2058 | 0.10596 | 1.4073e-05 | 0
[13 empty] | 10:00 | 0.75164 | 0.91146 | 0.91784 |  | 10:00 | 0.75552 | 0.15298 | 1657.8935 | 10:00 | 1.3122 | 1.2062 | 0.10599 | 1.4078e-05 | 0
[13 empty] | 10:00 | 0.74403 | 0.91146 | 0.91784 |  | 10:00 | 0.74784 | 0.15298 | 1669.1693 | 10:00 | 1.3127 | 1.2066 | 0.10603 | 1.4083e-05 | 0
[13 empty] | 10:01 | 0.73658 | 0.91146 | 0.91784 |  | 10:01 | 0.74031 | 0.15298 | 1680.3305 | 10:01 | 1.3131 | 1.2071 | 0.10606 | 1.4088e-05 | 0
[13 empty] | 10:01 | 0.72929 | 0.91146 | 0.91784 |  | 10:01 | 0.73294 | 0.15298 | 1691.379 | 10:01 | 1.3136 | 1.2075 | 0.1061 | 1.4092e-05 | 0
[13 empty] | 10:01 | 1.1629 | 0.91146 | 0.91784 |  | 10:01 | 0.94609 | 0.15298 | 1703.9726 | 10:01 | 1.3143 | 1.2081 | 0.10616 | 1.41e-05 | 0
[13 empty] | 10:02 | 1.1468 | 0.91146 | 0.91784 |  | 10:02 | 1.1549 | 0.15298 | 1719.729 | 10:02 | 1.315 | 1.2087 | 0.10621 | 1.4107e-05 | 0
[13 empty] | 10:02 | 1.1311 | 0.91146 | 0.91784 |  | 10:02 | 1.139 | 0.15298 | 1736.933 | 10:02 | 1.3156 | 1.2094 | 0.10627 | 1.4115e-05 | 0
[13 empty] | 10:02 | 1.1157 | 0.91146 | 0.91784 |  | 10:02 | 1.1234 | 0.15298 | 1753.9021 | 10:02 | 1.3163 | 1.21 | 0.10632 | 1.4122e-05 | 0
[13 empty] | 10:02 | 1.1006 | 0.91146 | 0.91784 |  | 10:02 | 1.1082 | 0.15298 | 1770.6382 | 10:02 | 1.317 | 1.2106 | 0.10638 | 1.4129e-05 | 0
[13 empty] | 10:02 | 1.0859 | 0.91146 | 0.91784 |  | 10:02 | 1.0933 | 0.15298 | 1787.1489 | 10:02 | 1.3176 | 1.2112 | 0.10643 | 1.4136e-05 | 0
[13 empty] | 10:03 | 1.0714 | 0.91146 | 0.91784 |  | 10:03 | 1.0786 | 0.15298 | 1803.4381 | 10:03 | 1.3183 | 1.2118 | 0.10648 | 1.4143e-05 | 0
[13 empty] | 10:03 | 1.0572 | 0.91146 | 0.91784 |  | 10:03 | 1.0643 | 0.15298 | 1819.5115 | 10:03 | 1.3189 | 1.2124 | 0.10653 | 1.415e-05 | 0
[13 empty] | 10:03 | 1.0434 | 0.91146 | 0.91784 |  | 10:03 | 1.0503 | 0.15298 | 1835.3709 | 10:03 | 1.3196 | 1.213 | 0.10658 | 1.4157e-05 | 0
[13 empty] | 10:04 | 1.0298 | 0.91146 | 0.91784 |  | 10:04 | 1.0366 | 0.15298 | 1851.0222 | 10:04 | 1.3202 | 1.2135 | 0.10664 | 1.4163e-05 | 0
[13 empty] | 10:04 | 1.0164 | 0.91146 | 0.91784 |  | 10:04 | 1.0231 | 0.15298 | 1866.4692 | 10:04 | 1.3208 | 1.2141 | 0.10668 | 1.417e-05 | 0
[13 empty] | 10:04 | 1.0034 | 0.91146 | 0.91784 |  | 10:04 | 1.0099 | 0.15298 | 1881.7175 | 10:04 | 1.3214 | 1.2147 | 0.10673 | 1.4177e-05 | 0
[13 empty] | 10:04 | 0.99062 | 0.91146 | 0.91784 |  | 10:04 | 0.99701 | 0.15298 | 1896.7691 | 10:04 | 1.322 | 1.2152 | 0.10678 | 1.4183e-05 | 0
[13 empty] | 10:04 | 0.97811 | 0.91146 | 0.91784 |  | 10:04 | 0.98437 | 0.15298 | 1911.6354 | 10:04 | 1.3226 | 1.2158 | 0.10683 | 1.4189e-05 | 0
[13 empty] | 10:05 | 0.96585 | 0.91146 | 0.91784 |  | 10:05 | 0.97198 | 0.15298 | 1926.3032 | 10:05 | 1.3232 | 1.2163 | 0.10688 | 1.4196e-05 | 0
[13 empty] | 10:05 | 0.95385 | 0.91146 | 0.91784 |  | 10:05 | 0.95985 | 0.15298 | 1940.799 | 10:05 | 1.3238 | 1.2168 | 0.10692 | 1.4202e-05 | 0
[13 empty] | 10:05 | 0.94209 | 0.91146 | 0.91784 |  | 10:05 | 0.94797 | 0.15298 | 1955.1038 | 10:05 | 1.3243 | 1.2173 | 0.10697 | 1.4208e-05 | 0
[13 empty] | 10:06 | 0.93058 | 0.91146 | 0.91784 |  | 10:06 | 0.93634 | 0.15298 | 1969.2368 | 10:06 | 1.3249 | 1.2179 | 0.10702 | 1.4214e-05 | 0
[13 empty] | 10:06 | 0.9193 | 0.91146 | 0.91784 |  | 10:06 | 0.92494 | 0.15298 | 1983.1979 | 10:06 | 1.3254 | 1.2184 | 0.10706 | 1.422e-05 | 0
[13 empty] | 10:06 | 0.90825 | 0.91146 | 0.91784 |  | 10:06 | 0.91377 | 0.15298 | 1996.9871 | 10:06 | 1.326 | 1.2189 | 0.1071 | 1.4226e-05 | 0
[13 empty] | 10:06 | 0.89743 | 0.91146 | 0.91784 |  | 10:06 | 0.90284 | 0.15298 | 2010.6044 | 10:06 | 1.3266 | 1.2194 | 0.10715 | 1.4232e-05 | 0
[13 empty] | 10:06 | 0.88683 | 0.91146 | 0.91784 |  | 10:06 | 0.89213 | 0.15298 | 2024.0689 | 10:06 | 1.3271 | 1.2199 | 0.10719 | 1.4237e-05 | 0
[13 empty] | 10:07 | 0.87645 | 0.91146 | 0.91784 |  | 10:07 | 0.88164 | 0.15298 | 2037.3806 | 10:07 | 1.3276 | 1.2204 | 0.10723 | 1.4243e-05 | 0
[13 empty] | 10:07 | 0.86628 | 0.91146 | 0.91784 |  | 10:07 | 0.87137 | 0.15298 | 2050.5204 | 10:07 | 1.3281 | 1.2208 | 0.10728 | 1.4249e-05 | 0
[13 empty] | 10:07 | 0.85633 | 0.91146 | 0.91784 |  | 10:07 | 0.8613 | 0.15298 | 2063.5075 | 10:07 | 1.3286 | 1.2213 | 0.10732 | 1.4254e-05 | 0
[13 empty] | 10:08 | 0.84657 | 0.91146 | 0.91784 |  | 10:08 | 0.85145 | 0.15298 | 2076.3608 | 10:08 | 1.3292 | 1.2218 | 0.10736 | 1.426e-05 | 0
[13 empty] | 10:08 | 0.83702 | 0.91146 | 0.91784 |  | 10:08 | 0.8418 | 0.15298 | 2089.0614 | 10:08 | 1.3297 | 1.2223 | 0.1074 | 1.4265e-05 | 0
[13 empty] | 10:08 | 0.82766 | 0.91146 | 0.91784 |  | 10:08 | 0.83234 | 0.15298 | 2101.6092 | 10:08 | 1.3302 | 1.2227 | 0.10744 | 1.4271e-05 | 0
[13 empty] | 10:08 | 0.8185 | 0.91146 | 0.91784 |  | 10:08 | 0.82308 | 0.15298 | 2114.0232 | 10:08 | 1.3307 | 1.2232 | 0.10748 | 1.4276e-05 | 0
[13 empty] | 10:09 | 0.80952 | 0.91146 | 0.91784 |  | 10:09 | 0.81401 | 0.15298 | 2126.3036 | 10:09 | 1.3312 | 1.2236 | 0.10752 | 1.4281e-05 | 0
[13 empty] | 10:09 | 0.80073 | 0.91146 | 0.91784 |  | 10:09 | 0.80512 | 0.15298 | 2138.4503 | 10:09 | 1.3316 | 1.2241 | 0.10756 | 1.4286e-05 | 0
[13 empty] | 10:09 | 0.79211 | 0.91146 | 0.91784 |  | 10:09 | 0.79642 | 0.15298 | 2150.4634 | 10:09 | 1.3321 | 1.2245 | 0.1076 | 1.4291e-05 | 0
[13 empty] | 10:09 | 0.78368 | 0.91146 | 0.91784 |  | 10:09 | 0.7879 | 0.15298 | 2162.3427 | 10:09 | 1.3326 | 1.2249 | 0.10764 | 1.4297e-05 | 0
[13 empty] | 10:10 | 0.77542 | 0.91146 | 0.91784 |  | 10:10 | 0.77955 | 0.15298 | 2174.1074 | 10:10 | 1.3331 | 1.2254 | 0.10768 | 1.4302e-05 | 0
[13 empty] | 10:10 | 0.76733 | 0.91146 | 0.91784 |  | 10:10 | 0.77137 | 0.15298 | 2185.7385 | 10:10 | 1.3335 | 1.2258 | 0.10771 | 1.4307e-05 | 0
[13 empty] | 10:10 | 0.7594 | 0.91146 | 0.91784 |  | 10:10 | 0.76336 | 0.15298 | 2197.2358 | 10:10 | 1.334 | 1.2262 | 0.10775 | 1.4312e-05 | 0
[13 empty] | 10:10 | 0.75164 | 0.91146 | 0.91784 |  | 10:10 | 0 | 0.15298 | 2202.9654 | 10:10 | 1.3344 | 1.2266 | 0.10779 | 1.4316e-05 | 0
[13 empty] | 10:11 | 0.74403 | 0.91146 | 0.91784 |  | 10:11 | 0 | 0.15298 | 2202.9654 | 10:11 | 1.3349 | 1.2271 | 0.10782 | 1.4321e-05 | 0
[13 empty] | 10:11 | 0.73658 | 0.91146 | 0.91784 |  | 10:11 | 0 | 0.15298 | 2202.9654 | 10:11 | 1.3353 | 1.2275 | 0.10786 | 1.4326e-05 | 0
[13 empty] | 10:11 | 0.72929 | 0.91146 | 0.91784 |  | 10:11 | 0 | 0.15298 | 2202.9654 | 10:11 | 1.3358 | 1.2279 | 0.10789 | 1.4331e-05 | 0
[13 empty] | 10:11 | 1.1629 | 0.91146 | 0.91784 |  | 10:11 | 0 | 0.15298 | 2202.9654 | 10:11 | 1.3365 | 1.2285 | 0.10795 | 1.4338e-05 | 0
[13 empty] | 10:12 | 1.1468 | 0.91146 | 0.91784 |  | 10:12 | 0 | 0.15298 | 2202.9654 | 10:12 | 1.3372 | 1.2292 | 0.10801 | 1.4346e-05 | 0
[13 empty] | 10:12 | 1.1311 | 0.91146 | 0.91784 |  | 10:12 | 0 | 0.15298 | 2202.9654 | 10:12 | 1.3379 | 1.2298 | 0.10806 | 1.4353e-05 | 0
[13 empty] | 10:12 | 1.1157 | 0.91146 | 0.91784 |  | 10:12 | 0 | 0.15298 | 2202.9654 | 10:12 | 1.3385 | 1.2304 | 0.10812 | 1.436e-05 | 0
[13 empty] | 10:12 | 1.1006 | 0.91146 | 0.91784 |  | 10:12 | 0 | 0.15298 | 2202.9654 | 10:12 | 1.3392 | 1.231 | 0.10817 | 1.4367e-05 | 0
[13 empty] | 10:13 | 1.0859 | 0.91146 | 0.91784 |  | 10:13 | 0 | 0.15298 | 2202.9654 | 10:13 | 1.3399 | 1.2316 | 0.10822 | 1.4375e-05 | 0
[13 empty] | 10:13 | 1.0714 | 0.91146 | 0.91784 |  | 10:13 | 0 | 0.15298 | 2202.9654 | 10:13 | 1.3405 | 1.2322 | 0.10828 | 1.4381e-05 | 0
[13 empty] | 10:13 | 1.0572 | 0.91146 | 0.91784 |  | 10:13 | 0 | 0.15298 | 2202.9654 | 10:13 | 1.3412 | 1.2328 | 0.10833 | 1.4388e-05 | 0
[13 empty] | 10:13 | 1.0434 | 0.91146 | 0.91784 |  | 10:13 | 0 | 0.15298 | 2202.9654 | 10:13 | 1.3418 | 1.2334 | 0.10838 | 1.4395e-05 | 0
[13 empty] | 10:14 | 1.0298 | 0.91146 | 0.91784 |  | 10:14 | 0 | 0.15298 | 2202.9654 | 10:14 | 1.3424 | 1.234 | 0.10843 | 1.4402e-05 | 0
[13 empty] | 10:14 | 1.0164 | 0.91146 | 0.91784 |  | 10:14 | 0 | 0.15298 | 2202.9654 | 10:14 | 1.343 | 1.2345 | 0.10848 | 1.4409e-05 | 0
[13 empty] | 10:14 | 1.0034 | 0.91146 | 0.91784 |  | 10:14 | 0 | 0.15298 | 2202.9654 | 10:14 | 1.3436 | 1.2351 | 0.10853 | 1.4415e-05 | 0
[13 empty] | 10:14 | 0.99062 | 0.91146 | 0.91784 |  | 10:14 | 0 | 0.15298 | 2202.9654 | 10:14 | 1.3442 | 1.2356 | 0.10858 | 1.4421e-05 | 0
[13 empty] | 10:14 | 0.97811 | 0.91146 | 0.91784 |  | 10:14 | 0 | 0.15298 | 2202.9654 | 10:14 | 1.3448 | 1.2362 | 0.10863 | 1.4428e-05 | 0
[13 empty] | 10:15 | 0.96585 | 0.91146 | 0.91784 |  | 10:15 | 0 | 0.15298 | 2202.9654 | 10:15 | 1.3454 | 1.2367 | 0.10867 | 1.4434e-05 | 0
[13 empty] | 10:15 | 0.95385 | 0.91146 | 0.91784 |  | 10:15 | 0 | 0.15298 | 2202.9654 | 10:15 | 1.346 | 1.2373 | 0.10872 | 1.444e-05 | 0
[13 empty] | 10:15 | 0.94209 | 0.91146 | 0.91784 |  | 10:15 | 0 | 0.15298 | 2202.9654 | 10:15 | 1.3466 | 1.2378 | 0.10876 | 1.4446e-05 | 0
[13 empty] | 10:16 | 0.93058 | 0.91146 | 0.91784 |  | 10:16 | 0 | 0.15298 | 2202.9654 | 10:16 | 1.3471 | 1.2383 | 0.10881 | 1.4452e-05 | 0
[13 empty] | 10:16 | 0.9193 | 0.91146 | 0.91784 |  | 10:16 | 0 | 0.15298 | 2202.9654 | 10:16 | 1.3477 | 1.2388 | 0.10885 | 1.4458e-05 | 0
[13 empty] | 10:16 | 0.90825 | 0.91146 | 0.91784 |  | 10:16 | 0 | 0.15298 | 2202.9654 | 10:16 | 1.3482 | 1.2393 | 0.1089 | 1.4464e-05 | 0
[13 empty] | 10:16 | 0.89743 | 0.91146 | 0.91784 |  | 10:16 | 0 | 0.15298 | 2202.9654 | 10:16 | 1.3488 | 1.2398 | 0.10894 | 1.447e-05 | 0
[13 empty] | 10:16 | 0.88683 | 0.91146 | 0.91784 |  | 10:16 | 0 | 0.15298 | 2202.9654 | 10:16 | 1.3493 | 1.2403 | 0.10899 | 1.4476e-05 | 0
[13 empty] | 10:17 | 0.87645 | 0.91146 | 0.91784 |  | 10:17 | 0 | 0.15298 | 2202.9654 | 10:17 | 1.3498 | 1.2408 | 0.10903 | 1.4482e-05 | 0
[13 empty] | 10:17 | 0.86628 | 0.91146 | 0.91784 |  | 10:17 | 0 | 0.15298 | 2202.9654 | 10:17 | 1.3504 | 1.2413 | 0.10907 | 1.4487e-05 | 0
[13 empty] | 10:17 | 0.85633 | 0.91146 | 0.91784 |  | 10:17 | 0 | 0.15298 | 2202.9654 | 10:17 | 1.3509 | 1.2418 | 0.10911 | 1.4493e-05 | 0
[13 empty] | 10:18 | 0.84657 | 0.91146 | 0.91784 |  | 10:18 | 0 | 0.15298 | 2202.9654 | 10:18 | 1.3514 | 1.2422 | 0.10916 | 1.4498e-05 | 0
[13 empty] | 10:18 | 0.83702 | 0.91146 | 0.91784 |  | 10:18 | 0 | 0.15298 | 2202.9654 | 10:18 | 1.3519 | 1.2427 | 0.1092 | 1.4504e-05 | 0
[13 empty] | 10:18 | 0.82766 | 0.91146 | 0.91784 |  | 10:18 | 0 | 0.15298 | 2202.9654 | 10:18 | 1.3524 | 1.2431 | 0.10924 | 1.4509e-05 | 0
[13 empty] | 10:18 | 0.8185 | 0.91146 | 0.91784 |  | 10:18 | 0 | 0.15298 | 2202.9654 | 10:18 | 1.3529 | 1.2436 | 0.10928 | 1.4514e-05 | 0
[13 empty] | 10:18 | 0.80952 | 0.91146 | 0.91784 |  | 10:18 | 0 | 0.15298 | 2202.9654 | 10:18 | 1.3534 | 1.2441 | 0.10932 | 1.452e-05 | 0
[13 empty] | 10:19 | 0.80073 | 0.91146 | 0.91784 |  | 10:19 | 0 | 0.15298 | 2202.9654 | 10:19 | 1.3539 | 1.2445 | 0.10935 | 1.4525e-05 | 0
[13 empty] | 10:19 | 0.79211 | 0.91146 | 0.91784 |  | 10:19 | 0 | 0.15298 | 2202.9654 | 10:19 | 1.3544 | 1.2449 | 0.10939 | 1.453e-05 | 0
[13 empty] | 10:19 | 0.78368 | 0.91146 | 0.91784 |  | 10:19 | 0 | 0.15298 | 2202.9654 | 10:19 | 1.3548 | 1.2454 | 0.10943 | 1.4535e-05 | 0
[13 empty] | 10:20 | 0.77542 | 0.91146 | 0.91784 |  | 10:20 | 0 | 0.15298 | 2202.9654 | 10:20 | 1.3553 | 1.2458 | 0.10947 | 1.454e-05 | 0
[13 empty] | 10:20 | 0.76733 | 0.91146 | 0.91784 |  | 10:20 | 0 | 0.15298 | 2202.9654 | 10:20 | 1.3558 | 1.2462 | 0.10951 | 1.4545e-05 | 0
[13 empty] | 10:20 | 0.7594 | 0.91146 | 0.91784 |  | 10:20 | 0 | 0.15298 | 2202.9654 | 10:20 | 1.3562 | 1.2467 | 0.10955 | 1.455e-05 | 0
[13 empty] | 10:20 | 0.75164 | 0.91146 | 0.91784 |  | 10:20 | 0 | 0.15298 | 2202.9654 | 10:20 | 1.3567 | 1.2471 | 0.10958 | 1.4555e-05 | 0
[13 empty] | 10:20 | 0.74403 | 0.91146 | 0.91784 |  | 10:20 | 0 | 0.15298 | 2202.9654 | 10:20 | 1.3571 | 1.2475 | 0.10962 | 1.456e-05 | 0
[13 empty] | 10:21 | 0.73658 | 0.91146 | 0.91784 |  | 10:21 | 0 | 0.15298 | 2202.9654 | 10:21 | 1.3576 | 1.2479 | 0.10965 | 1.4565e-05 | 0
[13 empty] | 10:21 | 0.72929 | 0.91146 | 0.91784 |  | 10:21 | 0 | 0.15298 | 2202.9654 | 10:21 | 1.358 | 1.2483 | 0.10969 | 1.4569e-05 | 0
[13 empty] | 10:21 | 1.1629 | 0.91146 | 0.91784 |  | 10:21 | 0 | 0.15298 | 2202.9654 | 10:21 | 1.3587 | 1.249 | 0.10975 | 1.4577e-05 | 0
[13 empty] | 10:22 | 1.1468 | 0.91146 | 0.91784 |  | 10:22 | 0 | 0.15298 | 2202.9654 | 10:22 | 1.3594 | 1.2496 | 0.1098 | 1.4584e-05 | 0
[13 empty] | 10:22 | 1.1311 | 0.91146 | 0.91784 |  | 10:22 | 0 | 0.15298 | 2202.9654 | 10:22 | 1.3601 | 1.2502 | 0.10986 | 1.4592e-05 | 0
[13 empty] | 10:22 | 1.1157 | 0.91146 | 0.91784 |  | 10:22 | 0 | 0.15298 | 2202.9654 | 10:22 | 1.3608 | 1.2508 | 0.10991 | 1.4599e-05 | 0
[13 empty] | 10:22 | 1.1006 | 0.91146 | 0.91784 |  | 10:22 | 0 | 0.15298 | 2202.9654 | 10:22 | 1.3614 | 1.2515 | 0.10997 | 1.4606e-05 | 0
[13 empty] | 10:22 | 1.0859 | 0.91146 | 0.91784 |  | 10:22 | 0 | 0.15298 | 2202.9654 | 10:22 | 1.3621 | 1.2521 | 0.11002 | 1.4613e-05 | 0
[13 empty] | 10:23 | 1.0714 | 0.91146 | 0.91784 |  | 10:23 | 0 | 0.15298 | 2202.9654 | 10:23 | 1.3627 | 1.2527 | 0.11007 | 1.462e-05 | 0
[13 empty] | 10:23 | 1.0572 | 0.91146 | 0.91784 |  | 10:23 | 0 | 0.15298 | 2202.9654 | 10:23 | 1.3634 | 1.2532 | 0.11012 | 1.4627e-05 | 0
[13 empty] | 10:23 | 1.0434 | 0.91146 | 0.91784 |  | 10:23 | 0 | 0.15298 | 2202.9654 | 10:23 | 1.364 | 1.2538 | 0.11017 | 1.4634e-05 | 0
[13 empty] | 10:24 | 1.0298 | 0.91146 | 0.91784 |  | 10:24 | 0 | 0.15298 | 2202.9654 | 10:24 | 1.3646 | 1.2544 | 0.11023 | 1.464e-05 | 0
[13 empty] | 10:24 | 1.0164 | 0.91146 | 0.91784 |  | 10:24 | 0 | 0.15298 | 2202.9654 | 10:24 | 1.3653 | 1.255 | 0.11028 | 1.4647e-05 | 0
[13 empty] | 10:24 | 1.0034 | 0.91146 | 0.91784 |  | 10:24 | 0 | 0.15298 | 2202.9654 | 10:24 | 1.3659 | 1.2555 | 0.11032 | 1.4653e-05 | 0
[13 empty] | 10:24 | 0.99062 | 0.91146 | 0.91784 |  | 10:24 | 0 | 0.15298 | 2202.9654 | 10:24 | 1.3665 | 1.2561 | 0.11037 | 1.466e-05 | 0
[13 empty] | 10:24 | 0.97811 | 0.91146 | 0.91784 |  | 10:24 | 0 | 0.15298 | 2202.9654 | 10:24 | 1.3671 | 1.2566 | 0.11042 | 1.4666e-05 | 0
[13 empty] | 10:25 | 0.96585 | 0.91146 | 0.91784 |  | 10:25 | 0 | 0.15298 | 2202.9654 | 10:25 | 1.3676 | 1.2572 | 0.11047 | 1.4672e-05 | 0
[13 empty] | 10:25 | 0.95385 | 0.91146 | 0.91784 |  | 10:25 | 0 | 0.15298 | 2202.9654 | 10:25 | 1.3682 | 1.2577 | 0.11051 | 1.4679e-05 | 0
[13 empty] | 10:25 | 0.94209 | 0.91146 | 0.91784 |  | 10:25 | 0 | 0.15298 | 2202.9654 | 10:25 | 1.3688 | 1.2582 | 0.11056 | 1.4685e-05 | 0
[13 empty] | 10:26 | 0.93058 | 0.91146 | 0.91784 |  | 10:26 | 0 | 0.15298 | 2202.9654 | 10:26 | 1.3694 | 1.2587 | 0.11061 | 1.4691e-05 | 0
[13 empty] | 10:26 | 0.9193 | 0.91146 | 0.91784 |  | 10:26 | 0 | 0.15298 | 2202.9654 | 10:26 | 1.3699 | 1.2592 | 0.11065 | 1.4697e-05 | 0
[13 empty] | 10:26 | 0.90825 | 0.91146 | 0.91784 |  | 10:26 | 0 | 0.15298 | 2202.9654 | 10:26 | 1.3705 | 1.2597 | 0.1107 | 1.4703e-05 | 0
[13 empty] | 10:26 | 0.89743 | 0.91146 | 0.91784 |  | 10:26 | 0 | 0.15298 | 2202.9654 | 10:26 | 1.371 | 1.2602 | 0.11074 | 1.4709e-05 | 0
[13 empty] | 10:26 | 0.88683 | 0.91146 | 0.91784 |  | 10:26 | 0 | 0.15298 | 2202.9654 | 10:26 | 1.3715 | 1.2607 | 0.11078 | 1.4714e-05 | 0
[13 empty] | 10:27 | 0.87645 | 0.91146 | 0.91784 |  | 10:27 | 0 | 0.15298 | 2202.9654 | 10:27 | 1.3721 | 1.2612 | 0.11083 | 1.472e-05 | 0
[13 empty] | 10:27 | 0.86628 | 0.91146 | 0.91784 |  | 10:27 | 0 | 0.15298 | 2202.9654 | 10:27 | 1.3726 | 1.2617 | 0.11087 | 1.4726e-05 | 0
[13 empty] | 10:27 | 0.85633 | 0.91146 | 0.91784 |  | 10:27 | 0 | 0.15298 | 2202.9654 | 10:27 | 1.3731 | 1.2622 | 0.11091 | 1.4731e-05 | 0
[13 empty] | 10:28 | 0.84657 | 0.91146 | 0.91784 |  | 10:28 | 0 | 0.15298 | 2202.9654 | 10:28 | 1.3736 | 1.2627 | 0.11095 | 1.4737e-05 | 0
[13 empty] | 10:28 | 0.83702 | 0.91146 | 0.91784 |  | 10:28 | 0 | 0.15298 | 2202.9654 | 10:28 | 1.3741 | 1.2631 | 0.11099 | 1.4742e-05 | 0
[13 empty] | 10:28 | 0.82766 | 0.91146 | 0.91784 |  | 10:28 | 0 | 0.15298 | 2202.9654 | 10:28 | 1.3746 | 1.2636 | 0.11103 | 1.4748e-05 | 0
[13 empty] | 10:28 | 0.8185 | 0.91146 | 0.91784 |  | 10:28 | 0 | 0.15298 | 2202.9654 | 10:28 | 1.3751 | 1.264 | 0.11107 | 1.4753e-05 | 0
[13 empty] | 10:28 | 0.80952 | 0.91146 | 0.91784 |  | 10:28 | 0 | 0.15298 | 2202.9654 | 10:28 | 1.3756 | 1.2645 | 0.11111 | 1.4758e-05 | 0
[13 empty] | 10:29 | 0.80073 | 0.91146 | 0.91784 |  | 10:29 | 0 | 0.15298 | 2202.9654 | 10:29 | 1.3761 | 1.2649 | 0.11115 | 1.4763e-05 | 0
[13 empty] | 10:29 | 0.79211 | 0.91146 | 0.91784 |  | 10:29 | 0 | 0.15298 | 2202.9654 | 10:29 | 1.3766 | 1.2654 | 0.11119 | 1.4768e-05 | 0
[13 empty] | 10:29 | 0.78368 | 0.91146 | 0.91784 |  | 10:29 | 0 | 0.15298 | 2202.9654 | 10:29 | 1.3771 | 1.2658 | 0.11123 | 1.4774e-05 | 0
[13 empty] | 10:30 | 0.77542 | 0.91146 | 0.91784 |  | 10:30 | 0 | 0.15298 | 2202.9654 | 10:30 | 1.3775 | 1.2663 | 0.11127 | 1.4778e-05 | 0
[13 empty] | 10:30 | 0.76733 | 0.91146 | 0.91784 |  | 10:30 | 0 | 0.15298 | 2202.9654 | 10:30 | 1.378 | 1.2667 | 0.1113 | 1.4783e-05 | 0
[13 empty] | 10:30 | 0.7594 | 0.91146 | 0.91784 |  | 10:30 | 0 | 0.15298 | 2202.9654 | 10:30 | 1.3785 | 1.2671 | 0.11134 | 1.4788e-05 | 0
[13 empty] | 10:30 | 0.75164 | 0.91146 | 0.91784 |  | 10:30 | 0 | 0.15298 | 2202.9654 | 10:30 | 1.3789 | 1.2675 | 0.11138 | 1.4793e-05 | 0
[13 empty] | 10:30 | 0.74403 | 0.91146 | 0.91784 |  | 10:30 | 0 | 0.15298 | 2202.9654 | 10:30 | 1.3794 | 1.2679 | 0.11141 | 1.4798e-05 | 0
[13 empty] | 10:31 | 0.73658 | 0.91146 | 0.91784 |  | 10:31 | 0 | 0.15298 | 2202.9654 | 10:31 | 1.3798 | 1.2683 | 0.11145 | 1.4803e-05 | 0
[13 empty] | 10:31 | 0.72929 | 0.91146 | 0.91784 |  | 10:31 | 0 | 0.15298 | 2202.9654 | 10:31 | 1.3802 | 1.2687 | 0.11149 | 1.4808e-05 | 0
[13 empty] | 10:31 | 1.1629 | 0.91146 | 0.91784 |  | 10:31 | 0 | 0.15298 | 2202.9654 | 10:31 | 1.3809 | 1.2694 | 0.11154 | 1.4815e-05 | 0
[13 empty] | 10:32 | 1.1468 | 0.91146 | 0.91784 |  | 10:32 | 0 | 0.15298 | 2202.9654 | 10:32 | 1.3817 | 1.27 | 0.1116 | 1.4823e-05 | 0
[13 empty] | 10:32 | 1.1311 | 0.91146 | 0.91784 |  | 10:32 | 0 | 0.15298 | 2202.9654 | 10:32 | 1.3823 | 1.2707 | 0.11165 | 1.483e-05 | 0
[13 empty] | 10:32 | 1.1157 | 0.91146 | 0.91784 |  | 10:32 | 0 | 0.15298 | 2202.9654 | 10:32 | 1.383 | 1.2713 | 0.11171 | 1.4837e-05 | 0
[13 empty] | 10:32 | 1.1006 | 0.91146 | 0.91784 |  | 10:32 | 0 | 0.15298 | 2202.9654 | 10:32 | 1.3837 | 1.2719 | 0.11176 | 1.4844e-05 | 0
[13 empty] | 10:32 | 1.0859 | 0.91146 | 0.91784 |  | 10:32 | 0 | 0.15298 | 2202.9654 | 10:32 | 1.3843 | 1.2725 | 0.11181 | 1.4851e-05 | 0
[13 empty] | 10:33 | 1.0714 | 0.91146 | 0.91784 |  | 10:33 | 0 | 0.15298 | 2202.9654 | 10:33 | 1.385 | 1.2731 | 0.11187 | 1.4859e-05 | 0
[13 empty] | 10:33 | 1.0572 | 0.91146 | 0.91784 |  | 10:33 | 0 | 0.15298 | 2202.9654 | 10:33 | 1.3856 | 1.2737 | 0.11192 | 1.4865e-05 | 0
[13 empty] | 10:33 | 1.0434 | 0.91146 | 0.91784 |  | 10:33 | 0 | 0.15298 | 2202.9654 | 10:33 | 1.3862 | 1.2743 | 0.11197 | 1.4872e-05 | 0
[13 empty] | 10:34 | 1.0298 | 0.91146 | 0.91784 |  | 10:34 | 0 | 0.15298 | 2202.9654 | 10:34 | 1.3869 | 1.2748 | 0.11202 | 1.4879e-05 | 0
[13 empty] | 10:34 | 1.0164 | 0.91146 | 0.91784 |  | 10:34 | 0 | 0.15298 | 2202.9654 | 10:34 | 1.3875 | 1.2754 | 0.11207 | 1.4885e-05 | 0
[13 empty] | 10:34 | 1.0034 | 0.91146 | 0.91784 |  | 10:34 | 0 | 0.15298 | 2202.9654 | 10:34 | 1.3881 | 1.276 | 0.11212 | 1.4892e-05 | 0
[13 empty] | 10:34 | 0.99062 | 0.91146 | 0.91784 |  | 10:34 | 0 | 0.15298 | 2202.9654 | 10:34 | 1.3887 | 1.2765 | 0.11217 | 1.4898e-05 | 0
[13 empty] | 10:34 | 0.97811 | 0.91146 | 0.91784 |  | 10:34 | 0 | 0.15298 | 2202.9654 | 10:34 | 1.3893 | 1.277 | 0.11222 | 1.4905e-05 | 0
[13 empty] | 10:35 | 0.96585 | 0.91146 | 0.91784 |  | 10:35 | 0 | 0.15298 | 2202.9654 | 10:35 | 1.3899 | 1.2776 | 0.11226 | 1.4911e-05 | 0
[13 empty] | 10:35 | 0.95385 | 0.91146 | 0.91784 |  | 10:35 | 0 | 0.15298 | 2202.9654 | 10:35 | 1.3904 | 1.2781 | 0.11231 | 1.4917e-05 | 0
[13 empty] | 10:35 | 0.94209 | 0.91146 | 0.91784 |  | 10:35 | 0 | 0.15298 | 2202.9654 | 10:35 | 1.391 | 1.2787 | 0.11236 | 1.4923e-05 | 0
[13 empty] | 10:36 | 0.93058 | 0.91146 | 0.91784 |  | 10:36 | 0 | 0.15298 | 2202.9654 | 10:36 | 1.3916 | 1.2792 | 0.1124 | 1.4929e-05 | 0
[13 empty] | 10:36 | 0.9193 | 0.91146 | 0.91784 |  | 10:36 | 0 | 0.15298 | 2202.9654 | 10:36 | 1.3921 | 1.2797 | 0.11245 | 1.4935e-05 | 0
[13 empty] | 10:36 | 0.90825 | 0.91146 | 0.91784 |  | 10:36 | 0 | 0.15298 | 2202.9654 | 10:36 | 1.3927 | 1.2802 | 0.11249 | 1.4941e-05 | 0
[13 empty] | 10:36 | 0.89743 | 0.91146 | 0.91784 |  | 10:36 | 0 | 0.15298 | 2202.9654 | 10:36 | 1.3932 | 1.2807 | 0.11253 | 1.4947e-05 | 0
[13 empty] | 10:36 | 0.88683 | 0.91146 | 0.91784 |  | 10:36 | 0 | 0.15298 | 2202.9654 | 10:36 | 1.3938 | 1.2812 | 0.11258 | 1.4953e-05 | 0
[13 empty] | 10:37 | 0.87645 | 0.91146 | 0.91784 |  | 10:37 | 0 | 0.15298 | 2202.9654 | 10:37 | 1.3943 | 1.2817 | 0.11262 | 1.4958e-05 | 0
[13 empty] | 10:37 | 0.86628 | 0.91146 | 0.91784 |  | 10:37 | 0 | 0.15298 | 2202.9654 | 10:37 | 1.3948 | 1.2821 | 0.11266 | 1.4964e-05 | 0
[13 empty] | 10:37 | 0.85633 | 0.91146 | 0.91784 |  | 10:37 | 0 | 0.15298 | 2202.9654 | 10:37 | 1.3953 | 1.2826 | 0.1127 | 1.497e-05 | 0
[13 empty] | 10:38 | 0.84657 | 0.91146 | 0.91784 |  | 10:38 | 0 | 0.15298 | 2202.9654 | 10:38 | 1.3959 | 1.2831 | 0.11275 | 1.4975e-05 | 0
[13 empty] | 10:38 | 0.83702 | 0.91146 | 0.91784 |  | 10:38 | 0 | 0.15298 | 2202.9654 | 10:38 | 1.3964 | 1.2836 | 0.11279 | 1.4981e-05 | 0
[13 empty] | 10:38 | 0.82766 | 0.91146 | 0.91784 |  | 10:38 | 0 | 0.15298 | 2202.9654 | 10:38 | 1.3969 | 1.284 | 0.11283 | 1.4986e-05 | 0
[13 empty] | 10:38 | 0.8185 | 0.91146 | 0.91784 |  | 10:38 | 0 | 0.15298 | 2202.9654 | 10:38 | 1.3974 | 1.2845 | 0.11287 | 1.4991e-05 | 0
[13 empty] | 10:38 | 0.80952 | 0.91146 | 0.91784 |  | 10:38 | 0 | 0.15298 | 2202.9654 | 10:38 | 1.3979 | 1.2849 | 0.11291 | 1.4997e-05 | 0
[13 empty] | 10:39 | 0.80073 | 0.91146 | 0.91784 |  | 10:39 | 0 | 0.15298 | 2202.9654 | 10:39 | 1.3983 | 1.2854 | 0.11295 | 1.5002e-05 | 0
[13 empty] | 10:39 | 0.79211 | 0.91146 | 0.91784 |  | 10:39 | 0 | 0.15298 | 2202.9654 | 10:39 | 1.3988 | 1.2858 | 0.11299 | 1.5007e-05 | 0
[13 empty] | 10:39 | 0.78368 | 0.91146 | 0.91784 |  | 10:39 | 0 | 0.15298 | 2202.9654 | 10:39 | 1.3993 | 1.2863 | 0.11302 | 1.5012e-05 | 0
[13 empty] | 10:40 | 0.77542 | 0.91146 | 0.91784 |  | 10:40 | 0 | 0.15298 | 2202.9654 | 10:40 | 1.3997 | 1.2867 | 0.11306 | 1.5017e-05 | 0
[13 empty] | 10:40 | 0.76733 | 0.91146 | 0.91784 |  | 10:40 | 0 | 0.15298 | 2202.9654 | 10:40 | 1.4002 | 1.2871 | 0.1131 | 1.5022e-05 | 0
[13 empty] | 10:40 | 0.7594 | 0.91146 | 0.91784 |  | 10:40 | 0 | 0.15298 | 2202.9654 | 10:40 | 1.4007 | 1.2875 | 0.11314 | 1.5027e-05 | 0
[13 empty] | 10:40 | 0.75164 | 0.91146 | 0.91784 |  | 10:40 | 0 | 0.15298 | 2202.9654 | 10:40 | 1.4011 | 1.288 | 0.11317 | 1.5032e-05 | 0
[13 empty] | 10:40 | 0.74403 | 0.91146 | 0.91784 |  | 10:40 | 0 | 0.15298 | 2202.9654 | 10:40 | 1.4016 | 1.2884 | 0.11321 | 1.5037e-05 | 0
[13 empty] | 10:41 | 0.73658 | 0.91146 | 0.91784 |  | 10:41 | 0 | 0.15298 | 2202.9654 | 10:41 | 1.402 | 1.2888 | 0.11325 | 1.5041e-05 | 0
[13 empty] | 10:41 | 0.72929 | 0.91146 | 0.91784 |  | 10:41 | 0 | 0.15298 | 2202.9654 | 10:41 | 1.4025 | 1.2892 | 0.11328 | 1.5046e-05 | 0
[13 empty] | 10:41 | 1.1629 | 0.91146 | 0.91784 |  | 10:41 | 0 | 0.15298 | 2202.9654 | 10:41 | 1.4032 | 1.2898 | 0.11334 | 1.5054e-05 | 0
[13 empty] | 10:42 | 1.1468 | 0.91146 | 0.91784 |  | 10:42 | 0 | 0.15298 | 2202.9654 | 10:42 | 1.4039 | 1.2905 | 0.11339 | 1.5061e-05 | 0
[13 empty] | 10:42 | 1.1311 | 0.91146 | 0.91784 |  | 10:42 | 0 | 0.15298 | 2202.9654 | 10:42 | 1.4045 | 1.2911 | 0.11345 | 1.5069e-05 | 0
[13 empty] | 10:42 | 1.1157 | 0.91146 | 0.91784 |  | 10:42 | 0 | 0.15298 | 2202.9654 | 10:42 | 1.4052 | 1.2917 | 0.1135 | 1.5076e-05 | 0
[13 empty] | 10:42 | 1.1006 | 0.91146 | 0.91784 |  | 10:42 | 0 | 0.15298 | 2202.9654 | 10:42 | 1.4059 | 1.2923 | 0.11356 | 1.5083e-05 | 0
[13 empty] | 10:42 | 1.0859 | 0.91146 | 0.91784 |  | 10:42 | 0 | 0.15298 | 2202.9654 | 10:42 | 1.4066 | 1.2929 | 0.11361 | 1.509e-05 | 0
[13 empty] | 10:43 | 1.0714 | 0.91146 | 0.91784 |  | 10:43 | 0 | 0.15298 | 2202.9654 | 10:43 | 1.4072 | 1.2935 | 0.11366 | 1.5097e-05 | 0
[13 empty] | 10:43 | 1.0572 | 0.91146 | 0.91784 |  | 10:43 | 0 | 0.15298 | 2202.9654 | 10:43 | 1.4079 | 1.2941 | 0.11371 | 1.5104e-05 | 0
[13 empty] | 10:43 | 1.0434 | 0.91146 | 0.91784 |  | 10:43 | 0 | 0.15298 | 2202.9654 | 10:43 | 1.4085 | 1.2947 | 0.11377 | 1.5111e-05 | 0
[13 empty] | 10:44 | 1.0298 | 0.91146 | 0.91784 |  | 10:44 | 0 | 0.15298 | 2202.9654 | 10:44 | 1.4091 | 1.2953 | 0.11382 | 1.5117e-05 | 0
[13 empty] | 10:44 | 1.0164 | 0.91146 | 0.91784 |  | 10:44 | 0 | 0.15298 | 2202.9654 | 10:44 | 1.4097 | 1.2958 | 0.11387 | 1.5124e-05 | 0
[13 empty] | 10:44 | 1.0034 | 0.91146 | 0.91784 |  | 10:44 | 0 | 0.15298 | 2202.9654 | 10:44 | 1.4103 | 1.2964 | 0.11392 | 1.513e-05 | 0
[13 empty] | 10:44 | 0.99062 | 0.91146 | 0.91784 |  | 10:44 | 0 | 0.15298 | 2202.9654 | 10:44 | 1.4109 | 1.2969 | 0.11396 | 1.5137e-05 | 0
[13 empty] | 10:44 | 0.97811 | 0.91146 | 0.91784 |  | 10:44 | 0 | 0.15298 | 2202.9654 | 10:44 | 1.4115 | 1.2975 | 0.11401 | 1.5143e-05 | 0
[13 empty] | 10:45 | 0.96585 | 0.91146 | 0.91784 |  | 10:45 | 0 | 0.15298 | 2202.9654 | 10:45 | 1.4121 | 1.298 | 0.11406 | 1.5149e-05 | 0
[13 empty] | 10:45 | 0.95385 | 0.91146 | 0.91784 |  | 10:45 | 0 | 0.15298 | 2202.9654 | 10:45 | 1.4127 | 1.2986 | 0.1141 | 1.5156e-05 | 0
[13 empty] | 10:45 | 0.94209 | 0.91146 | 0.91784 |  | 10:45 | 0 | 0.15298 | 2202.9654 | 10:45 | 1.4133 | 1.2991 | 0.11415 | 1.5162e-05 | 0
[13 empty] | 10:46 | 0.93058 | 0.91146 | 0.91784 |  | 10:46 | 0 | 0.15298 | 2202.9654 | 10:46 | 1.4138 | 1.2996 | 0.1142 | 1.5168e-05 | 0
[13 empty] | 10:46 | 0.9193 | 0.91146 | 0.91784 |  | 10:46 | 0 | 0.15298 | 2202.9654 | 10:46 | 1.4144 | 1.3001 | 0.11424 | 1.5174e-05 | 0
[13 empty] | 10:46 | 0.90825 | 0.91146 | 0.91784 |  | 10:46 | 0 | 0.15298 | 2202.9654 | 10:46 | 1.4149 | 1.3006 | 0.11429 | 1.518e-05 | 0
[13 empty] | 10:46 | 0.89743 | 0.91146 | 0.91784 |  | 10:46 | 0 | 0.15298 | 2202.9654 | 10:46 | 1.4155 | 1.3011 | 0.11433 | 1.5185e-05 | 0
[13 empty] | 10:46 | 0.88683 | 0.91146 | 0.91784 |  | 10:46 | 0 | 0.15298 | 2202.9654 | 10:46 | 1.416 | 1.3016 | 0.11437 | 1.5191e-05 | 0
[13 empty] | 10:47 | 0.87645 | 0.91146 | 0.91784 |  | 10:47 | 0 | 0.15298 | 2202.9654 | 10:47 | 1.4165 | 1.3021 | 0.11442 | 1.5197e-05 | 0
[13 empty] | 10:47 | 0.86628 | 0.91146 | 0.91784 |  | 10:47 | 0 | 0.15298 | 2202.9654 | 10:47 | 1.4171 | 1.3026 | 0.11446 | 1.5203e-05 | 0
[13 empty] | 10:47 | 0.85633 | 0.91146 | 0.91784 |  | 10:47 | 0 | 0.15298 | 2202.9654 | 10:47 | 1.4176 | 1.3031 | 0.1145 | 1.5208e-05 | 0
[13 empty] | 10:47 | 0.84657 | 0.91146 | 0.91784 |  | 10:47 | 0 | 0.15298 | 2202.9654 | 10:47 | 1.4181 | 1.3035 | 0.11454 | 1.5214e-05 | 0
[13 empty] | 10:48 | 0.83702 | 0.91146 | 0.91784 |  | 10:48 | 0 | 0.15298 | 2202.9654 | 10:48 | 1.4186 | 1.304 | 0.11458 | 1.5219e-05 | 0
[13 empty] | 10:48 | 0.82766 | 0.91146 | 0.91784 |  | 10:48 | 0 | 0.15298 | 2202.9654 | 10:48 | 1.4191 | 1.3045 | 0.11462 | 1.5224e-05 | 0
[13 empty] | 10:48 | 0.8185 | 0.91146 | 0.91784 |  | 10:48 | 0 | 0.15298 | 2202.9654 | 10:48 | 1.4196 | 1.3049 | 0.11466 | 1.523e-05 | 0
[13 empty] | 10:48 | 0.80952 | 0.91146 | 0.91784 |  | 10:48 | 0 | 0.15298 | 2202.9654 | 10:48 | 1.4201 | 1.3054 | 0.1147 | 1.5235e-05 | 0
[13 empty] | 10:49 | 0.80073 | 0.91146 | 0.91784 |  | 10:49 | 0 | 0.15298 | 2202.9654 | 10:49 | 1.4206 | 1.3058 | 0.11474 | 1.524e-05 | 0
[13 empty] | 10:49 | 0.79211 | 0.91146 | 0.91784 |  | 10:49 | 0 | 0.15298 | 2202.9654 | 10:49 | 1.421 | 1.3062 | 0.11478 | 1.5245e-05 | 0
[13 empty] | 10:49 | 0.78368 | 0.91146 | 0.91784 |  | 10:49 | 0 | 0.15298 | 2202.9654 | 10:49 | 1.4215 | 1.3067 | 0.11482 | 1.525e-05 | 0
[13 empty] | 10:49 | 0.77542 | 0.91146 | 0.91784 |  | 10:49 | 0 | 0.15298 | 2202.9654 | 10:49 | 1.422 | 1.3071 | 0.11486 | 1.5256e-05 | 0
[13 empty] | 10:50 | 0.76733 | 0.91146 | 0.91784 |  | 10:50 | 0 | 0.15298 | 2202.9654 | 10:50 | 1.4225 | 1.3075 | 0.11489 | 1.5261e-05 | 0
[13 empty] | 10:50 | 0.7594 | 0.91146 | 0.91784 |  | 10:50 | 0 | 0.15298 | 2202.9654 | 10:50 | 1.4229 | 1.308 | 0.11493 | 1.5266e-05 | 0
[13 empty] | 10:50 | 0.75164 | 0.91146 | 0.91784 |  | 10:50 | 0 | 0.15298 | 2202.9654 | 10:50 | 1.4234 | 1.3084 | 0.11497 | 1.527e-05 | 0
[13 empty] | 10:50 | 0.74403 | 0.91146 | 0.91784 |  | 10:50 | 0 | 0.15298 | 2202.9654 | 10:50 | 1.4238 | 1.3088 | 0.115 | 1.5275e-05 | 0
[13 empty] | 10:51 | 0.73658 | 0.91146 | 0.91784 |  | 10:51 | 0 | 0.15298 | 2202.9654 | 10:51 | 1.4243 | 1.3092 | 0.11504 | 1.528e-05 | 0
[13 empty] | 10:51 | 0.72929 | 0.91146 | 0.91784 |  | 10:51 | 0 | 0.15298 | 2202.9654 | 10:51 | 1.4247 | 1.3096 | 0.11508 | 1.5285e-05 | 0
[13 empty] | 10:51 | 1.1629 | 0.91146 | 0.91784 |  | 10:51 | 0 | 0.15298 | 2202.9654 | 10:51 | 1.4254 | 1.3103 | 0.11513 | 1.5292e-05 | 0
[13 empty] | 10:51 | 1.1468 | 0.91146 | 0.91784 |  | 10:51 | 0 | 0.15298 | 2202.9654 | 10:51 | 1.4261 | 1.3109 | 0.11519 | 1.53e-05 | 0
[13 empty] | 10:52 | 1.1311 | 0.91146 | 0.91784 |  | 10:52 | 0 | 0.15298 | 2202.9654 | 10:52 | 1.4268 | 1.3115 | 0.11524 | 1.5307e-05 | 0
[13 empty] | 10:52 | 1.1157 | 0.91146 | 0.91784 |  | 10:52 | 0 | 0.15298 | 2202.9654 | 10:52 | 1.4275 | 1.3121 | 0.1153 | 1.5314e-05 | 0
[13 empty] | 10:52 | 1.1006 | 0.91146 | 0.91784 |  | 10:52 | 0 | 0.15298 | 2202.9654 | 10:52 | 1.4281 | 1.3128 | 0.11535 | 1.5321e-05 | 0
[13 empty] | 10:52 | 1.0859 | 0.91146 | 0.91784 |  | 10:52 | 0 | 0.15298 | 2202.9654 | 10:52 | 1.4288 | 1.3134 | 0.11541 | 1.5329e-05 | 0
[13 empty] | 10:53 | 1.0714 | 0.91146 | 0.91784 |  | 10:53 | 0 | 0.15298 | 2202.9654 | 10:53 | 1.4294 | 1.314 | 0.11546 | 1.5335e-05 | 0
[13 empty] | 10:53 | 1.0572 | 0.91146 | 0.91784 |  | 10:53 | 0 | 0.15298 | 2202.9654 | 10:53 | 1.4301 | 1.3145 | 0.11551 | 1.5342e-05 | 0
[13 empty] | 10:53 | 1.0434 | 0.91146 | 0.91784 |  | 10:53 | 0 | 0.15298 | 2202.9654 | 10:53 | 1.4307 | 1.3151 | 0.11556 | 1.5349e-05 | 0
[13 empty] | 10:54 | 1.0298 | 0.91146 | 0.91784 |  | 10:54 | 0 | 0.15298 | 2202.9654 | 10:54 | 1.4313 | 1.3157 | 0.11561 | 1.5356e-05 | 0
[13 empty] | 10:54 | 1.0164 | 0.91146 | 0.91784 |  | 10:54 | 0 | 0.15298 | 2202.9654 | 10:54 | 1.4319 | 1.3163 | 0.11566 | 1.5362e-05 | 0
[13 empty] | 10:54 | 1.0034 | 0.91146 | 0.91784 |  | 10:54 | 0 | 0.15298 | 2202.9654 | 10:54 | 1.4326 | 1.3168 | 0.11571 | 1.5369e-05 | 0
[13 empty] | 10:54 | 0.99062 | 0.91146 | 0.91784 |  | 10:54 | 0 | 0.15298 | 2202.9654 | 10:54 | 1.4332 | 1.3174 | 0.11576 | 1.5375e-05 | 0
[13 empty] | 10:54 | 0.97811 | 0.91146 | 0.91784 |  | 10:54 | 0 | 0.15298 | 2202.9654 | 10:54 | 1.4337 | 1.3179 | 0.11581 | 1.5382e-05 | 0
[13 empty] | 10:55 | 0.96585 | 0.91146 | 0.91784 |  | 10:55 | 0 | 0.15298 | 2202.9654 | 10:55 | 1.4343 | 1.3185 | 0.11585 | 1.5388e-05 | 0
[13 empty] | 10:55 | 0.95385 | 0.91146 | 0.91784 |  | 10:55 | 0 | 0.15298 | 2202.9654 | 10:55 | 1.4349 | 1.319 | 0.1159 | 1.5394e-05 | 0
[13 empty] | 10:55 | 0.94209 | 0.91146 | 0.91784 |  | 10:55 | 0 | 0.15298 | 2202.9654 | 10:55 | 1.4355 | 1.3195 | 0.11595 | 1.54e-05 | 0
[13 empty] | 10:56 | 0.93058 | 0.91146 | 0.91784 |  | 10:56 | 0 | 0.15298 | 2202.9654 | 10:56 | 1.436 | 1.32 | 0.11599 | 1.5406e-05 | 0
[13 empty] | 10:56 | 0.9193 | 0.91146 | 0.91784 |  | 10:56 | 0 | 0.15298 | 2202.9654 | 10:56 | 1.4366 | 1.3205 | 0.11604 | 1.5412e-05 | 0
[13 empty] | 10:56 | 0.90825 | 0.91146 | 0.91784 |  | 10:56 | 0 | 0.15298 | 2202.9654 | 10:56 | 1.4371 | 1.321 | 0.11608 | 1.5418e-05 | 0
[13 empty] | 10:56 | 0.89743 | 0.91146 | 0.91784 |  | 10:56 | 0 | 0.15298 | 2202.9654 | 10:56 | 1.4377 | 1.3215 | 0.11613 | 1.5424e-05 | 0
[13 empty] | 10:56 | 0.88683 | 0.91146 | 0.91784 |  | 10:56 | 0 | 0.15298 | 2202.9654 | 10:56 | 1.4382 | 1.322 | 0.11617 | 1.543e-05 | 0
[13 empty] | 10:57 | 0.87645 | 0.91146 | 0.91784 |  | 10:57 | 0 | 0.15298 | 2202.9654 | 10:57 | 1.4387 | 1.3225 | 0.11621 | 1.5435e-05 | 0
[13 empty] | 10:57 | 0.86628 | 0.91146 | 0.91784 |  | 10:57 | 0 | 0.15298 | 2202.9654 | 10:57 | 1.4393 | 1.323 | 0.11625 | 1.5441e-05 | 0
[13 empty] | 10:57 | 0.85633 | 0.91146 | 0.91784 |  | 10:57 | 0 | 0.15298 | 2202.9654 | 10:57 | 1.4398 | 1.3235 | 0.1163 | 1.5447e-05 | 0
[13 empty] | 10:58 | 0.84657 | 0.91146 | 0.91784 |  | 10:58 | 0 | 0.15298 | 2202.9654 | 10:58 | 1.4403 | 1.324 | 0.11634 | 1.5452e-05 | 0
[13 empty] | 10:58 | 0.83702 | 0.91146 | 0.91784 |  | 10:58 | 0 | 0.15298 | 2202.9654 | 10:58 | 1.4408 | 1.3244 | 0.11638 | 1.5458e-05 | 0
[13 empty] | 10:58 | 0.82766 | 0.91146 | 0.91784 |  | 10:58 | 0 | 0.15298 | 2202.9654 | 10:58 | 1.4413 | 1.3249 | 0.11642 | 1.5463e-05 | 0
[13 empty] | 10:58 | 0.8185 | 0.91146 | 0.91784 |  | 10:58 | 0 | 0.15298 | 2202.9654 | 10:58 | 1.4418 | 1.3253 | 0.11646 | 1.5468e-05 | 0
[13 empty] | 10:58 | 0.80952 | 0.91146 | 0.91784 |  | 10:58 | 0 | 0.15298 | 2202.9654 | 10:58 | 1.4423 | 1.3258 | 0.1165 | 1.5473e-05 | 0
[13 empty] | 10:59 | 0.80073 | 0.91146 | 0.91784 |  | 10:59 | 0 | 0.15298 | 2202.9654 | 10:59 | 1.4428 | 1.3262 | 0.11654 | 1.5479e-05 | 0
[13 empty] | 10:59 | 0.79211 | 0.91146 | 0.91784 |  | 10:59 | 0 | 0.15298 | 2202.9654 | 10:59 | 1.4433 | 1.3267 | 0.11658 | 1.5484e-05 | 0
[13 empty] | 10:59 | 0.78368 | 0.91146 | 0.91784 |  | 10:59 | 0 | 0.15298 | 2202.9654 | 10:59 | 1.4437 | 1.3271 | 0.11661 | 1.5489e-05 | 0
[13 empty] | 11:00 | 0.77542 | 0.91146 | 0.91784 |  | 11:00 | 0 | 0.15298 | 2202.9654 | 11:00 | 1.4442 | 1.3275 | 0.11665 | 1.5494e-05 | 0
[13 empty] | 11:00 | 0.76733 | 0.91146 | 0.91784 |  | 11:00 | 0 | 0.15298 | 2202.9654 | 11:00 | 1.4447 | 1.328 | 0.11669 | 1.5499e-05 | 0
[13 empty] | 11:00 | 0.7594 | 0.91146 | 0.91784 |  | 11:00 | 0 | 0.15298 | 2202.9654 | 11:00 | 1.4451 | 1.3284 | 0.11673 | 1.5504e-05 | 0
[13 empty] | 11:00 | 0.75164 | 0.91146 | 0.91784 |  | 11:00 | 0.75552 | 0.15298 | 2208.6377 | 11:00 | 1.4456 | 1.3288 | 0.11676 | 1.5509e-05 | 0
[13 empty] | 11:00 | 0.74403 | 0.91146 | 0.91784 |  | 11:00 | 0.74784 | 0.15298 | 2219.9058 | 11:00 | 1.446 | 1.3292 | 0.1168 | 1.5514e-05 | 0
[13 empty] | 11:01 | 0.73658 | 0.91146 | 0.91784 |  | 11:01 | 0.74031 | 0.15298 | 2231.0785 | 11:01 | 1.4465 | 1.3296 | 0.11684 | 1.5518e-05 | 0
[13 empty] | 11:01 | 0.72929 | 0.91146 | 0.91784 |  | 11:01 | 0.73294 | 0.15298 | 2242.1175 | 11:01 | 1.4469 | 1.33 | 0.11687 | 1.5523e-05 | 0
[13 empty] | 11:01 | 1.1629 | 0.91146 | 0.91784 |  | 11:01 | 0.94609 | 0.15298 | 2254.7226 | 11:01 | 1.4476 | 1.3307 | 0.11693 | 1.5531e-05 | 0
[13 empty] | 11:02 | 1.1468 | 0.91146 | 0.91784 |  | 11:02 | 1.1549 | 0.15298 | 2270.4789 | 11:02 | 1.4483 | 1.3313 | 0.11698 | 1.5538e-05 | 0
[13 empty] | 11:02 | 1.1311 | 0.91146 | 0.91784 |  | 11:02 | 1.139 | 0.15298 | 2287.6676 | 11:02 | 1.449 | 1.332 | 0.11704 | 1.5545e-05 | 0
[13 empty] | 11:02 | 1.1157 | 0.91146 | 0.91784 |  | 11:02 | 1.1234 | 0.15298 | 2304.6463 | 11:02 | 1.4497 | 1.3326 | 0.11709 | 1.5553e-05 | 0
[13 empty] | 11:02 | 1.1006 | 0.91146 | 0.91784 |  | 11:02 | 1.1082 | 0.15298 | 2321.3767 | 11:02 | 1.4504 | 1.3332 | 0.11715 | 1.556e-05 | 0
[13 empty] | 11:02 | 1.0859 | 0.91146 | 0.91784 |  | 11:02 | 1.0933 | 0.15298 | 2337.8969 | 11:02 | 1.451 | 1.3338 | 0.1172 | 1.5567e-05 | 0
[13 empty] | 11:03 | 1.0714 | 0.91146 | 0.91784 |  | 11:03 | 1.0786 | 0.15298 | 2354.188 | 11:03 | 1.4517 | 1.3344 | 0.11725 | 1.5574e-05 | 0
[13 empty] | 11:03 | 1.0572 | 0.91146 | 0.91784 |  | 11:03 | 1.0643 | 0.15298 | 2370.25 | 11:03 | 1.4523 | 1.335 | 0.11731 | 1.5581e-05 | 0
[13 empty] | 11:03 | 1.0434 | 0.91146 | 0.91784 |  | 11:03 | 1.0503 | 0.15298 | 2386.1209 | 11:03 | 1.4529 | 1.3356 | 0.11736 | 1.5588e-05 | 0
[13 empty] | 11:04 | 1.0298 | 0.91146 | 0.91784 |  | 11:04 | 1.0366 | 0.15298 | 2401.7626 | 11:04 | 1.4536 | 1.3361 | 0.11741 | 1.5594e-05 | 0
[13 empty] | 11:04 | 1.0164 | 0.91146 | 0.91784 |  | 11:04 | 1.0231 | 0.15298 | 2417.2134 | 11:04 | 1.4542 | 1.3367 | 0.11746 | 1.5601e-05 | 0
[13 empty] | 11:04 | 1.0034 | 0.91146 | 0.91784 |  | 11:04 | 1.0099 | 0.15298 | 2432.4541 | 11:04 | 1.4548 | 1.3373 | 0.11751 | 1.5607e-05 | 0
[13 empty] | 11:04 | 0.99062 | 0.91146 | 0.91784 |  | 11:04 | 0.99701 | 0.15298 | 2447.5038 | 11:04 | 1.4554 | 1.3378 | 0.11755 | 1.5614e-05 | 0
[13 empty] | 11:04 | 0.97811 | 0.91146 | 0.91784 |  | 11:04 | 0.98437 | 0.15298 | 2462.3625 | 11:04 | 1.456 | 1.3384 | 0.1176 | 1.562e-05 | 0
[13 empty] | 11:05 | 0.96585 | 0.91146 | 0.91784 |  | 11:05 | 0.97198 | 0.15298 | 2477.0493 | 11:05 | 1.4566 | 1.3389 | 0.11765 | 1.5626e-05 | 0
[13 empty] | 11:05 | 0.95385 | 0.91146 | 0.91784 |  | 11:05 | 0.95985 | 0.15298 | 2491.526 | 11:05 | 1.4571 | 1.3394 | 0.1177 | 1.5633e-05 | 0
[13 empty] | 11:05 | 0.94209 | 0.91146 | 0.91784 |  | 11:05 | 0.94797 | 0.15298 | 2505.85 | 11:05 | 1.4577 | 1.3399 | 0.11774 | 1.5639e-05 | 0
[13 empty] | 11:06 | 0.93058 | 0.91146 | 0.91784 |  | 11:06 | 0.93634 | 0.15298 | 2519.9829 | 11:06 | 1.4583 | 1.3405 | 0.11779 | 1.5645e-05 | 0
[13 empty] | 11:06 | 0.9193 | 0.91146 | 0.91784 |  | 11:06 | 0.92494 | 0.15298 | 2533.9249 | 11:06 | 1.4588 | 1.341 | 0.11783 | 1.5651e-05 | 0
[13 empty] | 11:06 | 0.90825 | 0.91146 | 0.91784 |  | 11:06 | 0.91377 | 0.15298 | 2547.7332 | 11:06 | 1.4594 | 1.3415 | 0.11788 | 1.5657e-05 | 0
[13 empty] | 11:06 | 0.89743 | 0.91146 | 0.91784 |  | 11:06 | 0.90284 | 0.15298 | 2561.3505 | 11:06 | 1.4599 | 1.342 | 0.11792 | 1.5662e-05 | 0
[13 empty] | 11:06 | 0.88683 | 0.91146 | 0.91784 |  | 11:06 | 0.89213 | 0.15298 | 2574.815 | 11:06 | 1.4605 | 1.3425 | 0.11796 | 1.5668e-05 | 0
[13 empty] | 11:07 | 0.87645 | 0.91146 | 0.91784 |  | 11:07 | 0.88164 | 0.15298 | 2588.1076 | 11:07 | 1.461 | 1.343 | 0.11801 | 1.5674e-05 | 0
[13 empty] | 11:07 | 0.86628 | 0.91146 | 0.91784 |  | 11:07 | 0.87137 | 0.15298 | 2601.2665 | 11:07 | 1.4615 | 1.3434 | 0.11805 | 1.568e-05 | 0
[13 empty] | 11:07 | 0.85633 | 0.91146 | 0.91784 |  | 11:07 | 0.8613 | 0.15298 | 2614.2536 | 11:07 | 1.462 | 1.3439 | 0.11809 | 1.5685e-05 | 0
[13 empty] | 11:08 | 0.84657 | 0.91146 | 0.91784 |  | 11:08 | 0.85145 | 0.15298 | 2627.1069 | 11:08 | 1.4625 | 1.3444 | 0.11813 | 1.5691e-05 | 0
[13 empty] | 11:08 | 0.83702 | 0.91146 | 0.91784 |  | 11:08 | 0.8418 | 0.15298 | 2639.8075 | 11:08 | 1.463 | 1.3448 | 0.11817 | 1.5696e-05 | 0
[13 empty] | 11:08 | 0.82766 | 0.91146 | 0.91784 |  | 11:08 | 0.83234 | 0.15298 | 2652.3553 | 11:08 | 1.4636 | 1.3453 | 0.11821 | 1.5701e-05 | 0
[13 empty] | 11:08 | 0.8185 | 0.91146 | 0.91784 |  | 11:08 | 0.82308 | 0.15298 | 2664.7694 | 11:08 | 1.464 | 1.3458 | 0.11825 | 1.5707e-05 | 0
[13 empty] | 11:08 | 0.80952 | 0.91146 | 0.91784 |  | 11:08 | 0.81401 | 0.15298 | 2677.0498 | 11:08 | 1.4645 | 1.3462 | 0.11829 | 1.5712e-05 | 0
[13 empty] | 11:09 | 0.80073 | 0.91146 | 0.91784 |  | 11:09 | 0.80512 | 0.15298 | 2689.1965 | 11:09 | 1.465 | 1.3467 | 0.11833 | 1.5717e-05 | 0
[13 empty] | 11:09 | 0.79211 | 0.91146 | 0.91784 |  | 11:09 | 0.79642 | 0.15298 | 2701.2095 | 11:09 | 1.4655 | 1.3471 | 0.11837 | 1.5722e-05 | 0
[13 empty] | 11:09 | 0.78368 | 0.91146 | 0.91784 |  | 11:09 | 0.7879 | 0.15298 | 2713.0888 | 11:09 | 1.466 | 1.3475 | 0.11841 | 1.5728e-05 | 0
[13 empty] | 11:10 | 0.77542 | 0.91146 | 0.91784 |  | 11:10 | 0.77955 | 0.15298 | 2724.8535 | 11:10 | 1.4664 | 1.348 | 0.11845 | 1.5732e-05 | 0
[13 empty] | 11:10 | 0.76733 | 0.91146 | 0.91784 |  | 11:10 | 0.77137 | 0.15298 | 2736.4846 | 11:10 | 1.4669 | 1.3484 | 0.11849 | 1.5737e-05 | 0
[13 empty] | 11:10 | 0.7594 | 0.91146 | 0.91784 |  | 11:10 | 0.76336 | 0.15298 | 2747.9819 | 11:10 | 1.4674 | 1.3488 | 0.11852 | 1.5742e-05 | 0
[13 empty] | 11:10 | 0.75164 | 0.91146 | 0.91784 |  | 11:10 | 0 | 0.15298 | 2753.7115 | 11:10 | 1.4678 | 1.3492 | 0.11856 | 1.5747e-05 | 0
[13 empty] | 11:10 | 0.74403 | 0.91146 | 0.91784 |  | 11:10 | 0 | 0.15298 | 2753.7115 | 11:10 | 1.4683 | 1.3497 | 0.11859 | 1.5752e-05 | 0
[13 empty] | 11:11 | 0.73658 | 0.91146 | 0.91784 |  | 11:11 | 0 | 0.15298 | 2753.7115 | 11:11 | 1.4687 | 1.3501 | 0.11863 | 1.5757e-05 | 0
[13 empty] | 11:11 | 0.72929 | 0.91146 | 0.91784 |  | 11:11 | 0 | 0.15298 | 2753.7115 | 11:11 | 1.4692 | 1.3505 | 0.11867 | 1.5762e-05 | 0
[13 empty] | 11:11 | 1.1629 | 0.91146 | 0.91784 |  | 11:11 | 0 | 0.15298 | 2753.7115 | 11:11 | 1.4699 | 1.3511 | 0.11872 | 1.5769e-05 | 0
[13 empty] | 11:12 | 1.1468 | 0.91146 | 0.91784 |  | 11:12 | 0 | 0.15298 | 2753.7115 | 11:12 | 1.4706 | 1.3518 | 0.11878 | 1.5777e-05 | 0
[13 empty] | 11:12 | 1.1311 | 0.91146 | 0.91784 |  | 11:12 | 0 | 0.15298 | 2753.7115 | 11:12 | 1.4712 | 1.3524 | 0.11884 | 1.5784e-05 | 0
[13 empty] | 11:12 | 1.1157 | 0.91146 | 0.91784 |  | 11:12 | 0 | 0.15298 | 2753.7115 | 11:12 | 1.4719 | 1.353 | 0.11889 | 1.5791e-05 | 0
[13 empty] | 11:12 | 1.1006 | 0.91146 | 0.91784 |  | 11:12 | 0 | 0.15298 | 2753.7115 | 11:12 | 1.4726 | 1.3536 | 0.11894 | 1.5798e-05 | 0
[13 empty] | 11:12 | 1.0859 | 0.91146 | 0.91784 |  | 11:12 | 0 | 0.15298 | 2753.7115 | 11:12 | 1.4732 | 1.3542 | 0.119 | 1.5805e-05 | 0
[13 empty] | 11:13 | 1.0714 | 0.91146 | 0.91784 |  | 11:13 | 0 | 0.15298 | 2753.7115 | 11:13 | 1.4739 | 1.3548 | 0.11905 | 1.5812e-05 | 0
[13 empty] | 11:13 | 1.0572 | 0.91146 | 0.91784 |  | 11:13 | 0 | 0.15298 | 2753.7115 | 11:13 | 1.4745 | 1.3554 | 0.1191 | 1.5819e-05 | 0
[13 empty] | 11:13 | 1.0434 | 0.91146 | 0.91784 |  | 11:13 | 0 | 0.15298 | 2753.7115 | 11:13 | 1.4752 | 1.356 | 0.11915 | 1.5826e-05 | 0
[13 empty] | 11:14 | 1.0298 | 0.91146 | 0.91784 |  | 11:14 | 0 | 0.15298 | 2753.7115 | 11:14 | 1.4758 | 1.3566 | 0.1192 | 1.5833e-05 | 0
[13 empty] | 11:14 | 1.0164 | 0.91146 | 0.91784 |  | 11:14 | 0 | 0.15298 | 2753.7115 | 11:14 | 1.4764 | 1.3571 | 0.11925 | 1.5839e-05 | 0
[13 empty] | 11:14 | 1.0034 | 0.91146 | 0.91784 |  | 11:14 | 0 | 0.15298 | 2753.7115 | 11:14 | 1.477 | 1.3577 | 0.1193 | 1.5846e-05 | 0
[13 empty] | 11:14 | 0.99062 | 0.91146 | 0.91784 |  | 11:14 | 0 | 0.15298 | 2753.7115 | 11:14 | 1.4776 | 1.3582 | 0.11935 | 1.5852e-05 | 0
[13 empty] | 11:14 | 0.97811 | 0.91146 | 0.91784 |  | 11:14 | 0 | 0.15298 | 2753.7115 | 11:14 | 1.4782 | 1.3588 | 0.1194 | 1.5859e-05 | 0
[13 empty] | 11:15 | 0.96585 | 0.91146 | 0.91784 |  | 11:15 | 0 | 0.15298 | 2753.7115 | 11:15 | 1.4788 | 1.3593 | 0.11944 | 1.5865e-05 | 0
[13 empty] | 11:15 | 0.95385 | 0.91146 | 0.91784 |  | 11:15 | 0 | 0.15298 | 2753.7115 | 11:15 | 1.4794 | 1.3599 | 0.11949 | 1.5871e-05 | 0
[13 empty] | 11:15 | 0.94209 | 0.91146 | 0.91784 |  | 11:15 | 0 | 0.15298 | 2753.7115 | 11:15 | 1.4799 | 1.3604 | 0.11954 | 1.5877e-05 | 0
[13 empty] | 11:16 | 0.93058 | 0.91146 | 0.91784 |  | 11:16 | 0 | 0.15298 | 2753.7115 | 11:16 | 1.4805 | 1.3609 | 0.11958 | 1.5883e-05 | 0
[13 empty] | 11:16 | 0.9193 | 0.91146 | 0.91784 |  | 11:16 | 0 | 0.15298 | 2753.7115 | 11:16 | 1.481 | 1.3614 | 0.11963 | 1.5889e-05 | 0
[13 empty] | 11:16 | 0.90825 | 0.91146 | 0.91784 |  | 11:16 | 0 | 0.15298 | 2753.7115 | 11:16 | 1.4816 | 1.3619 | 0.11967 | 1.5895e-05 | 0
[13 empty] | 11:16 | 0.89743 | 0.91146 | 0.91784 |  | 11:16 | 0 | 0.15298 | 2753.7115 | 11:16 | 1.4821 | 1.3624 | 0.11972 | 1.5901e-05 | 0
[13 empty] | 11:16 | 0.88683 | 0.91146 | 0.91784 |  | 11:16 | 0 | 0.15298 | 2753.7115 | 11:16 | 1.4827 | 1.3629 | 0.11976 | 1.5907e-05 | 0
[13 empty] | 11:17 | 0.87645 | 0.91146 | 0.91784 |  | 11:17 | 0 | 0.15298 | 2753.7115 | 11:17 | 1.4832 | 1.3634 | 0.1198 | 1.5912e-05 | 0
[13 empty] | 11:17 | 0.86628 | 0.91146 | 0.91784 |  | 11:17 | 0 | 0.15298 | 2753.7115 | 11:17 | 1.4837 | 1.3639 | 0.11984 | 1.5918e-05 | 0
[13 empty] | 11:17 | 0.85633 | 0.91146 | 0.91784 |  | 11:17 | 0 | 0.15298 | 2753.7115 | 11:17 | 1.4842 | 1.3643 | 0.11989 | 1.5924e-05 | 0
[13 empty] | 11:18 | 0.84657 | 0.91146 | 0.91784 |  | 11:18 | 0 | 0.15298 | 2753.7115 | 11:18 | 1.4848 | 1.3648 | 0.11993 | 1.5929e-05 | 0
[13 empty] | 11:18 | 0.83702 | 0.91146 | 0.91784 |  | 11:18 | 0 | 0.15298 | 2753.7115 | 11:18 | 1.4853 | 1.3653 | 0.11997 | 1.5935e-05 | 0
[13 empty] | 11:18 | 0.82766 | 0.91146 | 0.91784 |  | 11:18 | 0 | 0.15298 | 2753.7115 | 11:18 | 1.4858 | 1.3657 | 0.12001 | 1.594e-05 | 0
[13 empty] | 11:18 | 0.8185 | 0.91146 | 0.91784 |  | 11:18 | 0 | 0.15298 | 2753.7115 | 11:18 | 1.4863 | 1.3662 | 0.12005 | 1.5945e-05 | 0
[13 empty] | 11:18 | 0.80952 | 0.91146 | 0.91784 |  | 11:18 | 0 | 0.15298 | 2753.7115 | 11:18 | 1.4868 | 1.3667 | 0.12009 | 1.595e-05 | 0
[13 empty] | 11:19 | 0.80073 | 0.91146 | 0.91784 |  | 11:19 | 0 | 0.15298 | 2753.7115 | 11:19 | 1.4872 | 1.3671 | 0.12013 | 1.5956e-05 | 0
[13 empty] | 11:19 | 0.79211 | 0.91146 | 0.91784 |  | 11:19 | 0 | 0.15298 | 2753.7115 | 11:19 | 1.4877 | 1.3675 | 0.12017 | 1.5961e-05 | 0
[13 empty] | 11:19 | 0.78368 | 0.91146 | 0.91784 |  | 11:19 | 0 | 0.15298 | 2753.7115 | 11:19 | 1.4882 | 1.368 | 0.1202 | 1.5966e-05 | 0
[13 empty] | 11:20 | 0.77542 | 0.91146 | 0.91784 |  | 11:20 | 0 | 0.15298 | 2753.7115 | 11:20 | 1.4887 | 1.3684 | 0.12024 | 1.5971e-05 | 0
[13 empty] | 11:20 | 0.76733 | 0.91146 | 0.91784 |  | 11:20 | 0 | 0.15298 | 2753.7115 | 11:20 | 1.4891 | 1.3688 | 0.12028 | 1.5976e-05 | 0
[13 empty] | 11:20 | 0.7594 | 0.91146 | 0.91784 |  | 11:20 | 0 | 0.15298 | 2753.7115 | 11:20 | 1.4896 | 1.3693 | 0.12032 | 1.5981e-05 | 0
[13 empty] | 11:20 | 0.75164 | 0.91146 | 0.91784 |  | 11:20 | 0 | 0.15298 | 2753.7115 | 11:20 | 1.49 | 1.3697 | 0.12035 | 1.5986e-05 | 0
[13 empty] | 11:20 | 0.74403 | 0.91146 | 0.91784 |  | 11:20 | 0 | 0.15298 | 2753.7115 | 11:20 | 1.4905 | 1.3701 | 0.12039 | 1.599e-05 | 0
[13 empty] | 11:21 | 0.73658 | 0.91146 | 0.91784 |  | 11:21 | 0 | 0.15298 | 2753.7115 | 11:21 | 1.4909 | 1.3705 | 0.12043 | 1.5995e-05 | 0
[13 empty] | 11:21 | 0.72929 | 0.91146 | 0.91784 |  | 11:21 | 0 | 0.15298 | 2753.7115 | 11:21 | 1.4914 | 1.3709 | 0.12046 | 1.6e-05 | 0
[13 empty] | 11:21 | 1.1629 | 0.91146 | 0.91784 |  | 11:21 | 0 | 0.15298 | 2753.7115 | 11:21 | 1.4921 | 1.3715 | 0.12052 | 1.6008e-05 | 0
[13 empty] | 11:22 | 1.1468 | 0.91146 | 0.91784 |  | 11:22 | 0 | 0.15298 | 2753.7115 | 11:22 | 1.4928 | 1.3722 | 0.12058 | 1.6015e-05 | 0
[13 empty] | 11:22 | 1.1311 | 0.91146 | 0.91784 |  | 11:22 | 0 | 0.15298 | 2753.7115 | 11:22 | 1.4935 | 1.3728 | 0.12063 | 1.6022e-05 | 0
[13 empty] | 11:22 | 1.1157 | 0.91146 | 0.91784 |  | 11:22 | 0 | 0.15298 | 2753.7115 | 11:22 | 1.4941 | 1.3734 | 0.12069 | 1.603e-05 | 0
[13 empty] | 11:22 | 1.1006 | 0.91146 | 0.91784 |  | 11:22 | 0 | 0.15298 | 2753.7115 | 11:22 | 1.4948 | 1.374 | 0.12074 | 1.6037e-05 | 0
[13 empty] | 11:22 | 1.0859 | 0.91146 | 0.91784 |  | 11:22 | 0 | 0.15298 | 2753.7115 | 11:22 | 1.4955 | 1.3747 | 0.12079 | 1.6044e-05 | 0
[13 empty] | 11:23 | 1.0714 | 0.91146 | 0.91784 |  | 11:23 | 0 | 0.15298 | 2753.7115 | 11:23 | 1.4961 | 1.3753 | 0.12084 | 1.6051e-05 | 0
[13 empty] | 11:23 | 1.0572 | 0.91146 | 0.91784 |  | 11:23 | 0 | 0.15298 | 2753.7115 | 11:23 | 1.4968 | 1.3758 | 0.1209 | 1.6058e-05 | 0
[13 empty] | 11:23 | 1.0434 | 0.91146 | 0.91784 |  | 11:23 | 0 | 0.15298 | 2753.7115 | 11:23 | 1.4974 | 1.3764 | 0.12095 | 1.6064e-05 | 0
[13 empty] | 11:24 | 1.0298 | 0.91146 | 0.91784 |  | 11:24 | 0 | 0.15298 | 2753.7115 | 11:24 | 1.498 | 1.377 | 0.121 | 1.6071e-05 | 0
[13 empty] | 11:24 | 1.0164 | 0.91146 | 0.91784 |  | 11:24 | 0 | 0.15298 | 2753.7115 | 11:24 | 1.4986 | 1.3776 | 0.12105 | 1.6078e-05 | 0
[13 empty] | 11:24 | 1.0034 | 0.91146 | 0.91784 |  | 11:24 | 0 | 0.15298 | 2753.7115 | 11:24 | 1.4992 | 1.3781 | 0.1211 | 1.6084e-05 | 0
[13 empty] | 11:24 | 0.99062 | 0.91146 | 0.91784 |  | 11:24 | 0 | 0.15298 | 2753.7115 | 11:24 | 1.4998 | 1.3787 | 0.12114 | 1.6091e-05 | 0
[13 empty] | 11:24 | 0.97811 | 0.91146 | 0.91784 |  | 11:24 | 0 | 0.15298 | 2753.7115 | 11:24 | 1.5004 | 1.3792 | 0.12119 | 1.6097e-05 | 0
[13 empty] | 11:25 | 0.96585 | 0.91146 | 0.91784 |  | 11:25 | 0 | 0.15298 | 2753.7115 | 11:25 | 1.501 | 1.3798 | 0.12124 | 1.6103e-05 | 0
[13 empty] | 11:25 | 0.95385 | 0.91146 | 0.91784 |  | 11:25 | 0 | 0.15298 | 2753.7115 | 11:25 | 1.5016 | 1.3803 | 0.12129 | 1.6109e-05 | 0
[13 empty] | 11:25 | 0.94209 | 0.91146 | 0.91784 |  | 11:25 | 0 | 0.15298 | 2753.7115 | 11:25 | 1.5022 | 1.3808 | 0.12133 | 1.6116e-05 | 0
[13 empty] | 11:26 | 0.93058 | 0.91146 | 0.91784 |  | 11:26 | 0 | 0.15298 | 2753.7115 | 11:26 | 1.5027 | 1.3813 | 0.12138 | 1.6122e-05 | 0
[13 empty] | 11:26 | 0.9193 | 0.91146 | 0.91784 |  | 11:26 | 0 | 0.15298 | 2753.7115 | 11:26 | 1.5033 | 1.3818 | 0.12142 | 1.6128e-05 | 0
[13 empty] | 11:26 | 0.90825 | 0.91146 | 0.91784 |  | 11:26 | 0 | 0.15298 | 2753.7115 | 11:26 | 1.5038 | 1.3823 | 0.12147 | 1.6134e-05 | 0
[13 empty] | 11:26 | 0.89743 | 0.91146 | 0.91784 |  | 11:26 | 0 | 0.15298 | 2753.7115 | 11:26 | 1.5044 | 1.3829 | 0.12151 | 1.6139e-05 | 0
[13 empty] | 11:26 | 0.88683 | 0.91146 | 0.91784 |  | 11:26 | 0 | 0.15298 | 2753.7115 | 11:26 | 1.5049 | 1.3833 | 0.12155 | 1.6145e-05 | 0
[13 empty] | 11:27 | 0.87645 | 0.91146 | 0.91784 |  | 11:27 | 0 | 0.15298 | 2753.7115 | 11:27 | 1.5054 | 1.3838 | 0.1216 | 1.6151e-05 | 0
[13 empty] | 11:27 | 0.86628 | 0.91146 | 0.91784 |  | 11:27 | 0 | 0.15298 | 2753.7115 | 11:27 | 1.506 | 1.3843 | 0.12164 | 1.6156e-05 | 0
[13 empty] | 11:27 | 0.85633 | 0.91146 | 0.91784 |  | 11:27 | 0 | 0.15298 | 2753.7115 | 11:27 | 1.5065 | 1.3848 | 0.12168 | 1.6162e-05 | 0
[13 empty] | 11:28 | 0.84657 | 0.91146 | 0.91784 |  | 11:28 | 0 | 0.15298 | 2753.7115 | 11:28 | 1.507 | 1.3853 | 0.12172 | 1.6168e-05 | 0
[13 empty] | 11:28 | 0.83702 | 0.91146 | 0.91784 |  | 11:28 | 0 | 0.15298 | 2753.7115 | 11:28 | 1.5075 | 1.3857 | 0.12176 | 1.6173e-05 | 0
[13 empty] | 11:28 | 0.82766 | 0.91146 | 0.91784 |  | 11:28 | 0 | 0.15298 | 2753.7115 | 11:28 | 1.508 | 1.3862 | 0.12181 | 1.6178e-05 | 0
[13 empty] | 11:28 | 0.8185 | 0.91146 | 0.91784 |  | 11:28 | 0 | 0.15298 | 2753.7115 | 11:28 | 1.5085 | 1.3866 | 0.12185 | 1.6184e-05 | 0
[13 empty] | 11:28 | 0.80952 | 0.91146 | 0.91784 |  | 11:28 | 0 | 0.15298 | 2753.7115 | 11:28 | 1.509 | 1.3871 | 0.12188 | 1.6189e-05 | 0
[13 empty] | 11:29 | 0.80073 | 0.91146 | 0.91784 |  | 11:29 | 0 | 0.15298 | 2753.7115 | 11:29 | 1.5095 | 1.3875 | 0.12192 | 1.6194e-05 | 0
[13 empty] | 11:29 | 0.79211 | 0.91146 | 0.91784 |  | 11:29 | 0 | 0.15298 | 2753.7115 | 11:29 | 1.5099 | 1.388 | 0.12196 | 1.6199e-05 | 0
[13 empty] | 11:29 | 0.78368 | 0.91146 | 0.91784 |  | 11:29 | 0 | 0.15298 | 2753.7115 | 11:29 | 1.5104 | 1.3884 | 0.122 | 1.6204e-05 | 0
[13 empty] | 11:30 | 0.77542 | 0.91146 | 0.91784 |  | 11:30 | 0 | 0.15298 | 2753.7115 | 11:30 | 1.5109 | 1.3888 | 0.12204 | 1.6209e-05 | 0
[13 empty] | 11:30 | 0.76733 | 0.91146 | 0.91784 |  | 11:30 | 0 | 0.15298 | 2753.7115 | 11:30 | 1.5114 | 1.3893 | 0.12208 | 1.6214e-05 | 0
[13 empty] | 11:30 | 0.7594 | 0.91146 | 0.91784 |  | 11:30 | 0 | 0.15298 | 2753.7115 | 11:30 | 1.5118 | 1.3897 | 0.12211 | 1.6219e-05 | 0
[13 empty] | 11:30 | 0.75164 | 0.91146 | 0.91784 |  | 11:30 | 0 | 0.15298 | 2753.7115 | 11:30 | 1.5123 | 1.3901 | 0.12215 | 1.6224e-05 | 0
[13 empty] | 11:30 | 0.74403 | 0.91146 | 0.91784 |  | 11:30 | 0 | 0.15298 | 2753.7115 | 11:30 | 1.5127 | 1.3905 | 0.12219 | 1.6229e-05 | 0
[13 empty] | 11:31 | 0.73658 | 0.91146 | 0.91784 |  | 11:31 | 0 | 0.15298 | 2753.7115 | 11:31 | 1.5132 | 1.3909 | 0.12222 | 1.6234e-05 | 0
[13 empty] | 11:31 | 0.72929 | 0.91146 | 0.91784 |  | 11:31 | 0 | 0.15298 | 2753.7115 | 11:31 | 1.5136 | 1.3913 | 0.12226 | 1.6239e-05 | 0
[13 empty] | 11:31 | 1.1629 | 0.91146 | 0.91784 |  | 11:31 | 0 | 0.15298 | 2753.7115 | 11:31 | 1.5143 | 1.392 | 0.12232 | 1.6246e-05 | 0
[13 empty] | 11:32 | 1.1468 | 0.91146 | 0.91784 |  | 11:32 | 0 | 0.15298 | 2753.7115 | 11:32 | 1.515 | 1.3926 | 0.12237 | 1.6253e-05 | 0
[13 empty] | 11:32 | 1.1311 | 0.91146 | 0.91784 |  | 11:32 | 0 | 0.15298 | 2753.7115 | 11:32 | 1.5157 | 1.3933 | 0.12243 | 1.6261e-05 | 0
[13 empty] | 11:32 | 1.1157 | 0.91146 | 0.91784 |  | 11:32 | 0 | 0.15298 | 2753.7115 | 11:32 | 1.5164 | 1.3939 | 0.12248 | 1.6268e-05 | 0
[13 empty] | 11:32 | 1.1006 | 0.91146 | 0.91784 |  | 11:32 | 0 | 0.15298 | 2753.7115 | 11:32 | 1.517 | 1.3945 | 0.12253 | 1.6275e-05 | 0
[13 empty] | 11:32 | 1.0859 | 0.91146 | 0.91784 |  | 11:32 | 0 | 0.15298 | 2753.7115 | 11:32 | 1.5177 | 1.3951 | 0.12259 | 1.6282e-05 | 0
[13 empty] | 11:33 | 1.0714 | 0.91146 | 0.91784 |  | 11:33 | 0 | 0.15298 | 2753.7115 | 11:33 | 1.5183 | 1.3957 | 0.12264 | 1.6289e-05 | 0
[13 empty] | 11:33 | 1.0572 | 0.91146 | 0.91784 |  | 11:33 | 0 | 0.15298 | 2753.7115 | 11:33 | 1.519 | 1.3963 | 0.12269 | 1.6296e-05 | 0
[13 empty] | 11:33 | 1.0434 | 0.91146 | 0.91784 |  | 11:33 | 0 | 0.15298 | 2753.7115 | 11:33 | 1.5196 | 1.3969 | 0.12274 | 1.6303e-05 | 0
[13 empty] | 11:34 | 1.0298 | 0.91146 | 0.91784 |  | 11:34 | 0 | 0.15298 | 2753.7115 | 11:34 | 1.5202 | 1.3974 | 0.12279 | 1.631e-05 | 0
[13 empty] | 11:34 | 1.0164 | 0.91146 | 0.91784 |  | 11:34 | 0 | 0.15298 | 2753.7115 | 11:34 | 1.5209 | 1.398 | 0.12284 | 1.6316e-05 | 0
[13 empty] | 11:34 | 1.0034 | 0.91146 | 0.91784 |  | 11:34 | 0 | 0.15298 | 2753.7115 | 11:34 | 1.5215 | 1.3986 | 0.12289 | 1.6323e-05 | 0
[13 empty] | 11:34 | 0.99062 | 0.91146 | 0.91784 |  | 11:34 | 0 | 0.15298 | 2753.7115 | 11:34 | 1.5221 | 1.3991 | 0.12294 | 1.6329e-05 | 0
[13 empty] | 11:34 | 0.97811 | 0.91146 | 0.91784 |  | 11:34 | 0 | 0.15298 | 2753.7115 | 11:34 | 1.5226 | 1.3996 | 0.12299 | 1.6336e-05 | 0
[13 empty] | 11:35 | 0.96585 | 0.91146 | 0.91784 |  | 11:35 | 0 | 0.15298 | 2753.7115 | 11:35 | 1.5232 | 1.4002 | 0.12304 | 1.6342e-05 | 0
[13 empty] | 11:35 | 0.95385 | 0.91146 | 0.91784 |  | 11:35 | 0 | 0.15298 | 2753.7115 | 11:35 | 1.5238 | 1.4007 | 0.12308 | 1.6348e-05 | 0
[13 empty] | 11:35 | 0.94209 | 0.91146 | 0.91784 |  | 11:35 | 0 | 0.15298 | 2753.7115 | 11:35 | 1.5244 | 1.4012 | 0.12313 | 1.6354e-05 | 0
[13 empty] | 11:36 | 0.93058 | 0.91146 | 0.91784 |  | 11:36 | 0 | 0.15298 | 2753.7115 | 11:36 | 1.525 | 1.4018 | 0.12317 | 1.636e-05 | 0
[13 empty] | 11:36 | 0.9193 | 0.91146 | 0.91784 |  | 11:36 | 0 | 0.15298 | 2753.7115 | 11:36 | 1.5255 | 1.4023 | 0.12322 | 1.6366e-05 | 0
[13 empty] | 11:36 | 0.90825 | 0.91146 | 0.91784 |  | 11:36 | 0 | 0.15298 | 2753.7115 | 11:36 | 1.5261 | 1.4028 | 0.12326 | 1.6372e-05 | 0
[13 empty] | 11:36 | 0.89743 | 0.91146 | 0.91784 |  | 11:36 | 0 | 0.15298 | 2753.7115 | 11:36 | 1.5266 | 1.4033 | 0.12331 | 1.6378e-05 | 0
[13 empty] | 11:36 | 0.88683 | 0.91146 | 0.91784 |  | 11:36 | 0 | 0.15298 | 2753.7115 | 11:36 | 1.5271 | 1.4038 | 0.12335 | 1.6384e-05 | 0
[13 empty] | 11:37 | 0.87645 | 0.91146 | 0.91784 |  | 11:37 | 0 | 0.15298 | 2753.7115 | 11:37 | 1.5277 | 1.4043 | 0.12339 | 1.6389e-05 | 0
[13 empty] | 11:37 | 0.86628 | 0.91146 | 0.91784 |  | 11:37 | 0 | 0.15298 | 2753.7115 | 11:37 | 1.5282 | 1.4047 | 0.12344 | 1.6395e-05 | 0
[13 empty] | 11:37 | 0.85633 | 0.91146 | 0.91784 |  | 11:37 | 0 | 0.15298 | 2753.7115 | 11:37 | 1.5287 | 1.4052 | 0.12348 | 1.6401e-05 | 0
[13 empty] | 11:38 | 0.84657 | 0.91146 | 0.91784 |  | 11:38 | 0 | 0.15298 | 2753.7115 | 11:38 | 1.5292 | 1.4057 | 0.12352 | 1.6406e-05 | 0
[13 empty] | 11:38 | 0.83702 | 0.91146 | 0.91784 |  | 11:38 | 0 | 0.15298 | 2753.7115 | 11:38 | 1.5297 | 1.4062 | 0.12356 | 1.6411e-05 | 0
[13 empty] | 11:38 | 0.82766 | 0.91146 | 0.91784 |  | 11:38 | 0 | 0.15298 | 2753.7115 | 11:38 | 1.5302 | 1.4066 | 0.1236 | 1.6417e-05 | 0
[13 empty] | 11:38 | 0.8185 | 0.91146 | 0.91784 |  | 11:38 | 0 | 0.15298 | 2753.7115 | 11:38 | 1.5307 | 1.4071 | 0.12364 | 1.6422e-05 | 0
[13 empty] | 11:39 | 0.80952 | 0.91146 | 0.91784 |  | 11:39 | 0 | 0.15298 | 2753.7115 | 11:39 | 1.5312 | 1.4075 | 0.12368 | 1.6427e-05 | 0
[13 empty] | 11:39 | 0.80073 | 0.91146 | 0.91784 |  | 11:39 | 0 | 0.15298 | 2753.7115 | 11:39 | 1.5317 | 1.408 | 0.12372 | 1.6433e-05 | 0
[13 empty] | 11:39 | 0.79211 | 0.91146 | 0.91784 |  | 11:39 | 0 | 0.15298 | 2753.7115 | 11:39 | 1.5322 | 1.4084 | 0.12376 | 1.6438e-05 | 0
[13 empty] | 11:39 | 0.78368 | 0.91146 | 0.91784 |  | 11:39 | 0 | 0.15298 | 2753.7115 | 11:39 | 1.5327 | 1.4088 | 0.1238 | 1.6443e-05 | 0
[13 empty] | 11:40 | 0.77542 | 0.91146 | 0.91784 |  | 11:40 | 0 | 0.15298 | 2753.7115 | 11:40 | 1.5331 | 1.4093 | 0.12383 | 1.6448e-05 | 0
[13 empty] | 11:40 | 0.76733 | 0.91146 | 0.91784 |  | 11:40 | 0 | 0.15298 | 2753.7115 | 11:40 | 1.5336 | 1.4097 | 0.12387 | 1.6453e-05 | 0
[13 empty] | 11:40 | 0.7594 | 0.91146 | 0.91784 |  | 11:40 | 0 | 0.15298 | 2753.7115 | 11:40 | 1.534 | 1.4101 | 0.12391 | 1.6458e-05 | 0
[13 empty] | 11:40 | 0.75164 | 0.91146 | 0.91784 |  | 11:40 | 0 | 0.15298 | 2753.7115 | 11:40 | 1.5345 | 1.4105 | 0.12395 | 1.6463e-05 | 0
[13 empty] | 11:41 | 0.74403 | 0.91146 | 0.91784 |  | 11:41 | 0 | 0.15298 | 2753.7115 | 11:41 | 1.5349 | 1.4109 | 0.12398 | 1.6468e-05 | 0
[13 empty] | 11:41 | 0.73658 | 0.91146 | 0.91784 |  | 11:41 | 0 | 0.15298 | 2753.7115 | 11:41 | 1.5354 | 1.4114 | 0.12402 | 1.6472e-05 | 0
[13 empty] | 11:41 | 0.72929 | 0.91146 | 0.91784 |  | 11:41 | 0 | 0.15298 | 2753.7115 | 11:41 | 1.5358 | 1.4118 | 0.12405 | 1.6477e-05 | 0
[13 empty] | 11:41 | 1.1629 | 0.91146 | 0.91784 |  | 11:41 | 0 | 0.15298 | 2753.7115 | 11:41 | 1.5365 | 1.4124 | 0.12411 | 1.6485e-05 | 0
[13 empty] | 11:42 | 1.1468 | 0.91146 | 0.91784 |  | 11:42 | 0 | 0.15298 | 2753.7115 | 11:42 | 1.5372 | 1.413 | 0.12417 | 1.6492e-05 | 0
[13 empty] | 11:42 | 1.1311 | 0.91146 | 0.91784 |  | 11:42 | 0 | 0.15298 | 2753.7115 | 11:42 | 1.5379 | 1.4137 | 0.12422 | 1.6499e-05 | 0
[13 empty] | 11:42 | 1.1157 | 0.91146 | 0.91784 |  | 11:42 | 0 | 0.15298 | 2753.7115 | 11:42 | 1.5386 | 1.4143 | 0.12428 | 1.6507e-05 | 0
[13 empty] | 11:42 | 1.1006 | 0.91146 | 0.91784 |  | 11:42 | 0 | 0.15298 | 2753.7115 | 11:42 | 1.5393 | 1.4149 | 0.12433 | 1.6514e-05 | 0
[13 empty] | 11:43 | 1.0859 | 0.91146 | 0.91784 |  | 11:43 | 0 | 0.15298 | 2753.7115 | 11:43 | 1.5399 | 1.4155 | 0.12438 | 1.6521e-05 | 0
[13 empty] | 11:43 | 1.0714 | 0.91146 | 0.91784 |  | 11:43 | 0 | 0.15298 | 2753.7115 | 11:43 | 1.5406 | 1.4161 | 0.12443 | 1.6528e-05 | 0
[13 empty] | 11:43 | 1.0572 | 0.91146 | 0.91784 |  | 11:43 | 0 | 0.15298 | 2753.7115 | 11:43 | 1.5412 | 1.4167 | 0.12449 | 1.6535e-05 | 0
[13 empty] | 11:43 | 1.0434 | 0.91146 | 0.91784 |  | 11:43 | 0 | 0.15298 | 2753.7115 | 11:43 | 1.5418 | 1.4173 | 0.12454 | 1.6541e-05 | 0
[13 empty] | 11:44 | 1.0298 | 0.91146 | 0.91784 |  | 11:44 | 0 | 0.15298 | 2753.7115 | 11:44 | 1.5425 | 1.4179 | 0.12459 | 1.6548e-05 | 0
[13 empty] | 11:44 | 1.0164 | 0.91146 | 0.91784 |  | 11:44 | 0 | 0.15298 | 2753.7115 | 11:44 | 1.5431 | 1.4184 | 0.12464 | 1.6555e-05 | 0
[13 empty] | 11:44 | 1.0034 | 0.91146 | 0.91784 |  | 11:44 | 0 | 0.15298 | 2753.7115 | 11:44 | 1.5437 | 1.419 | 0.12469 | 1.6561e-05 | 0
[13 empty] | 11:44 | 0.99062 | 0.91146 | 0.91784 |  | 11:44 | 0 | 0.15298 | 2753.7115 | 11:44 | 1.5443 | 1.4195 | 0.12473 | 1.6568e-05 | 0
[13 empty] | 11:44 | 0.97811 | 0.91146 | 0.91784 |  | 11:44 | 0 | 0.15298 | 2753.7115 | 11:44 | 1.5449 | 1.4201 | 0.12478 | 1.6574e-05 | 0
[13 empty] | 11:45 | 0.96585 | 0.91146 | 0.91784 |  | 11:45 | 0 | 0.15298 | 2753.7115 | 11:45 | 1.5455 | 1.4206 | 0.12483 | 1.658e-05 | 0
[13 empty] | 11:45 | 0.95385 | 0.91146 | 0.91784 |  | 11:45 | 0 | 0.15298 | 2753.7115 | 11:45 | 1.546 | 1.4211 | 0.12488 | 1.6587e-05 | 0
[13 empty] | 11:45 | 0.94209 | 0.91146 | 0.91784 |  | 11:45 | 0 | 0.15298 | 2753.7115 | 11:45 | 1.5466 | 1.4217 | 0.12492 | 1.6593e-05 | 0
[13 empty] | 11:46 | 0.93058 | 0.91146 | 0.91784 |  | 11:46 | 0 | 0.15298 | 2753.7115 | 11:46 | 1.5472 | 1.4222 | 0.12497 | 1.6599e-05 | 0
[13 empty] | 11:46 | 0.9193 | 0.91146 | 0.91784 |  | 11:46 | 0 | 0.15298 | 2753.7115 | 11:46 | 1.5477 | 1.4227 | 0.12501 | 1.6605e-05 | 0
[13 empty] | 11:46 | 0.90825 | 0.91146 | 0.91784 |  | 11:46 | 0 | 0.15298 | 2753.7115 | 11:46 | 1.5483 | 1.4232 | 0.12506 | 1.661e-05 | 0
[13 empty] | 11:46 | 0.89743 | 0.91146 | 0.91784 |  | 11:46 | 0 | 0.15298 | 2753.7115 | 11:46 | 1.5488 | 1.4237 | 0.1251 | 1.6616e-05 | 0
[13 empty] | 11:46 | 0.88683 | 0.91146 | 0.91784 |  | 11:46 | 0 | 0.15298 | 2753.7115 | 11:46 | 1.5494 | 1.4242 | 0.12515 | 1.6622e-05 | 0
[13 empty] | 11:47 | 0.87645 | 0.91146 | 0.91784 |  | 11:47 | 0 | 0.15298 | 2753.7115 | 11:47 | 1.5499 | 1.4247 | 0.12519 | 1.6628e-05 | 0
[13 empty] | 11:47 | 0.86628 | 0.91146 | 0.91784 |  | 11:47 | 0 | 0.15298 | 2753.7115 | 11:47 | 1.5504 | 1.4252 | 0.12523 | 1.6633e-05 | 0
[13 empty] | 11:47 | 0.85633 | 0.91146 | 0.91784 |  | 11:47 | 0 | 0.15298 | 2753.7115 | 11:47 | 1.5509 | 1.4257 | 0.12527 | 1.6639e-05 | 0
[13 empty] | 11:48 | 0.84657 | 0.91146 | 0.91784 |  | 11:48 | 0 | 0.15298 | 2753.7115 | 11:48 | 1.5514 | 1.4261 | 0.12531 | 1.6644e-05 | 0
[13 empty] | 11:48 | 0.83702 | 0.91146 | 0.91784 |  | 11:48 | 0 | 0.15298 | 2753.7115 | 11:48 | 1.552 | 1.4266 | 0.12536 | 1.665e-05 | 0
[13 empty] | 11:48 | 0.82766 | 0.91146 | 0.91784 |  | 11:48 | 0 | 0.15298 | 2753.7115 | 11:48 | 1.5525 | 1.427 | 0.1254 | 1.6655e-05 | 0
[13 empty] | 11:48 | 0.8185 | 0.91146 | 0.91784 |  | 11:48 | 0 | 0.15298 | 2753.7115 | 11:48 | 1.553 | 1.4275 | 0.12544 | 1.6661e-05 | 0
[13 empty] | 11:48 | 0.80952 | 0.91146 | 0.91784 |  | 11:48 | 0 | 0.15298 | 2753.7115 | 11:48 | 1.5534 | 1.4279 | 0.12548 | 1.6666e-05 | 0
[13 empty] | 11:49 | 0.80073 | 0.91146 | 0.91784 |  | 11:49 | 0 | 0.15298 | 2753.7115 | 11:49 | 1.5539 | 1.4284 | 0.12551 | 1.6671e-05 | 0
[13 empty] | 11:49 | 0.79211 | 0.91146 | 0.91784 |  | 11:49 | 0 | 0.15298 | 2753.7115 | 11:49 | 1.5544 | 1.4288 | 0.12555 | 1.6676e-05 | 0
[13 empty] | 11:49 | 0.78368 | 0.91146 | 0.91784 |  | 11:49 | 0 | 0.15298 | 2753.7115 | 11:49 | 1.5549 | 1.4293 | 0.12559 | 1.6681e-05 | 0
[13 empty] | 11:50 | 0.77542 | 0.91146 | 0.91784 |  | 11:50 | 0 | 0.15298 | 2753.7115 | 11:50 | 1.5553 | 1.4297 | 0.12563 | 1.6686e-05 | 0
[13 empty] | 11:50 | 0.76733 | 0.91146 | 0.91784 |  | 11:50 | 0 | 0.15298 | 2753.7115 | 11:50 | 1.5558 | 1.4301 | 0.12567 | 1.6691e-05 | 0
[13 empty] | 11:50 | 0.7594 | 0.91146 | 0.91784 |  | 11:50 | 0 | 0.15298 | 2753.7115 | 11:50 | 1.5563 | 1.4306 | 0.1257 | 1.6696e-05 | 0
[13 empty] | 11:50 | 0.75164 | 0.91146 | 0.91784 |  | 11:50 | 0 | 0.15298 | 2753.7115 | 11:50 | 1.5567 | 1.431 | 0.12574 | 1.6701e-05 | 0
[13 empty] | 11:50 | 0.74403 | 0.91146 | 0.91784 |  | 11:50 | 0 | 0.15298 | 2753.7115 | 11:50 | 1.5572 | 1.4314 | 0.12578 | 1.6706e-05 | 0
[13 empty] | 11:51 | 0.73658 | 0.91146 | 0.91784 |  | 11:51 | 0 | 0.15298 | 2753.7115 | 11:51 | 1.5576 | 1.4318 | 0.12581 | 1.6711e-05 | 0
[13 empty] | 11:51 | 0.72929 | 0.91146 | 0.91784 |  | 11:51 | 0 | 0.15298 | 2753.7115 | 11:51 | 1.5581 | 1.4322 | 0.12585 | 1.6715e-05 | 0
[13 empty] | 11:51 | 1.1629 | 0.91146 | 0.91784 |  | 11:51 | 0 | 0.15298 | 2753.7115 | 11:51 | 1.5588 | 1.4329 | 0.12591 | 1.6723e-05 | 0
[13 empty] | 11:52 | 1.1468 | 0.91146 | 0.91784 |  | 11:52 | 0 | 0.15298 | 2753.7115 | 11:52 | 1.5595 | 1.4335 | 0.12596 | 1.6731e-05 | 0
[13 empty] | 11:52 | 1.1311 | 0.91146 | 0.91784 |  | 11:52 | 0 | 0.15298 | 2753.7115 | 11:52 | 1.5601 | 1.4341 | 0.12602 | 1.6738e-05 | 0
[13 empty] | 11:52 | 1.1157 | 0.91146 | 0.91784 |  | 11:52 | 0 | 0.15298 | 2753.7115 | 11:52 | 1.5608 | 1.4347 | 0.12607 | 1.6745e-05 | 0
[13 empty] | 11:52 | 1.1006 | 0.91146 | 0.91784 |  | 11:52 | 0 | 0.15298 | 2753.7115 | 11:52 | 1.5615 | 1.4354 | 0.12613 | 1.6752e-05 | 0
[13 empty] | 11:52 | 1.0859 | 0.91146 | 0.91784 |  | 11:52 | 0 | 0.15298 | 2753.7115 | 11:52 | 1.5622 | 1.436 | 0.12618 | 1.6759e-05 | 0
[13 empty] | 11:53 | 1.0714 | 0.91146 | 0.91784 |  | 11:53 | 0 | 0.15298 | 2753.7115 | 11:53 | 1.5628 | 1.4366 | 0.12623 | 1.6766e-05 | 0
[13 empty] | 11:53 | 1.0572 | 0.91146 | 0.91784 |  | 11:53 | 0 | 0.15298 | 2753.7115 | 11:53 | 1.5634 | 1.4372 | 0.12628 | 1.6773e-05 | 0
[13 empty] | 11:53 | 1.0434 | 0.91146 | 0.91784 |  | 11:53 | 0 | 0.15298 | 2753.7115 | 11:53 | 1.5641 | 1.4377 | 0.12633 | 1.678e-05 | 0
[13 empty] | 11:54 | 1.0298 | 0.91146 | 0.91784 |  | 11:54 | 0 | 0.15298 | 2753.7115 | 11:54 | 1.5647 | 1.4383 | 0.12638 | 1.6787e-05 | 0
[13 empty] | 11:54 | 1.0164 | 0.91146 | 0.91784 |  | 11:54 | 0 | 0.15298 | 2753.7115 | 11:54 | 1.5653 | 1.4389 | 0.12643 | 1.6793e-05 | 0
[13 empty] | 11:54 | 1.0034 | 0.91146 | 0.91784 |  | 11:54 | 0 | 0.15298 | 2753.7115 | 11:54 | 1.5659 | 1.4394 | 0.12648 | 1.68e-05 | 0
[13 empty] | 11:54 | 0.99062 | 0.91146 | 0.91784 |  | 11:54 | 0 | 0.15298 | 2753.7115 | 11:54 | 1.5665 | 1.44 | 0.12653 | 1.6806e-05 | 0
[13 empty] | 11:54 | 0.97811 | 0.91146 | 0.91784 |  | 11:54 | 0 | 0.15298 | 2753.7115 | 11:54 | 1.5671 | 1.4405 | 0.12658 | 1.6812e-05 | 0
[13 empty] | 11:55 | 0.96585 | 0.91146 | 0.91784 |  | 11:55 | 0 | 0.15298 | 2753.7115 | 11:55 | 1.5677 | 1.441 | 0.12663 | 1.6819e-05 | 0
[13 empty] | 11:55 | 0.95385 | 0.91146 | 0.91784 |  | 11:55 | 0 | 0.15298 | 2753.7115 | 11:55 | 1.5683 | 1.4416 | 0.12667 | 1.6825e-05 | 0
[13 empty] | 11:55 | 0.94209 | 0.91146 | 0.91784 |  | 11:55 | 0 | 0.15298 | 2753.7115 | 11:55 | 1.5689 | 1.4421 | 0.12672 | 1.6831e-05 | 0
[13 empty] | 11:56 | 0.93058 | 0.91146 | 0.91784 |  | 11:56 | 0 | 0.15298 | 2753.7115 | 11:56 | 1.5694 | 1.4426 | 0.12676 | 1.6837e-05 | 0
[13 empty] | 11:56 | 0.9193 | 0.91146 | 0.91784 |  | 11:56 | 0 | 0.15298 | 2753.7115 | 11:56 | 1.57 | 1.4431 | 0.12681 | 1.6843e-05 | 0
[13 empty] | 11:56 | 0.90825 | 0.91146 | 0.91784 |  | 11:56 | 0 | 0.15298 | 2753.7115 | 11:56 | 1.5705 | 1.4436 | 0.12685 | 1.6849e-05 | 0
[13 empty] | 11:56 | 0.89743 | 0.91146 | 0.91784 |  | 11:56 | 0 | 0.15298 | 2753.7115 | 11:56 | 1.5711 | 1.4441 | 0.1269 | 1.6855e-05 | 0
[13 empty] | 11:56 | 0.88683 | 0.91146 | 0.91784 |  | 11:56 | 0 | 0.15298 | 2753.7115 | 11:56 | 1.5716 | 1.4446 | 0.12694 | 1.6861e-05 | 0
[13 empty] | 11:57 | 0.87645 | 0.91146 | 0.91784 |  | 11:57 | 0 | 0.15298 | 2753.7115 | 11:57 | 1.5721 | 1.4451 | 0.12698 | 1.6866e-05 | 0
[13 empty] | 11:57 | 0.86628 | 0.91146 | 0.91784 |  | 11:57 | 0 | 0.15298 | 2753.7115 | 11:57 | 1.5727 | 1.4456 | 0.12703 | 1.6872e-05 | 0
[13 empty] | 11:57 | 0.85633 | 0.91146 | 0.91784 |  | 11:57 | 0 | 0.15298 | 2753.7115 | 11:57 | 1.5732 | 1.4461 | 0.12707 | 1.6877e-05 | 0
[13 empty] | 11:58 | 0.84657 | 0.91146 | 0.91784 |  | 11:58 | 0 | 0.15298 | 2753.7115 | 11:58 | 1.5737 | 1.4465 | 0.12711 | 1.6883e-05 | 0
[13 empty] | 11:58 | 0.83702 | 0.91146 | 0.91784 |  | 11:58 | 0 | 0.15298 | 2753.7115 | 11:58 | 1.5742 | 1.447 | 0.12715 | 1.6888e-05 | 0
[13 empty] | 11:58 | 0.82766 | 0.91146 | 0.91784 |  | 11:58 | 0 | 0.15298 | 2753.7115 | 11:58 | 1.5747 | 1.4475 | 0.12719 | 1.6894e-05 | 0
[13 empty] | 11:58 | 0.8185 | 0.91146 | 0.91784 |  | 11:58 | 0 | 0.15298 | 2753.7115 | 11:58 | 1.5752 | 1.4479 | 0.12723 | 1.6899e-05 | 0
[13 empty] | 11:58 | 0.80952 | 0.91146 | 0.91784 |  | 11:58 | 0 | 0.15298 | 2753.7115 | 11:58 | 1.5757 | 1.4484 | 0.12727 | 1.6904e-05 | 0
[13 empty] | 11:59 | 0.80073 | 0.91146 | 0.91784 |  | 11:59 | 0 | 0.15298 | 2753.7115 | 11:59 | 1.5762 | 1.4488 | 0.12731 | 1.691e-05 | 0
[13 empty] | 11:59 | 0.79211 | 0.91146 | 0.91784 |  | 11:59 | 0 | 0.15298 | 2753.7115 | 11:59 | 1.5766 | 1.4493 | 0.12735 | 1.6915e-05 | 0
[13 empty] | 11:59 | 0.78368 | 0.91146 | 0.91784 |  | 11:59 | 0 | 0.15298 | 2753.7115 | 11:59 | 1.5771 | 1.4497 | 0.12739 | 1.692e-05 | 0
[13 empty] | 12:00 | 0.77542 | 0.91146 | 0.91784 |  | 12:00 | 0 | 0.15298 | 2753.7115 | 12:00 | 1.5776 | 1.4501 | 0.12742 | 1.6925e-05 | 0
[13 empty] | 12:00 | 0.76733 | 0.91146 | 0.91784 |  | 12:00 | 0 | 0.15298 | 2753.7115 | 12:00 | 1.578 | 1.4506 | 0.12746 | 1.693e-05 | 0
[13 empty] | 12:00 | 0.7594 | 0.91146 | 0.91784 |  | 12:00 | 0 | 0.15298 | 2753.7115 | 12:00 | 1.5785 | 1.451 | 0.1275 | 1.6935e-05 | 0
[13 empty] | 12:00 | 0.75164 | 0.91146 | 0.91784 |  | 12:00 | 0.75552 | 0.15298 | 2759.3838 | 12:00 | 1.579 | 1.4514 | 0.12754 | 1.694e-05 | 0
[13 empty] | 12:00 | 0.74403 | 0.91146 | 0.91784 |  | 12:00 | 0.74784 | 0.15298 | 2770.652 | 12:00 | 1.5794 | 1.4518 | 0.12757 | 1.6944e-05 | 0
[13 empty] | 12:01 | 0.73658 | 0.91146 | 0.91784 |  | 12:01 | 0.74031 | 0.15298 | 2781.8055 | 12:01 | 1.5799 | 1.4522 | 0.12761 | 1.6949e-05 | 0
[13 empty] | 12:01 | 0.72929 | 0.91146 | 0.91784 |  | 12:01 | 0.73294 | 0.15298 | 2792.8636 | 12:01 | 1.5803 | 1.4526 | 0.12764 | 1.6954e-05 | 0
[13 empty] | 12:01 | 1.1629 | 0.91146 | 0.91784 |  | 12:01 | 0.94609 | 0.15298 | 2805.4496 | 12:01 | 1.581 | 1.4533 | 0.1277 | 1.6961e-05 | 0
[13 empty] | 12:02 | 1.1468 | 0.91146 | 0.91784 |  | 12:02 | 1.1549 | 0.15298 | 2821.2059 | 12:02 | 1.5817 | 1.4539 | 0.12776 | 1.6969e-05 | 0
[13 empty] | 12:02 | 1.1311 | 0.91146 | 0.91784 |  | 12:02 | 1.139 | 0.15298 | 2838.4138 | 12:02 | 1.5824 | 1.4545 | 0.12781 | 1.6976e-05 | 0
[13 empty] | 12:02 | 1.1157 | 0.91146 | 0.91784 |  | 12:02 | 1.1234 | 0.15298 | 2855.3924 | 12:02 | 1.5831 | 1.4552 | 0.12787 | 1.6984e-05 | 0
[13 empty] | 12:02 | 1.1006 | 0.91146 | 0.91784 |  | 12:02 | 1.1082 | 0.15298 | 2872.1228 | 12:02 | 1.5837 | 1.4558 | 0.12792 | 1.6991e-05 | 0
[13 empty] | 12:02 | 1.0859 | 0.91146 | 0.91784 |  | 12:02 | 1.0933 | 0.15298 | 2888.6431 | 12:02 | 1.5844 | 1.4564 | 0.12797 | 1.6998e-05 | 0
[13 empty] | 12:03 | 1.0714 | 0.91146 | 0.91784 |  | 12:03 | 1.0786 | 0.15298 | 2904.9151 | 12:03 | 1.585 | 1.457 | 0.12803 | 1.7005e-05 | 0
[13 empty] | 12:03 | 1.0572 | 0.91146 | 0.91784 |  | 12:03 | 1.0643 | 0.15298 | 2920.9961 | 12:03 | 1.5857 | 1.4576 | 0.12808 | 1.7011e-05 | 0
[13 empty] | 12:03 | 1.0434 | 0.91146 | 0.91784 |  | 12:03 | 1.0503 | 0.15298 | 2936.8479 | 12:03 | 1.5863 | 1.4582 | 0.12813 | 1.7018e-05 | 0
[13 empty] | 12:04 | 1.0298 | 0.91146 | 0.91784 |  | 12:04 | 1.0366 | 0.15298 | 2952.5088 | 12:04 | 1.5869 | 1.4587 | 0.12818 | 1.7025e-05 | 0
[13 empty] | 12:04 | 1.0164 | 0.91146 | 0.91784 |  | 12:04 | 1.0231 | 0.15298 | 2967.9595 | 12:04 | 1.5875 | 1.4593 | 0.12823 | 1.7032e-05 | 0
[13 empty] | 12:04 | 1.0034 | 0.91146 | 0.91784 |  | 12:04 | 1.0099 | 0.15298 | 2983.2002 | 12:04 | 1.5882 | 1.4599 | 0.12828 | 1.7038e-05 | 0
[13 empty] | 12:04 | 0.99062 | 0.91146 | 0.91784 |  | 12:04 | 0.99701 | 0.15298 | 2998.2499 | 12:04 | 1.5888 | 1.4604 | 0.12833 | 1.7045e-05 | 0
[13 empty] | 12:04 | 0.97811 | 0.91146 | 0.91784 |  | 12:04 | 0.98437 | 0.15298 | 3013.1086 | 12:04 | 1.5893 | 1.4609 | 0.12838 | 1.7051e-05 | 0
[13 empty] | 12:05 | 0.96585 | 0.91146 | 0.91784 |  | 12:05 | 0.97198 | 0.15298 | 3027.7954 | 12:05 | 1.5899 | 1.4615 | 0.12842 | 1.7057e-05 | 0
[13 empty] | 12:05 | 0.95385 | 0.91146 | 0.91784 |  | 12:05 | 0.95985 | 0.15298 | 3042.2721 | 12:05 | 1.5905 | 1.462 | 0.12847 | 1.7063e-05 | 0
[13 empty] | 12:05 | 0.94209 | 0.91146 | 0.91784 |  | 12:05 | 0.94797 | 0.15298 | 3056.577 | 12:05 | 1.5911 | 1.4625 | 0.12851 | 1.707e-05 | 0
[13 empty] | 12:06 | 0.93058 | 0.91146 | 0.91784 |  | 12:06 | 0.93634 | 0.15298 | 3070.7099 | 12:06 | 1.5916 | 1.4631 | 0.12856 | 1.7076e-05 | 0
[13 empty] | 12:06 | 0.9193 | 0.91146 | 0.91784 |  | 12:06 | 0.92494 | 0.15298 | 3084.671 | 12:06 | 1.5922 | 1.4636 | 0.1286 | 1.7082e-05 | 0
[13 empty] | 12:06 | 0.90825 | 0.91146 | 0.91784 |  | 12:06 | 0.91377 | 0.15298 | 3098.4602 | 12:06 | 1.5927 | 1.4641 | 0.12865 | 1.7088e-05 | 0
[13 empty] | 12:06 | 0.89743 | 0.91146 | 0.91784 |  | 12:06 | 0.90284 | 0.15298 | 3112.0966 | 12:06 | 1.5933 | 1.4646 | 0.12869 | 1.7093e-05 | 0
[13 empty] | 12:06 | 0.88683 | 0.91146 | 0.91784 |  | 12:06 | 0.89213 | 0.15298 | 3125.5611 | 12:06 | 1.5938 | 1.4651 | 0.12874 | 1.7099e-05 | 0
[13 empty] | 12:07 | 0.87645 | 0.91146 | 0.91784 |  | 12:07 | 0.88164 | 0.15298 | 3138.8537 | 12:07 | 1.5943 | 1.4655 | 0.12878 | 1.7105e-05 | 0
[13 empty] | 12:07 | 0.86628 | 0.91146 | 0.91784 |  | 12:07 | 0.87137 | 0.15298 | 3152.0127 | 12:07 | 1.5949 | 1.466 | 0.12882 | 1.711e-05 | 0
[13 empty] | 12:07 | 0.85633 | 0.91146 | 0.91784 |  | 12:07 | 0.8613 | 0.15298 | 3164.9997 | 12:07 | 1.5954 | 1.4665 | 0.12886 | 1.7116e-05 | 0
[13 empty] | 12:08 | 0.84657 | 0.91146 | 0.91784 |  | 12:08 | 0.85145 | 0.15298 | 3177.8531 | 12:08 | 1.5959 | 1.467 | 0.1289 | 1.7122e-05 | 0
[13 empty] | 12:08 | 0.83702 | 0.91146 | 0.91784 |  | 12:08 | 0.8418 | 0.15298 | 3190.5345 | 12:08 | 1.5964 | 1.4675 | 0.12895 | 1.7127e-05 | 0
[13 empty] | 12:08 | 0.82766 | 0.91146 | 0.91784 |  | 12:08 | 0.83234 | 0.15298 | 3203.1014 | 12:08 | 1.5969 | 1.4679 | 0.12899 | 1.7132e-05 | 0
[13 empty] | 12:08 | 0.8185 | 0.91146 | 0.91784 |  | 12:08 | 0.82308 | 0.15298 | 3215.5155 | 12:08 | 1.5974 | 1.4684 | 0.12903 | 1.7138e-05 | 0
[13 empty] | 12:08 | 0.80952 | 0.91146 | 0.91784 |  | 12:08 | 0.81401 | 0.15298 | 3227.7959 | 12:08 | 1.5979 | 1.4688 | 0.12907 | 1.7143e-05 | 0
[13 empty] | 12:09 | 0.80073 | 0.91146 | 0.91784 |  | 12:09 | 0.80512 | 0.15298 | 3239.9426 | 12:09 | 1.5984 | 1.4693 | 0.1291 | 1.7148e-05 | 0
[13 empty] | 12:09 | 0.79211 | 0.91146 | 0.91784 |  | 12:09 | 0.79642 | 0.15298 | 3251.9556 | 12:09 | 1.5989 | 1.4697 | 0.12914 | 1.7153e-05 | 0
[13 empty] | 12:09 | 0.78368 | 0.91146 | 0.91784 |  | 12:09 | 0.7879 | 0.15298 | 3263.8349 | 12:09 | 1.5993 | 1.4701 | 0.12918 | 1.7158e-05 | 0
[13 empty] | 12:10 | 0.77542 | 0.91146 | 0.91784 |  | 12:10 | 0.77955 | 0.15298 | 3275.5806 | 12:10 | 1.5998 | 1.4706 | 0.12922 | 1.7163e-05 | 0
[13 empty] | 12:10 | 0.76733 | 0.91146 | 0.91784 |  | 12:10 | 0.77137 | 0.15298 | 3287.2116 | 12:10 | 1.6003 | 1.471 | 0.12926 | 1.7168e-05 | 0
[13 empty] | 12:10 | 0.7594 | 0.91146 | 0.91784 |  | 12:10 | 0.76336 | 0.15298 | 3298.728 | 12:10 | 1.6007 | 1.4714 | 0.1293 | 1.7173e-05 | 0
[13 empty] | 12:10 | 0.75164 | 0.91146 | 0.91784 |  | 12:10 | 0 | 0.15298 | 3304.4576 | 12:10 | 1.6012 | 1.4718 | 0.12933 | 1.7178e-05 | 0
[13 empty] | 12:10 | 0.74403 | 0.91146 | 0.91784 |  | 12:10 | 0 | 0.15298 | 3304.4576 | 12:10 | 1.6016 | 1.4723 | 0.12937 | 1.7183e-05 | 0
[13 empty] | 12:11 | 0.73658 | 0.91146 | 0.91784 |  | 12:11 | 0 | 0.15298 | 3304.4576 | 12:11 | 1.6021 | 1.4727 | 0.1294 | 1.7188e-05 | 0
[13 empty] | 12:11 | 0.72929 | 0.91146 | 0.91784 |  | 12:11 | 0 | 0.15298 | 3304.4576 | 12:11 | 1.6025 | 1.4731 | 0.12944 | 1.7192e-05 | 0
[13 empty] | 12:11 | 1.1629 | 0.91146 | 0.91784 |  | 12:11 | 0 | 0.15298 | 3304.4576 | 12:11 | 1.6032 | 1.4737 | 0.1295 | 1.72e-05 | 0
[13 empty] | 12:12 | 1.1468 | 0.91146 | 0.91784 |  | 12:12 | 0 | 0.15298 | 3304.4576 | 12:12 | 1.6039 | 1.4744 | 0.12955 | 1.7207e-05 | 0
[13 empty] | 12:12 | 1.1311 | 0.91146 | 0.91784 |  | 12:12 | 0 | 0.15298 | 3304.4576 | 12:12 | 1.6046 | 1.475 | 0.12961 | 1.7215e-05 | 0
[13 empty] | 12:12 | 1.1157 | 0.91146 | 0.91784 |  | 12:12 | 0 | 0.15298 | 3304.4576 | 12:12 | 1.6053 | 1.4756 | 0.12966 | 1.7222e-05 | 0
[13 empty] | 12:12 | 1.1006 | 0.91146 | 0.91784 |  | 12:12 | 0 | 0.15298 | 3304.4576 | 12:12 | 1.606 | 1.4762 | 0.12972 | 1.7229e-05 | 0
[13 empty] | 12:12 | 1.0859 | 0.91146 | 0.91784 |  | 12:12 | 0 | 0.15298 | 3304.4576 | 12:12 | 1.6066 | 1.4768 | 0.12977 | 1.7236e-05 | 0
[13 empty] | 12:13 | 1.0714 | 0.91146 | 0.91784 |  | 12:13 | 0 | 0.15298 | 3304.4576 | 12:13 | 1.6072 | 1.4774 | 0.12982 | 1.7243e-05 | 0
[13 empty] | 12:13 | 1.0572 | 0.91146 | 0.91784 |  | 12:13 | 0 | 0.15298 | 3304.4576 | 12:13 | 1.6079 | 1.478 | 0.12987 | 1.725e-05 | 0
[13 empty] | 12:13 | 1.0434 | 0.91146 | 0.91784 |  | 12:13 | 0 | 0.15298 | 3304.4576 | 12:13 | 1.6085 | 1.4786 | 0.12992 | 1.7257e-05 | 0
[13 empty] | 12:14 | 1.0298 | 0.91146 | 0.91784 |  | 12:14 | 0 | 0.15298 | 3304.4576 | 12:14 | 1.6092 | 1.4792 | 0.12998 | 1.7264e-05 | 0
[13 empty] | 12:14 | 1.0164 | 0.91146 | 0.91784 |  | 12:14 | 0 | 0.15298 | 3304.4576 | 12:14 | 1.6098 | 1.4797 | 0.13003 | 1.727e-05 | 0
[13 empty] | 12:14 | 1.0034 | 0.91146 | 0.91784 |  | 12:14 | 0 | 0.15298 | 3304.4576 | 12:14 | 1.6104 | 1.4803 | 0.13007 | 1.7277e-05 | 0
[13 empty] | 12:14 | 0.99062 | 0.91146 | 0.91784 |  | 12:14 | 0 | 0.15298 | 3304.4576 | 12:14 | 1.611 | 1.4808 | 0.13012 | 1.7283e-05 | 0
[13 empty] | 12:14 | 0.97811 | 0.91146 | 0.91784 |  | 12:14 | 0 | 0.15298 | 3304.4576 | 12:14 | 1.6116 | 1.4814 | 0.13017 | 1.7289e-05 | 0
[13 empty] | 12:15 | 0.96585 | 0.91146 | 0.91784 |  | 12:15 | 0 | 0.15298 | 3304.4576 | 12:15 | 1.6122 | 1.4819 | 0.13022 | 1.7296e-05 | 0
[13 empty] | 12:15 | 0.95385 | 0.91146 | 0.91784 |  | 12:15 | 0 | 0.15298 | 3304.4576 | 12:15 | 1.6127 | 1.4825 | 0.13026 | 1.7302e-05 | 0
[13 empty] | 12:15 | 0.94209 | 0.91146 | 0.91784 |  | 12:15 | 0 | 0.15298 | 3304.4576 | 12:15 | 1.6133 | 1.483 | 0.13031 | 1.7308e-05 | 0
[13 empty] | 12:16 | 0.93058 | 0.91146 | 0.91784 |  | 12:16 | 0 | 0.15298 | 3304.4576 | 12:16 | 1.6139 | 1.4835 | 0.13036 | 1.7314e-05 | 0
[13 empty] | 12:16 | 0.9193 | 0.91146 | 0.91784 |  | 12:16 | 0 | 0.15298 | 3304.4576 | 12:16 | 1.6144 | 1.484 | 0.1304 | 1.732e-05 | 0
[13 empty] | 12:16 | 0.90825 | 0.91146 | 0.91784 |  | 12:16 | 0 | 0.15298 | 3304.4576 | 12:16 | 1.615 | 1.4845 | 0.13045 | 1.7326e-05 | 0
[13 empty] | 12:16 | 0.89743 | 0.91146 | 0.91784 |  | 12:16 | 0 | 0.15298 | 3304.4576 | 12:16 | 1.6155 | 1.485 | 0.13049 | 1.7332e-05 | 0
[13 empty] | 12:16 | 0.88683 | 0.91146 | 0.91784 |  | 12:16 | 0 | 0.15298 | 3304.4576 | 12:16 | 1.6161 | 1.4855 | 0.13053 | 1.7338e-05 | 0
[13 empty] | 12:17 | 0.87645 | 0.91146 | 0.91784 |  | 12:17 | 0 | 0.15298 | 3304.4576 | 12:17 | 1.6166 | 1.486 | 0.13058 | 1.7343e-05 | 0
[13 empty] | 12:17 | 0.86628 | 0.91146 | 0.91784 |  | 12:17 | 0 | 0.15298 | 3304.4576 | 12:17 | 1.6171 | 1.4865 | 0.13062 | 1.7349e-05 | 0
[13 empty] | 12:17 | 0.85633 | 0.91146 | 0.91784 |  | 12:17 | 0 | 0.15298 | 3304.4576 | 12:17 | 1.6176 | 1.4869 | 0.13066 | 1.7354e-05 | 0
[13 empty] | 12:18 | 0.84657 | 0.91146 | 0.91784 |  | 12:18 | 0 | 0.15298 | 3304.4576 | 12:18 | 1.6181 | 1.4874 | 0.1307 | 1.736e-05 | 0
[13 empty] | 12:18 | 0.83702 | 0.91146 | 0.91784 |  | 12:18 | 0 | 0.15298 | 3304.4576 | 12:18 | 1.6186 | 1.4879 | 0.13074 | 1.7365e-05 | 0
[13 empty] | 12:18 | 0.82766 | 0.91146 | 0.91784 |  | 12:18 | 0 | 0.15298 | 3304.4576 | 12:18 | 1.6191 | 1.4883 | 0.13078 | 1.7371e-05 | 0
[13 empty] | 12:18 | 0.8185 | 0.91146 | 0.91784 |  | 12:18 | 0 | 0.15298 | 3304.4576 | 12:18 | 1.6196 | 1.4888 | 0.13082 | 1.7376e-05 | 0
[13 empty] | 12:18 | 0.80952 | 0.91146 | 0.91784 |  | 12:18 | 0 | 0.15298 | 3304.4576 | 12:18 | 1.6201 | 1.4893 | 0.13086 | 1.7381e-05 | 0
[13 empty] | 12:19 | 0.80073 | 0.91146 | 0.91784 |  | 12:19 | 0 | 0.15298 | 3304.4576 | 12:19 | 1.6206 | 1.4897 | 0.1309 | 1.7386e-05 | 0
[13 empty] | 12:19 | 0.79211 | 0.91146 | 0.91784 |  | 12:19 | 0 | 0.15298 | 3304.4576 | 12:19 | 1.6211 | 1.4901 | 0.13094 | 1.7392e-05 | 0
[13 empty] | 12:19 | 0.78368 | 0.91146 | 0.91784 |  | 12:19 | 0 | 0.15298 | 3304.4576 | 12:19 | 1.6216 | 1.4906 | 0.13098 | 1.7397e-05 | 0
[13 empty] | 12:20 | 0.77542 | 0.91146 | 0.91784 |  | 12:20 | 0 | 0.15298 | 3304.4576 | 12:20 | 1.622 | 1.491 | 0.13102 | 1.7402e-05 | 0
[13 empty] | 12:20 | 0.76733 | 0.91146 | 0.91784 |  | 12:20 | 0 | 0.15298 | 3304.4576 | 12:20 | 1.6225 | 1.4914 | 0.13105 | 1.7407e-05 | 0
[13 empty] | 12:20 | 0.7594 | 0.91146 | 0.91784 |  | 12:20 | 0 | 0.15298 | 3304.4576 | 12:20 | 1.623 | 1.4918 | 0.13109 | 1.7412e-05 | 0
[13 empty] | 12:20 | 0.75164 | 0.91146 | 0.91784 |  | 12:20 | 0 | 0.15298 | 3304.4576 | 12:20 | 1.6234 | 1.4923 | 0.13113 | 1.7417e-05 | 0
[13 empty] | 12:20 | 0.74403 | 0.91146 | 0.91784 |  | 12:20 | 0 | 0.15298 | 3304.4576 | 12:20 | 1.6239 | 1.4927 | 0.13116 | 1.7421e-05 | 0
[13 empty] | 12:21 | 0.73658 | 0.91146 | 0.91784 |  | 12:21 | 0 | 0.15298 | 3304.4576 | 12:21 | 1.6243 | 1.4931 | 0.1312 | 1.7426e-05 | 0
[13 empty] | 12:21 | 0.72929 | 0.91146 | 0.91784 |  | 12:21 | 0 | 0.15298 | 3304.4576 | 12:21 | 1.6248 | 1.4935 | 0.13123 | 1.7431e-05 | 0
[13 empty] | 12:21 | 1.1629 | 0.91146 | 0.91784 |  | 12:21 | 0 | 0.15298 | 3304.4576 | 12:21 | 1.6254 | 1.4941 | 0.13129 | 1.7438e-05 | 0
[13 empty] | 12:22 | 1.1468 | 0.91146 | 0.91784 |  | 12:22 | 0 | 0.15298 | 3304.4576 | 12:22 | 1.6262 | 1.4948 | 0.13135 | 1.7446e-05 | 0
[13 empty] | 12:22 | 1.1311 | 0.91146 | 0.91784 |  | 12:22 | 0 | 0.15298 | 3304.4576 | 12:22 | 1.6268 | 1.4954 | 0.1314 | 1.7453e-05 | 0
[13 empty] | 12:22 | 1.1157 | 0.91146 | 0.91784 |  | 12:22 | 0 | 0.15298 | 3304.4576 | 12:22 | 1.6275 | 1.496 | 0.13146 | 1.7461e-05 | 0
[13 empty] | 12:22 | 1.1006 | 0.91146 | 0.91784 |  | 12:22 | 0 | 0.15298 | 3304.4576 | 12:22 | 1.6282 | 1.4966 | 0.13151 | 1.7468e-05 | 0
[13 empty] | 12:22 | 1.0859 | 0.91146 | 0.91784 |  | 12:22 | 0 | 0.15298 | 3304.4576 | 12:22 | 1.6288 | 1.4973 | 0.13156 | 1.7475e-05 | 0
[13 empty] | 12:23 | 1.0714 | 0.91146 | 0.91784 |  | 12:23 | 0 | 0.15298 | 3304.4576 | 12:23 | 1.6295 | 1.4978 | 0.13162 | 1.7482e-05 | 0
[13 empty] | 12:23 | 1.0572 | 0.91146 | 0.91784 |  | 12:23 | 0 | 0.15298 | 3304.4576 | 12:23 | 1.6301 | 1.4984 | 0.13167 | 1.7489e-05 | 0
[13 empty] | 12:23 | 1.0434 | 0.91146 | 0.91784 |  | 12:23 | 0 | 0.15298 | 3304.4576 | 12:23 | 1.6307 | 1.499 | 0.13172 | 1.7495e-05 | 0
[13 empty] | 12:24 | 1.0298 | 0.91146 | 0.91784 |  | 12:24 | 0 | 0.15298 | 3304.4576 | 12:24 | 1.6314 | 1.4996 | 0.13177 | 1.7502e-05 | 0
[13 empty] | 12:24 | 1.0164 | 0.91146 | 0.91784 |  | 12:24 | 0 | 0.15298 | 3304.4576 | 12:24 | 1.632 | 1.5002 | 0.13182 | 1.7509e-05 | 0
[13 empty] | 12:24 | 1.0034 | 0.91146 | 0.91784 |  | 12:24 | 0 | 0.15298 | 3304.4576 | 12:24 | 1.6326 | 1.5007 | 0.13187 | 1.7515e-05 | 0
[13 empty] | 12:24 | 0.99062 | 0.91146 | 0.91784 |  | 12:24 | 0 | 0.15298 | 3304.4576 | 12:24 | 1.6332 | 1.5013 | 0.13192 | 1.7522e-05 | 0
[13 empty] | 12:24 | 0.97811 | 0.91146 | 0.91784 |  | 12:24 | 0 | 0.15298 | 3304.4576 | 12:24 | 1.6338 | 1.5018 | 0.13197 | 1.7528e-05 | 0
[13 empty] | 12:25 | 0.96585 | 0.91146 | 0.91784 |  | 12:25 | 0 | 0.15298 | 3304.4576 | 12:25 | 1.6344 | 1.5024 | 0.13201 | 1.7534e-05 | 0
[13 empty] | 12:25 | 0.95385 | 0.91146 | 0.91784 |  | 12:25 | 0 | 0.15298 | 3304.4576 | 12:25 | 1.635 | 1.5029 | 0.13206 | 1.754e-05 | 0
[13 empty] | 12:25 | 0.94209 | 0.91146 | 0.91784 |  | 12:25 | 0 | 0.15298 | 3304.4576 | 12:25 | 1.6355 | 1.5034 | 0.1321 | 1.7546e-05 | 0
[13 empty] | 12:26 | 0.93058 | 0.91146 | 0.91784 |  | 12:26 | 0 | 0.15298 | 3304.4576 | 12:26 | 1.6361 | 1.5039 | 0.13215 | 1.7553e-05 | 0
[13 empty] | 12:26 | 0.9193 | 0.91146 | 0.91784 |  | 12:26 | 0 | 0.15298 | 3304.4576 | 12:26 | 1.6366 | 1.5044 | 0.13219 | 1.7558e-05 | 0
[13 empty] | 12:26 | 0.90825 | 0.91146 | 0.91784 |  | 12:26 | 0 | 0.15298 | 3304.4576 | 12:26 | 1.6372 | 1.5049 | 0.13224 | 1.7564e-05 | 0
[13 empty] | 12:26 | 0.89743 | 0.91146 | 0.91784 |  | 12:26 | 0 | 0.15298 | 3304.4576 | 12:26 | 1.6377 | 1.5054 | 0.13228 | 1.757e-05 | 0
[13 empty] | 12:26 | 0.88683 | 0.91146 | 0.91784 |  | 12:26 | 0 | 0.15298 | 3304.4576 | 12:26 | 1.6383 | 1.5059 | 0.13233 | 1.7576e-05 | 0
[13 empty] | 12:27 | 0.87645 | 0.91146 | 0.91784 |  | 12:27 | 0 | 0.15298 | 3304.4576 | 12:27 | 1.6388 | 1.5064 | 0.13237 | 1.7582e-05 | 0
[13 empty] | 12:27 | 0.86628 | 0.91146 | 0.91784 |  | 12:27 | 0 | 0.15298 | 3304.4576 | 12:27 | 1.6393 | 1.5069 | 0.13241 | 1.7587e-05 | 0
[13 empty] | 12:27 | 0.85633 | 0.91146 | 0.91784 |  | 12:27 | 0 | 0.15298 | 3304.4576 | 12:27 | 1.6398 | 1.5074 | 0.13245 | 1.7593e-05 | 0
[13 empty] | 12:28 | 0.84657 | 0.91146 | 0.91784 |  | 12:28 | 0 | 0.15298 | 3304.4576 | 12:28 | 1.6404 | 1.5079 | 0.1325 | 1.7598e-05 | 0
[13 empty] | 12:28 | 0.83702 | 0.91146 | 0.91784 |  | 12:28 | 0 | 0.15298 | 3304.4576 | 12:28 | 1.6409 | 1.5083 | 0.13254 | 1.7604e-05 | 0
[13 empty] | 12:28 | 0.82766 | 0.91146 | 0.91784 |  | 12:28 | 0 | 0.15298 | 3304.4576 | 12:28 | 1.6414 | 1.5088 | 0.13258 | 1.7609e-05 | 0
[13 empty] | 12:28 | 0.8185 | 0.91146 | 0.91784 |  | 12:28 | 0 | 0.15298 | 3304.4576 | 12:28 | 1.6419 | 1.5092 | 0.13262 | 1.7614e-05 | 0
[13 empty] | 12:28 | 0.80952 | 0.91146 | 0.91784 |  | 12:28 | 0 | 0.15298 | 3304.4576 | 12:28 | 1.6424 | 1.5097 | 0.13266 | 1.762e-05 | 0
[13 empty] | 12:29 | 0.80073 | 0.91146 | 0.91784 |  | 12:29 | 0 | 0.15298 | 3304.4576 | 12:29 | 1.6428 | 1.5101 | 0.1327 | 1.7625e-05 | 0
[13 empty] | 12:29 | 0.79211 | 0.91146 | 0.91784 |  | 12:29 | 0 | 0.15298 | 3304.4576 | 12:29 | 1.6433 | 1.5106 | 0.13274 | 1.763e-05 | 0
[13 empty] | 12:29 | 0.78368 | 0.91146 | 0.91784 |  | 12:29 | 0 | 0.15298 | 3304.4576 | 12:29 | 1.6438 | 1.511 | 0.13277 | 1.7635e-05 | 0
[13 empty] | 12:30 | 0.77542 | 0.91146 | 0.91784 |  | 12:30 | 0 | 0.15298 | 3304.4576 | 12:30 | 1.6443 | 1.5114 | 0.13281 | 1.764e-05 | 0
[13 empty] | 12:30 | 0.76733 | 0.91146 | 0.91784 |  | 12:30 | 0 | 0.15298 | 3304.4576 | 12:30 | 1.6447 | 1.5119 | 0.13285 | 1.7645e-05 | 0
[13 empty] | 12:30 | 0.7594 | 0.91146 | 0.91784 |  | 12:30 | 0 | 0.15298 | 3304.4576 | 12:30 | 1.6452 | 1.5123 | 0.13289 | 1.765e-05 | 0
[13 empty] | 12:30 | 0.75164 | 0.91146 | 0.91784 |  | 12:30 | 0 | 0.15298 | 3304.4576 | 12:30 | 1.6456 | 1.5127 | 0.13292 | 1.7655e-05 | 0
[13 empty] | 12:30 | 0.74403 | 0.91146 | 0.91784 |  | 12:30 | 0 | 0.15298 | 3304.4576 | 12:30 | 1.6461 | 1.5131 | 0.13296 | 1.766e-05 | 0
[13 empty] | 12:31 | 0.73658 | 0.91146 | 0.91784 |  | 12:31 | 0 | 0.15298 | 3304.4576 | 12:31 | 1.6465 | 1.5135 | 0.13299 | 1.7665e-05 | 0
[13 empty] | 12:31 | 0.72929 | 0.91146 | 0.91784 |  | 12:31 | 0 | 0.15298 | 3304.4576 | 12:31 | 1.647 | 1.5139 | 0.13303 | 1.7669e-05 | 0
[13 empty] | 12:31 | 1.1629 | 0.91146 | 0.91784 |  | 12:31 | 0 | 0.15298 | 3304.4576 | 12:31 | 1.6477 | 1.5146 | 0.13309 | 1.7677e-05 | 0
[13 empty] | 12:32 | 1.1468 | 0.91146 | 0.91784 |  | 12:32 | 0 | 0.15298 | 3304.4576 | 12:32 | 1.6484 | 1.5152 | 0.13314 | 1.7684e-05 | 0
[13 empty] | 12:32 | 1.1311 | 0.91146 | 0.91784 |  | 12:32 | 0 | 0.15298 | 3304.4576 | 12:32 | 1.6491 | 1.5159 | 0.1332 | 1.7692e-05 | 0
[13 empty] | 12:32 | 1.1157 | 0.91146 | 0.91784 |  | 12:32 | 0 | 0.15298 | 3304.4576 | 12:32 | 1.6497 | 1.5165 | 0.13325 | 1.7699e-05 | 0
[13 empty] | 12:32 | 1.1006 | 0.91146 | 0.91784 |  | 12:32 | 0 | 0.15298 | 3304.4576 | 12:32 | 1.6504 | 1.5171 | 0.13331 | 1.7706e-05 | 0
[13 empty] | 12:32 | 1.0859 | 0.91146 | 0.91784 |  | 12:32 | 0 | 0.15298 | 3304.4576 | 12:32 | 1.6511 | 1.5177 | 0.13336 | 1.7713e-05 | 0
[13 empty] | 12:33 | 1.0714 | 0.91146 | 0.91784 |  | 12:33 | 0 | 0.15298 | 3304.4576 | 12:33 | 1.6517 | 1.5183 | 0.13341 | 1.772e-05 | 0
[13 empty] | 12:33 | 1.0572 | 0.91146 | 0.91784 |  | 12:33 | 0 | 0.15298 | 3304.4576 | 12:33 | 1.6524 | 1.5189 | 0.13346 | 1.7727e-05 | 0
[13 empty] | 12:33 | 1.0434 | 0.91146 | 0.91784 |  | 12:33 | 0 | 0.15298 | 3304.4576 | 12:33 | 1.653 | 1.5194 | 0.13351 | 1.7734e-05 | 0
[13 empty] | 12:34 | 1.0298 | 0.91146 | 0.91784 |  | 12:34 | 0 | 0.15298 | 3304.4576 | 12:34 | 1.6536 | 1.52 | 0.13357 | 1.774e-05 | 0
[13 empty] | 12:34 | 1.0164 | 0.91146 | 0.91784 |  | 12:34 | 0 | 0.15298 | 3304.4576 | 12:34 | 1.6542 | 1.5206 | 0.13362 | 1.7747e-05 | 0
[13 empty] | 12:34 | 1.0034 | 0.91146 | 0.91784 |  | 12:34 | 0 | 0.15298 | 3304.4576 | 12:34 | 1.6548 | 1.5211 | 0.13366 | 1.7753e-05 | 0
[13 empty] | 12:34 | 0.99062 | 0.91146 | 0.91784 |  | 12:34 | 0 | 0.15298 | 3304.4576 | 12:34 | 1.6554 | 1.5217 | 0.13371 | 1.776e-05 | 0
[13 empty] | 12:34 | 0.97811 | 0.91146 | 0.91784 |  | 12:34 | 0 | 0.15298 | 3304.4576 | 12:34 | 1.656 | 1.5223 | 0.13376 | 1.7766e-05 | 0
[13 empty] | 12:35 | 0.96585 | 0.91146 | 0.91784 |  | 12:35 | 0 | 0.15298 | 3304.4576 | 12:35 | 1.6566 | 1.5228 | 0.13381 | 1.7773e-05 | 0
[13 empty] | 12:35 | 0.95385 | 0.91146 | 0.91784 |  | 12:35 | 0 | 0.15298 | 3304.4576 | 12:35 | 1.6572 | 1.5233 | 0.13385 | 1.7779e-05 | 0
[13 empty] | 12:35 | 0.94209 | 0.91146 | 0.91784 |  | 12:35 | 0 | 0.15298 | 3304.4576 | 12:35 | 1.6578 | 1.5238 | 0.1339 | 1.7785e-05 | 0
[13 empty] | 12:36 | 0.93058 | 0.91146 | 0.91784 |  | 12:36 | 0 | 0.15298 | 3304.4576 | 12:36 | 1.6583 | 1.5244 | 0.13395 | 1.7791e-05 | 0
[13 empty] | 12:36 | 0.9193 | 0.91146 | 0.91784 |  | 12:36 | 0 | 0.15298 | 3304.4576 | 12:36 | 1.6589 | 1.5249 | 0.13399 | 1.7797e-05 | 0
[13 empty] | 12:36 | 0.90825 | 0.91146 | 0.91784 |  | 12:36 | 0 | 0.15298 | 3304.4576 | 12:36 | 1.6594 | 1.5254 | 0.13404 | 1.7803e-05 | 0
[13 empty] | 12:36 | 0.89743 | 0.91146 | 0.91784 |  | 12:36 | 0 | 0.15298 | 3304.4576 | 12:36 | 1.66 | 1.5259 | 0.13408 | 1.7809e-05 | 0
[13 empty] | 12:36 | 0.88683 | 0.91146 | 0.91784 |  | 12:36 | 0 | 0.15298 | 3304.4576 | 12:36 | 1.6605 | 1.5264 | 0.13412 | 1.7814e-05 | 0
[13 empty] | 12:37 | 0.87645 | 0.91146 | 0.91784 |  | 12:37 | 0 | 0.15298 | 3304.4576 | 12:37 | 1.661 | 1.5269 | 0.13417 | 1.782e-05 | 0
[13 empty] | 12:37 | 0.86628 | 0.91146 | 0.91784 |  | 12:37 | 0 | 0.15298 | 3304.4576 | 12:37 | 1.6616 | 1.5273 | 0.13421 | 1.7826e-05 | 0
[13 empty] | 12:37 | 0.85633 | 0.91146 | 0.91784 |  | 12:37 | 0 | 0.15298 | 3304.4576 | 12:37 | 1.6621 | 1.5278 | 0.13425 | 1.7831e-05 | 0
[13 empty] | 12:38 | 0.84657 | 0.91146 | 0.91784 |  | 12:38 | 0 | 0.15298 | 3304.4576 | 12:38 | 1.6626 | 1.5283 | 0.13429 | 1.7837e-05 | 0
[13 empty] | 12:38 | 0.83702 | 0.91146 | 0.91784 |  | 12:38 | 0 | 0.15298 | 3304.4576 | 12:38 | 1.6631 | 1.5287 | 0.13433 | 1.7842e-05 | 0
[13 empty] | 12:38 | 0.82766 | 0.91146 | 0.91784 |  | 12:38 | 0 | 0.15298 | 3304.4576 | 12:38 | 1.6636 | 1.5292 | 0.13437 | 1.7848e-05 | 0
[13 empty] | 12:38 | 0.8185 | 0.91146 | 0.91784 |  | 12:38 | 0 | 0.15298 | 3304.4576 | 12:38 | 1.6641 | 1.5297 | 0.13441 | 1.7853e-05 | 0
[13 empty] | 12:39 | 0.80952 | 0.91146 | 0.91784 |  | 12:39 | 0 | 0.15298 | 3304.4576 | 12:39 | 1.6646 | 1.5301 | 0.13445 | 1.7858e-05 | 0
[13 empty] | 12:39 | 0.80073 | 0.91146 | 0.91784 |  | 12:39 | 0 | 0.15298 | 3304.4576 | 12:39 | 1.6651 | 1.5306 | 0.13449 | 1.7863e-05 | 0
[13 empty] | 12:39 | 0.79211 | 0.91146 | 0.91784 |  | 12:39 | 0 | 0.15298 | 3304.4576 | 12:39 | 1.6655 | 1.531 | 0.13453 | 1.7869e-05 | 0
[13 empty] | 12:39 | 0.78368 | 0.91146 | 0.91784 |  | 12:39 | 0 | 0.15298 | 3304.4576 | 12:39 | 1.666 | 1.5314 | 0.13457 | 1.7874e-05 | 0
[13 empty] | 12:39 | 0.77542 | 0.91146 | 0.91784 |  | 12:39 | 0 | 0.15298 | 3304.4576 | 12:39 | 1.6665 | 1.5319 | 0.13461 | 1.7879e-05 | 0
[13 empty] | 12:40 | 0.76733 | 0.91146 | 0.91784 |  | 12:40 | 0 | 0.15298 | 3304.4576 | 12:40 | 1.667 | 1.5323 | 0.13464 | 1.7884e-05 | 0
[13 empty] | 12:40 | 0.7594 | 0.91146 | 0.91784 |  | 12:40 | 0 | 0.15298 | 3304.4576 | 12:40 | 1.6674 | 1.5327 | 0.13468 | 1.7889e-05 | 0
[13 empty] | 12:40 | 0.75164 | 0.91146 | 0.91784 |  | 12:40 | 0 | 0.15298 | 3304.4576 | 12:40 | 1.6679 | 1.5331 | 0.13472 | 1.7893e-05 | 0
[13 empty] | 12:41 | 0.74403 | 0.91146 | 0.91784 |  | 12:41 | 0 | 0.15298 | 3304.4576 | 12:41 | 1.6683 | 1.5336 | 0.13475 | 1.7898e-05 | 0
[13 empty] | 12:41 | 0.73658 | 0.91146 | 0.91784 |  | 12:41 | 0 | 0.15298 | 3304.4576 | 12:41 | 1.6688 | 1.534 | 0.13479 | 1.7903e-05 | 0
[13 empty] | 12:41 | 0.72929 | 0.91146 | 0.91784 |  | 12:41 | 0 | 0.15298 | 3304.4576 | 12:41 | 1.6692 | 1.5344 | 0.13483 | 1.7908e-05 | 0
[13 empty] | 12:41 | 1.1629 | 0.91146 | 0.91784 |  | 12:41 | 0 | 0.15298 | 3304.4576 | 12:41 | 1.6699 | 1.535 | 0.13488 | 1.7915e-05 | 0
[13 empty] | 12:41 | 1.1468 | 0.91146 | 0.91784 |  | 12:41 | 0 | 0.15298 | 3304.4576 | 12:41 | 1.6706 | 1.5357 | 0.13494 | 1.7923e-05 | 0
[13 empty] | 12:42 | 1.1311 | 0.91146 | 0.91784 |  | 12:42 | 0 | 0.15298 | 3304.4576 | 12:42 | 1.6713 | 1.5363 | 0.13499 | 1.793e-05 | 0
[13 empty] | 12:42 | 1.1157 | 0.91146 | 0.91784 |  | 12:42 | 0 | 0.15298 | 3304.4576 | 12:42 | 1.672 | 1.5369 | 0.13505 | 1.7937e-05 | 0
[13 empty] | 12:42 | 1.1006 | 0.91146 | 0.91784 |  | 12:42 | 0 | 0.15298 | 3304.4576 | 12:42 | 1.6726 | 1.5375 | 0.1351 | 1.7945e-05 | 0
[13 empty] | 12:43 | 1.0859 | 0.91146 | 0.91784 |  | 12:43 | 0 | 0.15298 | 3304.4576 | 12:43 | 1.6733 | 1.5381 | 0.13516 | 1.7952e-05 | 0
[13 empty] | 12:43 | 1.0714 | 0.91146 | 0.91784 |  | 12:43 | 0 | 0.15298 | 3304.4576 | 12:43 | 1.6739 | 1.5387 | 0.13521 | 1.7959e-05 | 0
[13 empty] | 12:43 | 1.0572 | 0.91146 | 0.91784 |  | 12:43 | 0 | 0.15298 | 3304.4576 | 12:43 | 1.6746 | 1.5393 | 0.13526 | 1.7965e-05 | 0
[13 empty] | 12:43 | 1.0434 | 0.91146 | 0.91784 |  | 12:43 | 0 | 0.15298 | 3304.4576 | 12:43 | 1.6752 | 1.5399 | 0.13531 | 1.7972e-05 | 0
[13 empty] | 12:43 | 1.0298 | 0.91146 | 0.91784 |  | 12:43 | 0 | 0.15298 | 3304.4576 | 12:43 | 1.6758 | 1.5405 | 0.13536 | 1.7979e-05 | 0
[13 empty] | 12:44 | 1.0164 | 0.91146 | 0.91784 |  | 12:44 | 0 | 0.15298 | 3304.4576 | 12:44 | 1.6765 | 1.541 | 0.13541 | 1.7986e-05 | 0
[13 empty] | 12:44 | 1.0034 | 0.91146 | 0.91784 |  | 12:44 | 0 | 0.15298 | 3304.4576 | 12:44 | 1.6771 | 1.5416 | 0.13546 | 1.7992e-05 | 0
[13 empty] | 12:44 | 0.99062 | 0.91146 | 0.91784 |  | 12:44 | 0 | 0.15298 | 3304.4576 | 12:44 | 1.6777 | 1.5421 | 0.13551 | 1.7999e-05 | 0
[13 empty] | 12:45 | 0.97811 | 0.91146 | 0.91784 |  | 12:45 | 0 | 0.15298 | 3304.4576 | 12:45 | 1.6782 | 1.5427 | 0.13556 | 1.8005e-05 | 0
[13 empty] | 12:45 | 0.96585 | 0.91146 | 0.91784 |  | 12:45 | 0 | 0.15298 | 3304.4576 | 12:45 | 1.6788 | 1.5432 | 0.1356 | 1.8011e-05 | 0
[13 empty] | 12:45 | 0.95385 | 0.91146 | 0.91784 |  | 12:45 | 0 | 0.15298 | 3304.4576 | 12:45 | 1.6794 | 1.5437 | 0.13565 | 1.8017e-05 | 0
[13 empty] | 12:45 | 0.94209 | 0.91146 | 0.91784 |  | 12:45 | 0 | 0.15298 | 3304.4576 | 12:45 | 1.68 | 1.5443 | 0.1357 | 1.8023e-05 | 0
[13 empty] | 12:45 | 0.93058 | 0.91146 | 0.91784 |  | 12:45 | 0 | 0.15298 | 3304.4576 | 12:45 | 1.6805 | 1.5448 | 0.13574 | 1.8029e-05 | 0
[13 empty] | 12:46 | 0.9193 | 0.91146 | 0.91784 |  | 12:46 | 0 | 0.15298 | 3304.4576 | 12:46 | 1.6811 | 1.5453 | 0.13579 | 1.8035e-05 | 0
[13 empty] | 12:46 | 0.90825 | 0.91146 | 0.91784 |  | 12:46 | 0 | 0.15298 | 3304.4576 | 12:46 | 1.6817 | 1.5458 | 0.13583 | 1.8041e-05 | 0
[13 empty] | 12:46 | 0.89743 | 0.91146 | 0.91784 |  | 12:46 | 0 | 0.15298 | 3304.4576 | 12:46 | 1.6822 | 1.5463 | 0.13588 | 1.8047e-05 | 0
[13 empty] | 12:47 | 0.88683 | 0.91146 | 0.91784 |  | 12:47 | 0 | 0.15298 | 3304.4576 | 12:47 | 1.6827 | 1.5468 | 0.13592 | 1.8053e-05 | 0
[13 empty] | 12:47 | 0.87645 | 0.91146 | 0.91784 |  | 12:47 | 0 | 0.15298 | 3304.4576 | 12:47 | 1.6833 | 1.5473 | 0.13596 | 1.8059e-05 | 0
[13 empty] | 12:47 | 0.86628 | 0.91146 | 0.91784 |  | 12:47 | 0 | 0.15298 | 3304.4576 | 12:47 | 1.6838 | 1.5478 | 0.136 | 1.8064e-05 | 0
[13 empty] | 12:47 | 0.85633 | 0.91146 | 0.91784 |  | 12:47 | 0 | 0.15298 | 3304.4576 | 12:47 | 1.6843 | 1.5482 | 0.13605 | 1.807e-05 | 0
[13 empty] | 12:47 | 0.84657 | 0.91146 | 0.91784 |  | 12:47 | 0 | 0.15298 | 3304.4576 | 12:47 | 1.6848 | 1.5487 | 0.13609 | 1.8075e-05 | 0
[13 empty] | 12:48 | 0.83702 | 0.91146 | 0.91784 |  | 12:48 | 0 | 0.15298 | 3304.4576 | 12:48 | 1.6853 | 1.5492 | 0.13613 | 1.8081e-05 | 0
[13 empty] | 12:48 | 0.82766 | 0.91146 | 0.91784 |  | 12:48 | 0 | 0.15298 | 3304.4576 | 12:48 | 1.6858 | 1.5496 | 0.13617 | 1.8086e-05 | 0
[13 empty] | 12:48 | 0.8185 | 0.91146 | 0.91784 |  | 12:48 | 0 | 0.15298 | 3304.4576 | 12:48 | 1.6863 | 1.5501 | 0.13621 | 1.8091e-05 | 0
[13 empty] | 12:49 | 0.80952 | 0.91146 | 0.91784 |  | 12:49 | 0 | 0.15298 | 3304.4576 | 12:49 | 1.6868 | 1.5505 | 0.13625 | 1.8097e-05 | 0
[13 empty] | 12:49 | 0.80073 | 0.91146 | 0.91784 |  | 12:49 | 0 | 0.15298 | 3304.4576 | 12:49 | 1.6873 | 1.551 | 0.13629 | 1.8102e-05 | 0
[13 empty] | 12:49 | 0.79211 | 0.91146 | 0.91784 |  | 12:49 | 0 | 0.15298 | 3304.4576 | 12:49 | 1.6878 | 1.5514 | 0.13633 | 1.8107e-05 | 0
[13 empty] | 12:49 | 0.78368 | 0.91146 | 0.91784 |  | 12:49 | 0 | 0.15298 | 3304.4576 | 12:49 | 1.6883 | 1.5519 | 0.13636 | 1.8112e-05 | 0
[13 empty] | 12:49 | 0.77542 | 0.91146 | 0.91784 |  | 12:49 | 0 | 0.15298 | 3304.4576 | 12:49 | 1.6887 | 1.5523 | 0.1364 | 1.8117e-05 | 0
[13 empty] | 12:50 | 0.76733 | 0.91146 | 0.91784 |  | 12:50 | 0 | 0.15298 | 3304.4576 | 12:50 | 1.6892 | 1.5527 | 0.13644 | 1.8122e-05 | 0
[13 empty] | 12:50 | 0.7594 | 0.91146 | 0.91784 |  | 12:50 | 0 | 0.15298 | 3304.4576 | 12:50 | 1.6896 | 1.5532 | 0.13648 | 1.8127e-05 | 0
[13 empty] | 12:50 | 0.75164 | 0.91146 | 0.91784 |  | 12:50 | 0 | 0.15298 | 3304.4576 | 12:50 | 1.6901 | 1.5536 | 0.13651 | 1.8132e-05 | 0
[13 empty] | 12:51 | 0.74403 | 0.91146 | 0.91784 |  | 12:51 | 0 | 0.15298 | 3304.4576 | 12:51 | 1.6905 | 1.554 | 0.13655 | 1.8137e-05 | 0
[13 empty] | 12:51 | 0.73658 | 0.91146 | 0.91784 |  | 12:51 | 0 | 0.15298 | 3304.4576 | 12:51 | 1.691 | 1.5544 | 0.13659 | 1.8142e-05 | 0
[13 empty] | 12:51 | 0.72929 | 0.91146 | 0.91784 |  | 12:51 | 0 | 0.15298 | 3304.4576 | 12:51 | 1.6914 | 1.5548 | 0.13662 | 1.8146e-05 | 0
[13 empty] | 12:51 | 1.1629 | 0.91146 | 0.91784 |  | 12:51 | 0 | 0.15298 | 3304.4576 | 12:51 | 1.6921 | 1.5554 | 0.13668 | 1.8154e-05 | 0
[13 empty] | 12:51 | 1.1468 | 0.91146 | 0.91784 |  | 12:51 | 0 | 0.15298 | 3304.4576 | 12:51 | 1.6928 | 1.5561 | 0.13673 | 1.8161e-05 | 0
[13 empty] | 12:52 | 1.1311 | 0.91146 | 0.91784 |  | 12:52 | 0 | 0.15298 | 3304.4576 | 12:52 | 1.6935 | 1.5567 | 0.13679 | 1.8169e-05 | 0
[13 empty] | 12:52 | 1.1157 | 0.91146 | 0.91784 |  | 12:52 | 0 | 0.15298 | 3304.4576 | 12:52 | 1.6942 | 1.5573 | 0.13684 | 1.8176e-05 | 0
[13 empty] | 12:52 | 1.1006 | 0.91146 | 0.91784 |  | 12:52 | 0 | 0.15298 | 3304.4576 | 12:52 | 1.6949 | 1.5579 | 0.1369 | 1.8183e-05 | 0
[13 empty] | 12:52 | 1.0859 | 0.91146 | 0.91784 |  | 12:52 | 0 | 0.15298 | 3304.4576 | 12:52 | 1.6955 | 1.5586 | 0.13695 | 1.819e-05 | 0
[13 empty] | 12:53 | 1.0714 | 0.91146 | 0.91784 |  | 12:53 | 0 | 0.15298 | 3304.4576 | 12:53 | 1.6962 | 1.5592 | 0.137 | 1.8197e-05 | 0
[13 empty] | 12:53 | 1.0572 | 0.91146 | 0.91784 |  | 12:53 | 0 | 0.15298 | 3304.4576 | 12:53 | 1.6968 | 1.5597 | 0.13706 | 1.8204e-05 | 0
[13 empty] | 12:53 | 1.0434 | 0.91146 | 0.91784 |  | 12:53 | 0 | 0.15298 | 3304.4576 | 12:53 | 1.6974 | 1.5603 | 0.13711 | 1.8211e-05 | 0
[13 empty] | 12:54 | 1.0298 | 0.91146 | 0.91784 |  | 12:54 | 0 | 0.15298 | 3304.4576 | 12:54 | 1.6981 | 1.5609 | 0.13716 | 1.8217e-05 | 0
[13 empty] | 12:54 | 1.0164 | 0.91146 | 0.91784 |  | 12:54 | 0 | 0.15298 | 3304.4576 | 12:54 | 1.6987 | 1.5615 | 0.13721 | 1.8224e-05 | 0
[13 empty] | 12:54 | 1.0034 | 0.91146 | 0.91784 |  | 12:54 | 0 | 0.15298 | 3304.4576 | 12:54 | 1.6993 | 1.562 | 0.13726 | 1.8231e-05 | 0
[13 empty] | 12:54 | 0.99062 | 0.91146 | 0.91784 |  | 12:54 | 0 | 0.15298 | 3304.4576 | 12:54 | 1.6999 | 1.5626 | 0.1373 | 1.8237e-05 | 0
[13 empty] | 12:54 | 0.97811 | 0.91146 | 0.91784 |  | 12:54 | 0 | 0.15298 | 3304.4576 | 12:54 | 1.7005 | 1.5631 | 0.13735 | 1.8243e-05 | 0
[13 empty] | 12:55 | 0.96585 | 0.91146 | 0.91784 |  | 12:55 | 0 | 0.15298 | 3304.4576 | 12:55 | 1.7011 | 1.5636 | 0.1374 | 1.825e-05 | 0
[13 empty] | 12:55 | 0.95385 | 0.91146 | 0.91784 |  | 12:55 | 0 | 0.15298 | 3304.4576 | 12:55 | 1.7016 | 1.5642 | 0.13744 | 1.8256e-05 | 0
[13 empty] | 12:55 | 0.94209 | 0.91146 | 0.91784 |  | 12:55 | 0 | 0.15298 | 3304.4576 | 12:55 | 1.7022 | 1.5647 | 0.13749 | 1.8262e-05 | 0
[13 empty] | 12:56 | 0.93058 | 0.91146 | 0.91784 |  | 12:56 | 0 | 0.15298 | 3304.4576 | 12:56 | 1.7028 | 1.5652 | 0.13754 | 1.8268e-05 | 0
[13 empty] | 12:56 | 0.9193 | 0.91146 | 0.91784 |  | 12:56 | 0 | 0.15298 | 3304.4576 | 12:56 | 1.7033 | 1.5657 | 0.13758 | 1.8274e-05 | 0
[13 empty] | 12:56 | 0.90825 | 0.91146 | 0.91784 |  | 12:56 | 0 | 0.15298 | 3304.4576 | 12:56 | 1.7039 | 1.5662 | 0.13763 | 1.828e-05 | 0
[13 empty] | 12:56 | 0.89743 | 0.91146 | 0.91784 |  | 12:56 | 0 | 0.15298 | 3304.4576 | 12:56 | 1.7044 | 1.5667 | 0.13767 | 1.8286e-05 | 0
[13 empty] | 12:56 | 0.88683 | 0.91146 | 0.91784 |  | 12:56 | 0 | 0.15298 | 3304.4576 | 12:56 | 1.705 | 1.5672 | 0.13771 | 1.8291e-05 | 0
[13 empty] | 12:57 | 0.87645 | 0.91146 | 0.91784 |  | 12:57 | 0 | 0.15298 | 3304.4576 | 12:57 | 1.7055 | 1.5677 | 0.13776 | 1.8297e-05 | 0
[13 empty] | 12:57 | 0.86628 | 0.91146 | 0.91784 |  | 12:57 | 0 | 0.15298 | 3304.4576 | 12:57 | 1.706 | 1.5682 | 0.1378 | 1.8303e-05 | 0
[13 empty] | 12:57 | 0.85633 | 0.91146 | 0.91784 |  | 12:57 | 0 | 0.15298 | 3304.4576 | 12:57 | 1.7065 | 1.5687 | 0.13784 | 1.8308e-05 | 0
[13 empty] | 12:58 | 0.84657 | 0.91146 | 0.91784 |  | 12:58 | 0 | 0.15298 | 3304.4576 | 12:58 | 1.707 | 1.5691 | 0.13788 | 1.8314e-05 | 0
[13 empty] | 12:58 | 0.83702 | 0.91146 | 0.91784 |  | 12:58 | 0 | 0.15298 | 3304.4576 | 12:58 | 1.7076 | 1.5696 | 0.13792 | 1.8319e-05 | 0
[13 empty] | 12:58 | 0.82766 | 0.91146 | 0.91784 |  | 12:58 | 0 | 0.15298 | 3304.4576 | 12:58 | 1.7081 | 1.5701 | 0.13796 | 1.8325e-05 | 0
[13 empty] | 12:58 | 0.8185 | 0.91146 | 0.91784 |  | 12:58 | 0 | 0.15298 | 3304.4576 | 12:58 | 1.7086 | 1.5705 | 0.138 | 1.833e-05 | 0
[13 empty] | 12:58 | 0.80952 | 0.91146 | 0.91784 |  | 12:58 | 0 | 0.15298 | 3304.4576 | 12:58 | 1.709 | 1.571 | 0.13804 | 1.8335e-05 | 0
[13 empty] | 12:59 | 0.80073 | 0.91146 | 0.91784 |  | 12:59 | 0 | 0.15298 | 3304.4576 | 12:59 | 1.7095 | 1.5714 | 0.13808 | 1.834e-05 | 0
[13 empty] | 12:59 | 0.79211 | 0.91146 | 0.91784 |  | 12:59 | 0 | 0.15298 | 3304.4576 | 12:59 | 1.71 | 1.5719 | 0.13812 | 1.8346e-05 | 0
[13 empty] | 12:59 | 0.78368 | 0.91146 | 0.91784 |  | 12:59 | 0 | 0.15298 | 3304.4576 | 12:59 | 1.7105 | 1.5723 | 0.13816 | 1.8351e-05 | 0
[13 empty] | 13:00 | 0.77542 | 0.91146 | 0.91784 |  | 13:00 | 0 | 0.15298 | 3304.4576 | 13:00 | 1.7109 | 1.5727 | 0.1382 | 1.8356e-05 | 0
[13 empty] | 13:00 | 0.76733 | 0.91146 | 0.91784 |  | 13:00 | 0 | 0.15298 | 3304.4576 | 13:00 | 1.7114 | 1.5732 | 0.13823 | 1.8361e-05 | 0
[13 empty] | 13:00 | 0.7594 | 0.91146 | 0.91784 |  | 13:00 | 0 | 0.15298 | 3304.4576 | 13:00 | 1.7119 | 1.5736 | 0.13827 | 1.8366e-05 | 0
[13 empty] | 13:00 | 0.75164 | 0.91146 | 0.91784 |  | 13:00 | 0.75552 | 0.15298 | 3310.1299 | 13:00 | 1.7123 | 1.574 | 0.13831 | 1.837e-05 | 0
[13 empty] | 13:00 | 0.74403 | 0.91146 | 0.91784 |  | 13:00 | 0.74784 | 0.15298 | 3321.3981 | 13:00 | 1.7128 | 1.5744 | 0.13834 | 1.8375e-05 | 0
[13 empty] | 13:01 | 0.73658 | 0.91146 | 0.91784 |  | 13:01 | 0.74031 | 0.15298 | 3332.5517 | 13:01 | 1.7132 | 1.5748 | 0.13838 | 1.838e-05 | 0
[13 empty] | 13:01 | 0.72929 | 0.91146 | 0.91784 |  | 13:01 | 0.73294 | 0.15298 | 3343.6097 | 13:01 | 1.7137 | 1.5752 | 0.13842 | 1.8385e-05 | 0
[13 empty] | 13:01 | 1.1629 | 0.91146 | 0.91784 |  | 13:01 | 0.94609 | 0.15298 | 3356.1957 | 13:01 | 1.7144 | 1.5759 | 0.13847 | 1.8392e-05 | 0
[13 empty] | 13:02 | 1.1468 | 0.91146 | 0.91784 |  | 13:02 | 1.1549 | 0.15298 | 3371.952 | 13:02 | 1.7151 | 1.5765 | 0.13853 | 1.84e-05 | 0
[13 empty] | 13:02 | 1.1311 | 0.91146 | 0.91784 |  | 13:02 | 1.139 | 0.15298 | 3389.1599 | 13:02 | 1.7157 | 1.5771 | 0.13859 | 1.8407e-05 | 0
[13 empty] | 13:02 | 1.1157 | 0.91146 | 0.91784 |  | 13:02 | 1.1234 | 0.15298 | 3406.1194 | 13:02 | 1.7164 | 1.5778 | 0.13864 | 1.8414e-05 | 0
[13 empty] | 13:02 | 1.1006 | 0.91146 | 0.91784 |  | 13:02 | 1.1082 | 0.15298 | 3422.8689 | 13:02 | 1.7171 | 1.5784 | 0.13869 | 1.8422e-05 | 0
[13 empty] | 13:02 | 1.0859 | 0.91146 | 0.91784 |  | 13:02 | 1.0933 | 0.15298 | 3439.3701 | 13:02 | 1.7177 | 1.579 | 0.13875 | 1.8429e-05 | 0
[13 empty] | 13:03 | 1.0714 | 0.91146 | 0.91784 |  | 13:03 | 1.0786 | 0.15298 | 3455.6612 | 13:03 | 1.7184 | 1.5796 | 0.1388 | 1.8435e-05 | 0
[13 empty] | 13:03 | 1.0572 | 0.91146 | 0.91784 |  | 13:03 | 1.0643 | 0.15298 | 3471.7422 | 13:03 | 1.719 | 1.5802 | 0.13885 | 1.8442e-05 | 0
[13 empty] | 13:03 | 1.0434 | 0.91146 | 0.91784 |  | 13:03 | 1.0503 | 0.15298 | 3487.594 | 13:03 | 1.7197 | 1.5808 | 0.1389 | 1.8449e-05 | 0
[13 empty] | 13:04 | 1.0298 | 0.91146 | 0.91784 |  | 13:04 | 1.0366 | 0.15298 | 3503.2549 | 13:04 | 1.7203 | 1.5813 | 0.13895 | 1.8456e-05 | 0
[13 empty] | 13:04 | 1.0164 | 0.91146 | 0.91784 |  | 13:04 | 1.0231 | 0.15298 | 3518.7056 | 13:04 | 1.7209 | 1.5819 | 0.139 | 1.8462e-05 | 0
[13 empty] | 13:04 | 1.0034 | 0.91146 | 0.91784 |  | 13:04 | 1.0099 | 0.15298 | 3533.9463 | 13:04 | 1.7215 | 1.5825 | 0.13905 | 1.8469e-05 | 0
[13 empty] | 13:04 | 0.99062 | 0.91146 | 0.91784 |  | 13:04 | 0.99701 | 0.15298 | 3548.996 | 13:04 | 1.7221 | 1.583 | 0.1391 | 1.8475e-05 | 0
[13 empty] | 13:04 | 0.97811 | 0.91146 | 0.91784 |  | 13:04 | 0.98437 | 0.15298 | 3563.8547 | 13:04 | 1.7227 | 1.5835 | 0.13915 | 1.8482e-05 | 0
[13 empty] | 13:05 | 0.96585 | 0.91146 | 0.91784 |  | 13:05 | 0.97198 | 0.15298 | 3578.5224 | 13:05 | 1.7233 | 1.5841 | 0.13919 | 1.8488e-05 | 0
[13 empty] | 13:05 | 0.95385 | 0.91146 | 0.91784 |  | 13:05 | 0.95985 | 0.15298 | 3593.0183 | 13:05 | 1.7239 | 1.5846 | 0.13924 | 1.8494e-05 | 0
[13 empty] | 13:05 | 0.94209 | 0.91146 | 0.91784 |  | 13:05 | 0.94797 | 0.15298 | 3607.3231 | 13:05 | 1.7244 | 1.5851 | 0.13929 | 1.85e-05 | 0
[13 empty] | 13:06 | 0.93058 | 0.91146 | 0.91784 |  | 13:06 | 0.93634 | 0.15298 | 3621.4561 | 13:06 | 1.725 | 1.5857 | 0.13933 | 1.8506e-05 | 0
[13 empty] | 13:06 | 0.9193 | 0.91146 | 0.91784 |  | 13:06 | 0.92494 | 0.15298 | 3635.4171 | 13:06 | 1.7256 | 1.5862 | 0.13938 | 1.8512e-05 | 0
[13 empty] | 13:06 | 0.90825 | 0.91146 | 0.91784 |  | 13:06 | 0.91377 | 0.15298 | 3649.2063 | 13:06 | 1.7261 | 1.5867 | 0.13942 | 1.8518e-05 | 0
[13 empty] | 13:06 | 0.89743 | 0.91146 | 0.91784 |  | 13:06 | 0.90284 | 0.15298 | 3662.8236 | 13:06 | 1.7267 | 1.5872 | 0.13947 | 1.8524e-05 | 0
[13 empty] | 13:06 | 0.88683 | 0.91146 | 0.91784 |  | 13:06 | 0.89213 | 0.15298 | 3676.2881 | 13:06 | 1.7272 | 1.5877 | 0.13951 | 1.853e-05 | 0
[13 empty] | 13:07 | 0.87645 | 0.91146 | 0.91784 |  | 13:07 | 0.88164 | 0.15298 | 3689.5998 | 13:07 | 1.7277 | 1.5881 | 0.13955 | 1.8536e-05 | 0
[13 empty] | 13:07 | 0.86628 | 0.91146 | 0.91784 |  | 13:07 | 0.87137 | 0.15298 | 3702.7397 | 13:07 | 1.7283 | 1.5886 | 0.13959 | 1.8541e-05 | 0
[13 empty] | 13:07 | 0.85633 | 0.91146 | 0.91784 |  | 13:07 | 0.8613 | 0.15298 | 3715.7458 | 13:07 | 1.7288 | 1.5891 | 0.13964 | 1.8547e-05 | 0
[13 empty] | 13:08 | 0.84657 | 0.91146 | 0.91784 |  | 13:08 | 0.85145 | 0.15298 | 3728.5801 | 13:08 | 1.7293 | 1.5896 | 0.13968 | 1.8552e-05 | 0
[13 empty] | 13:08 | 0.83702 | 0.91146 | 0.91784 |  | 13:08 | 0.8418 | 0.15298 | 3741.2806 | 13:08 | 1.7298 | 1.5901 | 0.13972 | 1.8558e-05 | 0
[13 empty] | 13:08 | 0.82766 | 0.91146 | 0.91784 |  | 13:08 | 0.83234 | 0.15298 | 3753.8475 | 13:08 | 1.7303 | 1.5905 | 0.13976 | 1.8563e-05 | 0
[13 empty] | 13:08 | 0.8185 | 0.91146 | 0.91784 |  | 13:08 | 0.82308 | 0.15298 | 3766.2616 | 13:08 | 1.7308 | 1.591 | 0.1398 | 1.8568e-05 | 0
[13 empty] | 13:08 | 0.80952 | 0.91146 | 0.91784 |  | 13:08 | 0.81401 | 0.15298 | 3778.542 | 13:08 | 1.7313 | 1.5914 | 0.13984 | 1.8574e-05 | 0
[13 empty] | 13:09 | 0.80073 | 0.91146 | 0.91784 |  | 13:09 | 0.80512 | 0.15298 | 3790.6887 | 13:09 | 1.7317 | 1.5918 | 0.13988 | 1.8579e-05 | 0
[13 empty] | 13:09 | 0.79211 | 0.91146 | 0.91784 |  | 13:09 | 0.79642 | 0.15298 | 3802.6826 | 13:09 | 1.7322 | 1.5923 | 0.13992 | 1.8584e-05 | 0
[13 empty] | 13:09 | 0.78368 | 0.91146 | 0.91784 |  | 13:09 | 0.7879 | 0.15298 | 3814.581 | 13:09 | 1.7327 | 1.5927 | 0.13995 | 1.8589e-05 | 0
[13 empty] | 13:10 | 0.77542 | 0.91146 | 0.91784 |  | 13:10 | 0.77955 | 0.15298 | 3826.3267 | 13:10 | 1.7332 | 1.5932 | 0.13999 | 1.8594e-05 | 0
[13 empty] | 13:10 | 0.76733 | 0.91146 | 0.91784 |  | 13:10 | 0.77137 | 0.15298 | 3837.9577 | 13:10 | 1.7336 | 1.5936 | 0.14003 | 1.8599e-05 | 0
[13 empty] | 13:10 | 0.7594 | 0.91146 | 0.91784 |  | 13:10 | 0.76336 | 0.15298 | 3849.4742 | 13:10 | 1.7341 | 1.594 | 0.14007 | 1.8604e-05 | 0
[13 empty] | 13:10 | 0.75164 | 0.91146 | 0.91784 |  | 13:10 | 0 | 0.15298 | 3855.2037 | 13:10 | 1.7345 | 1.5944 | 0.1401 | 1.8609e-05 | 0
[13 empty] | 13:10 | 0.74403 | 0.91146 | 0.91784 |  | 13:10 | 0 | 0.15298 | 3855.2037 | 13:10 | 1.735 | 1.5948 | 0.14014 | 1.8614e-05 | 0
[13 empty] | 13:11 | 0.73658 | 0.91146 | 0.91784 |  | 13:11 | 0 | 0.15298 | 3855.2037 | 13:11 | 1.7355 | 1.5953 | 0.14018 | 1.8618e-05 | 0
[13 empty] | 13:11 | 0.72929 | 0.91146 | 0.91784 |  | 13:11 | 0 | 0.15298 | 3855.2037 | 13:11 | 1.7359 | 1.5957 | 0.14021 | 1.8623e-05 | 0
[13 empty] | 13:11 | 1.1629 | 0.91146 | 0.91784 |  | 13:11 | 0 | 0.15298 | 3855.2037 | 13:11 | 1.7366 | 1.5963 | 0.14027 | 1.8631e-05 | 0
[13 empty] | 13:12 | 1.1468 | 0.91146 | 0.91784 |  | 13:12 | 0 | 0.15298 | 3855.2037 | 13:12 | 1.7373 | 1.5969 | 0.14033 | 1.8638e-05 | 0
[13 empty] | 13:12 | 1.1311 | 0.91146 | 0.91784 |  | 13:12 | 0 | 0.15298 | 3855.2037 | 13:12 | 1.738 | 1.5976 | 0.14038 | 1.8646e-05 | 0
[13 empty] | 13:12 | 1.1157 | 0.91146 | 0.91784 |  | 13:12 | 0 | 0.15298 | 3855.2037 | 13:12 | 1.7387 | 1.5982 | 0.14043 | 1.8653e-05 | 0
[13 empty] | 13:12 | 1.1006 | 0.91146 | 0.91784 |  | 13:12 | 0 | 0.15298 | 3855.2037 | 13:12 | 1.7393 | 1.5988 | 0.14049 | 1.866e-05 | 0
[13 empty] | 13:12 | 1.0859 | 0.91146 | 0.91784 |  | 13:12 | 0 | 0.15298 | 3855.2037 | 13:12 | 1.74 | 1.5994 | 0.14054 | 1.8667e-05 | 0
[13 empty] | 13:13 | 1.0714 | 0.91146 | 0.91784 |  | 13:13 | 0 | 0.15298 | 3855.2037 | 13:13 | 1.7406 | 1.6 | 0.14059 | 1.8674e-05 | 0
[13 empty] | 13:13 | 1.0572 | 0.91146 | 0.91784 |  | 13:13 | 0 | 0.15298 | 3855.2037 | 13:13 | 1.7413 | 1.6006 | 0.14065 | 1.8681e-05 | 0
[13 empty] | 13:13 | 1.0434 | 0.91146 | 0.91784 |  | 13:13 | 0 | 0.15298 | 3855.2037 | 13:13 | 1.7419 | 1.6012 | 0.1407 | 1.8688e-05 | 0
[13 empty] | 13:14 | 1.0298 | 0.91146 | 0.91784 |  | 13:14 | 0 | 0.15298 | 3855.2037 | 13:14 | 1.7425 | 1.6018 | 0.14075 | 1.8694e-05 | 0
[13 empty] | 13:14 | 1.0164 | 0.91146 | 0.91784 |  | 13:14 | 0 | 0.15298 | 3855.2037 | 13:14 | 1.7431 | 1.6023 | 0.1408 | 1.8701e-05 | 0
[13 empty] | 13:14 | 1.0034 | 0.91146 | 0.91784 |  | 13:14 | 0 | 0.15298 | 3855.2037 | 13:14 | 1.7438 | 1.6029 | 0.14085 | 1.8707e-05 | 0
[13 empty] | 13:14 | 0.99062 | 0.91146 | 0.91784 |  | 13:14 | 0 | 0.15298 | 3855.2037 | 13:14 | 1.7443 | 1.6034 | 0.14089 | 1.8714e-05 | 0
[13 empty] | 13:14 | 0.97811 | 0.91146 | 0.91784 |  | 13:14 | 0 | 0.15298 | 3855.2037 | 13:14 | 1.7449 | 1.604 | 0.14094 | 1.872e-05 | 0
[13 empty] | 13:15 | 0.96585 | 0.91146 | 0.91784 |  | 13:15 | 0 | 0.15298 | 3855.2037 | 13:15 | 1.7455 | 1.6045 | 0.14099 | 1.8727e-05 | 0
[13 empty] | 13:15 | 0.95385 | 0.91146 | 0.91784 |  | 13:15 | 0 | 0.15298 | 3855.2037 | 13:15 | 1.7461 | 1.605 | 0.14104 | 1.8733e-05 | 0
[13 empty] | 13:15 | 0.94209 | 0.91146 | 0.91784 |  | 13:15 | 0 | 0.15298 | 3855.2037 | 13:15 | 1.7467 | 1.6056 | 0.14108 | 1.8739e-05 | 0
[13 empty] | 13:16 | 0.93058 | 0.91146 | 0.91784 |  | 13:16 | 0 | 0.15298 | 3855.2037 | 13:16 | 1.7472 | 1.6061 | 0.14113 | 1.8745e-05 | 0
[13 empty] | 13:16 | 0.9193 | 0.91146 | 0.91784 |  | 13:16 | 0 | 0.15298 | 3855.2037 | 13:16 | 1.7478 | 1.6066 | 0.14117 | 1.8751e-05 | 0
[13 empty] | 13:16 | 0.90825 | 0.91146 | 0.91784 |  | 13:16 | 0 | 0.15298 | 3855.2037 | 13:16 | 1.7483 | 1.6071 | 0.14122 | 1.8757e-05 | 0
[13 empty] | 13:16 | 0.89743 | 0.91146 | 0.91784 |  | 13:16 | 0 | 0.15298 | 3855.2037 | 13:16 | 1.7489 | 1.6076 | 0.14126 | 1.8763e-05 | 0
[13 empty] | 13:16 | 0.88683 | 0.91146 | 0.91784 |  | 13:16 | 0 | 0.15298 | 3855.2037 | 13:16 | 1.7494 | 1.6081 | 0.1413 | 1.8768e-05 | 0
[13 empty] | 13:17 | 0.87645 | 0.91146 | 0.91784 |  | 13:17 | 0 | 0.15298 | 3855.2037 | 13:17 | 1.7499 | 1.6086 | 0.14135 | 1.8774e-05 | 0
[13 empty] | 13:17 | 0.86628 | 0.91146 | 0.91784 |  | 13:17 | 0 | 0.15298 | 3855.2037 | 13:17 | 1.7505 | 1.6091 | 0.14139 | 1.878e-05 | 0
[13 empty] | 13:17 | 0.85633 | 0.91146 | 0.91784 |  | 13:17 | 0 | 0.15298 | 3855.2037 | 13:17 | 1.751 | 1.6095 | 0.14143 | 1.8785e-05 | 0
[13 empty] | 13:18 | 0.84657 | 0.91146 | 0.91784 |  | 13:18 | 0 | 0.15298 | 3855.2037 | 13:18 | 1.7515 | 1.61 | 0.14147 | 1.8791e-05 | 0
[13 empty] | 13:18 | 0.83702 | 0.91146 | 0.91784 |  | 13:18 | 0 | 0.15298 | 3855.2037 | 13:18 | 1.752 | 1.6105 | 0.14151 | 1.8796e-05 | 0
[13 empty] | 13:18 | 0.82766 | 0.91146 | 0.91784 |  | 13:18 | 0 | 0.15298 | 3855.2037 | 13:18 | 1.7525 | 1.6109 | 0.14155 | 1.8802e-05 | 0
[13 empty] | 13:18 | 0.8185 | 0.91146 | 0.91784 |  | 13:18 | 0 | 0.15298 | 3855.2037 | 13:18 | 1.753 | 1.6114 | 0.1416 | 1.8807e-05 | 0
[13 empty] | 13:18 | 0.80952 | 0.91146 | 0.91784 |  | 13:18 | 0 | 0.15298 | 3855.2037 | 13:18 | 1.7535 | 1.6118 | 0.14163 | 1.8812e-05 | 0
[13 empty] | 13:19 | 0.80073 | 0.91146 | 0.91784 |  | 13:19 | 0 | 0.15298 | 3855.2037 | 13:19 | 1.754 | 1.6123 | 0.14167 | 1.8817e-05 | 0
[13 empty] | 13:19 | 0.79211 | 0.91146 | 0.91784 |  | 13:19 | 0 | 0.15298 | 3855.2037 | 13:19 | 1.7545 | 1.6127 | 0.14171 | 1.8822e-05 | 0
[13 empty] | 13:19 | 0.78368 | 0.91146 | 0.91784 |  | 13:19 | 0 | 0.15298 | 3855.2037 | 13:19 | 1.7549 | 1.6132 | 0.14175 | 1.8828e-05 | 0
[13 empty] | 13:20 | 0.77542 | 0.91146 | 0.91784 |  | 13:20 | 0 | 0.15298 | 3855.2037 | 13:20 | 1.7554 | 1.6136 | 0.14179 | 1.8833e-05 | 0
[13 empty] | 13:20 | 0.76733 | 0.91146 | 0.91784 |  | 13:20 | 0 | 0.15298 | 3855.2037 | 13:20 | 1.7559 | 1.614 | 0.14183 | 1.8838e-05 | 0
[13 empty] | 13:20 | 0.7594 | 0.91146 | 0.91784 |  | 13:20 | 0 | 0.15298 | 3855.2037 | 13:20 | 1.7563 | 1.6144 | 0.14186 | 1.8842e-05 | 0
[13 empty] | 13:20 | 0.75164 | 0.91146 | 0.91784 |  | 13:20 | 0 | 0.15298 | 3855.2037 | 13:20 | 1.7568 | 1.6149 | 0.1419 | 1.8847e-05 | 0
[13 empty] | 13:20 | 0.74403 | 0.91146 | 0.91784 |  | 13:20 | 0 | 0.15298 | 3855.2037 | 13:20 | 1.7572 | 1.6153 | 0.14194 | 1.8852e-05 | 0
[13 empty] | 13:21 | 0.73658 | 0.91146 | 0.91784 |  | 13:21 | 0 | 0.15298 | 3855.2037 | 13:21 | 1.7577 | 1.6157 | 0.14197 | 1.8857e-05 | 0
[13 empty] | 13:21 | 0.72929 | 0.91146 | 0.91784 |  | 13:21 | 0 | 0.15298 | 3855.2037 | 13:21 | 1.7581 | 1.6161 | 0.14201 | 1.8862e-05 | 0
[13 empty] | 13:21 | 1.1629 | 0.91146 | 0.91784 |  | 13:21 | 0 | 0.15298 | 3855.2037 | 13:21 | 1.7588 | 1.6168 | 0.14206 | 1.8869e-05 | 0
[13 empty] | 13:22 | 1.1468 | 0.91146 | 0.91784 |  | 13:22 | 0 | 0.15298 | 3855.2037 | 13:22 | 1.7595 | 1.6174 | 0.14212 | 1.8877e-05 | 0
[13 empty] | 13:22 | 1.1311 | 0.91146 | 0.91784 |  | 13:22 | 0 | 0.15298 | 3855.2037 | 13:22 | 1.7602 | 1.618 | 0.14218 | 1.8884e-05 | 0
[13 empty] | 13:22 | 1.1157 | 0.91146 | 0.91784 |  | 13:22 | 0 | 0.15298 | 3855.2037 | 13:22 | 1.7609 | 1.6186 | 0.14223 | 1.8891e-05 | 0
[13 empty] | 13:22 | 1.1006 | 0.91146 | 0.91784 |  | 13:22 | 0 | 0.15298 | 3855.2037 | 13:22 | 1.7615 | 1.6192 | 0.14228 | 1.8898e-05 | 0
[13 empty] | 13:22 | 1.0859 | 0.91146 | 0.91784 |  | 13:22 | 0 | 0.15298 | 3855.2037 | 13:22 | 1.7622 | 1.6198 | 0.14234 | 1.8906e-05 | 0
[13 empty] | 13:23 | 1.0714 | 0.91146 | 0.91784 |  | 13:23 | 0 | 0.15298 | 3855.2037 | 13:23 | 1.7628 | 1.6204 | 0.14239 | 1.8912e-05 | 0
[13 empty] | 13:23 | 1.0572 | 0.91146 | 0.91784 |  | 13:23 | 0 | 0.15298 | 3855.2037 | 13:23 | 1.7635 | 1.621 | 0.14244 | 1.8919e-05 | 0
[13 empty] | 13:23 | 1.0434 | 0.91146 | 0.91784 |  | 13:23 | 0 | 0.15298 | 3855.2037 | 13:23 | 1.7641 | 1.6216 | 0.14249 | 1.8926e-05 | 0
[13 empty] | 13:24 | 1.0298 | 0.91146 | 0.91784 |  | 13:24 | 0 | 0.15298 | 3855.2037 | 13:24 | 1.7648 | 1.6222 | 0.14254 | 1.8933e-05 | 0
[13 empty] | 13:24 | 1.0164 | 0.91146 | 0.91784 |  | 13:24 | 0 | 0.15298 | 3855.2037 | 13:24 | 1.7654 | 1.6228 | 0.14259 | 1.894e-05 | 0
[13 empty] | 13:24 | 1.0034 | 0.91146 | 0.91784 |  | 13:24 | 0 | 0.15298 | 3855.2037 | 13:24 | 1.766 | 1.6233 | 0.14264 | 1.8946e-05 | 0
[13 empty] | 13:24 | 0.99062 | 0.91146 | 0.91784 |  | 13:24 | 0 | 0.15298 | 3855.2037 | 13:24 | 1.7666 | 1.6239 | 0.14269 | 1.8952e-05 | 0
[13 empty] | 13:24 | 0.97811 | 0.91146 | 0.91784 |  | 13:24 | 0 | 0.15298 | 3855.2037 | 13:24 | 1.7672 | 1.6244 | 0.14274 | 1.8959e-05 | 0
[13 empty] | 13:25 | 0.96585 | 0.91146 | 0.91784 |  | 13:25 | 0 | 0.15298 | 3855.2037 | 13:25 | 1.7678 | 1.6249 | 0.14278 | 1.8965e-05 | 0
[13 empty] | 13:25 | 0.95385 | 0.91146 | 0.91784 |  | 13:25 | 0 | 0.15298 | 3855.2037 | 13:25 | 1.7683 | 1.6255 | 0.14283 | 1.8971e-05 | 0
[13 empty] | 13:25 | 0.94209 | 0.91146 | 0.91784 |  | 13:25 | 0 | 0.15298 | 3855.2037 | 13:25 | 1.7689 | 1.626 | 0.14288 | 1.8977e-05 | 0
[13 empty] | 13:26 | 0.93058 | 0.91146 | 0.91784 |  | 13:26 | 0 | 0.15298 | 3855.2037 | 13:26 | 1.7695 | 1.6265 | 0.14292 | 1.8983e-05 | 0
[13 empty] | 13:26 | 0.9193 | 0.91146 | 0.91784 |  | 13:26 | 0 | 0.15298 | 3855.2037 | 13:26 | 1.77 | 1.627 | 0.14297 | 1.8989e-05 | 0
[13 empty] | 13:26 | 0.90825 | 0.91146 | 0.91784 |  | 13:26 | 0 | 0.15298 | 3855.2037 | 13:26 | 1.7706 | 1.6275 | 0.14301 | 1.8995e-05 | 0
[13 empty] | 13:26 | 0.89743 | 0.91146 | 0.91784 |  | 13:26 | 0 | 0.15298 | 3855.2037 | 13:26 | 1.7711 | 1.628 | 0.14306 | 1.9001e-05 | 0
[13 empty] | 13:26 | 0.88683 | 0.91146 | 0.91784 |  | 13:26 | 0 | 0.15298 | 3855.2037 | 13:26 | 1.7716 | 1.6285 | 0.1431 | 1.9007e-05 | 0
[13 empty] | 13:27 | 0.87645 | 0.91146 | 0.91784 |  | 13:27 | 0 | 0.15298 | 3855.2037 | 13:27 | 1.7722 | 1.629 | 0.14314 | 1.9012e-05 | 0
[13 empty] | 13:27 | 0.86628 | 0.91146 | 0.91784 |  | 13:27 | 0 | 0.15298 | 3855.2037 | 13:27 | 1.7727 | 1.6295 | 0.14318 | 1.9018e-05 | 0
[13 empty] | 13:27 | 0.85633 | 0.91146 | 0.91784 |  | 13:27 | 0 | 0.15298 | 3855.2037 | 13:27 | 1.7732 | 1.63 | 0.14323 | 1.9024e-05 | 0
[13 empty] | 13:28 | 0.84657 | 0.91146 | 0.91784 |  | 13:28 | 0 | 0.15298 | 3855.2037 | 13:28 | 1.7737 | 1.6304 | 0.14327 | 1.9029e-05 | 0
[13 empty] | 13:28 | 0.83702 | 0.91146 | 0.91784 |  | 13:28 | 0 | 0.15298 | 3855.2037 | 13:28 | 1.7742 | 1.6309 | 0.14331 | 1.9035e-05 | 0
[13 empty] | 13:28 | 0.82766 | 0.91146 | 0.91784 |  | 13:28 | 0 | 0.15298 | 3855.2037 | 13:28 | 1.7747 | 1.6314 | 0.14335 | 1.904e-05 | 0
[13 empty] | 13:28 | 0.8185 | 0.91146 | 0.91784 |  | 13:28 | 0 | 0.15298 | 3855.2037 | 13:28 | 1.7752 | 1.6318 | 0.14339 | 1.9045e-05 | 0
[13 empty] | 13:28 | 0.80952 | 0.91146 | 0.91784 |  | 13:28 | 0 | 0.15298 | 3855.2037 | 13:28 | 1.7757 | 1.6323 | 0.14343 | 1.9051e-05 | 0
[13 empty] | 13:29 | 0.80073 | 0.91146 | 0.91784 |  | 13:29 | 0 | 0.15298 | 3855.2037 | 13:29 | 1.7762 | 1.6327 | 0.14347 | 1.9056e-05 | 0
[13 empty] | 13:29 | 0.79211 | 0.91146 | 0.91784 |  | 13:29 | 0 | 0.15298 | 3855.2037 | 13:29 | 1.7767 | 1.6332 | 0.14351 | 1.9061e-05 | 0
[13 empty] | 13:29 | 0.78368 | 0.91146 | 0.91784 |  | 13:29 | 0 | 0.15298 | 3855.2037 | 13:29 | 1.7772 | 1.6336 | 0.14355 | 1.9066e-05 | 0
[13 empty] | 13:30 | 0.77542 | 0.91146 | 0.91784 |  | 13:30 | 0 | 0.15298 | 3855.2037 | 13:30 | 1.7776 | 1.634 | 0.14358 | 1.9071e-05 | 0
[13 empty] | 13:30 | 0.76733 | 0.91146 | 0.91784 |  | 13:30 | 0 | 0.15298 | 3855.2037 | 13:30 | 1.7781 | 1.6345 | 0.14362 | 1.9076e-05 | 0
[13 empty] | 13:30 | 0.7594 | 0.91146 | 0.91784 |  | 13:30 | 0 | 0.15298 | 3855.2037 | 13:30 | 1.7786 | 1.6349 | 0.14366 | 1.9081e-05 | 0
[13 empty] | 13:30 | 0.75164 | 0.91146 | 0.91784 |  | 13:30 | 0 | 0.15298 | 3855.2037 | 13:30 | 1.779 | 1.6353 | 0.14369 | 1.9086e-05 | 0
[13 empty] | 13:30 | 0.74403 | 0.91146 | 0.91784 |  | 13:30 | 0 | 0.15298 | 3855.2037 | 13:30 | 1.7795 | 1.6357 | 0.14373 | 1.9091e-05 | 0
[13 empty] | 13:31 | 0.73658 | 0.91146 | 0.91784 |  | 13:31 | 0 | 0.15298 | 3855.2037 | 13:31 | 1.7799 | 1.6361 | 0.14377 | 1.9096e-05 | 0
[13 empty] | 13:31 | 0.72929 | 0.91146 | 0.91784 |  | 13:31 | 0 | 0.15298 | 3855.2037 | 13:31 | 1.7803 | 1.6365 | 0.1438 | 1.9101e-05 | 0
[13 empty] | 13:31 | 1.1629 | 0.91146 | 0.91784 |  | 13:31 | 0 | 0.15298 | 3855.2037 | 13:31 | 1.781 | 1.6372 | 0.14386 | 1.9108e-05 | 0
[13 empty] | 13:32 | 1.1468 | 0.91146 | 0.91784 |  | 13:32 | 0 | 0.15298 | 3855.2037 | 13:32 | 1.7818 | 1.6378 | 0.14392 | 1.9116e-05 | 0
[13 empty] | 13:32 | 1.1311 | 0.91146 | 0.91784 |  | 13:32 | 0 | 0.15298 | 3855.2037 | 13:32 | 1.7824 | 1.6384 | 0.14397 | 1.9123e-05 | 0
[13 empty] | 13:32 | 1.1157 | 0.91146 | 0.91784 |  | 13:32 | 0 | 0.15298 | 3855.2037 | 13:32 | 1.7831 | 1.6391 | 0.14403 | 1.9129e-05 | 0
[13 empty] | 13:32 | 1.1006 | 0.91146 | 0.91784 |  | 13:32 | 0 | 0.15298 | 3855.2037 | 13:32 | 1.7838 | 1.6397 | 0.14408 | 1.9137e-05 | 0
[13 empty] | 13:32 | 1.0859 | 0.91146 | 0.91784 |  | 13:32 | 0 | 0.15298 | 3855.2037 | 13:32 | 1.7844 | 1.6403 | 0.14413 | 1.9144e-05 | 0
[13 empty] | 13:33 | 1.0714 | 0.91146 | 0.91784 |  | 13:33 | 0 | 0.15298 | 3855.2037 | 13:33 | 1.7851 | 1.6409 | 0.14418 | 1.915e-05 | 0
[13 empty] | 13:33 | 1.0572 | 0.91146 | 0.91784 |  | 13:33 | 0 | 0.15298 | 3855.2037 | 13:33 | 1.7857 | 1.6415 | 0.14424 | 1.9158e-05 | 0
[13 empty] | 13:33 | 1.0434 | 0.91146 | 0.91784 |  | 13:33 | 0 | 0.15298 | 3855.2037 | 13:33 | 1.7863 | 1.642 | 0.14429 | 1.9165e-05 | 0
[13 empty] | 13:34 | 1.0298 | 0.91146 | 0.91784 |  | 13:34 | 0 | 0.15298 | 3855.2037 | 13:34 | 1.787 | 1.6426 | 0.14434 | 1.9171e-05 | 0
[13 empty] | 13:34 | 1.0164 | 0.91146 | 0.91784 |  | 13:34 | 0 | 0.15298 | 3855.2037 | 13:34 | 1.7876 | 1.6432 | 0.14439 | 1.9179e-05 | 0
[13 empty] | 13:34 | 1.0034 | 0.91146 | 0.91784 |  | 13:34 | 0 | 0.15298 | 3855.2037 | 13:34 | 1.7882 | 1.6437 | 0.14444 | 1.9185e-05 | 0
[13 empty] | 13:34 | 0.99062 | 0.91146 | 0.91784 |  | 13:34 | 0 | 0.15298 | 3855.2037 | 13:34 | 1.7888 | 1.6443 | 0.14448 | 1.919e-05 | 0
[13 empty] | 13:34 | 0.97811 | 0.91146 | 0.91784 |  | 13:34 | 0 | 0.15298 | 3855.2037 | 13:34 | 1.7894 | 1.6448 | 0.14453 | 1.9198e-05 | 0
[13 empty] | 13:35 | 0.96585 | 0.91146 | 0.91784 |  | 13:35 | 0 | 0.15298 | 3855.2037 | 13:35 | 1.79 | 1.6454 | 0.14458 | 1.9204e-05 | 0
[13 empty] | 13:35 | 0.95385 | 0.91146 | 0.91784 |  | 13:35 | 0 | 0.15298 | 3855.2037 | 13:35 | 1.7906 | 1.6459 | 0.14463 | 1.9209e-05 | 0
[13 empty] | 13:35 | 0.94209 | 0.91146 | 0.91784 |  | 13:35 | 0 | 0.15298 | 3855.2037 | 13:35 | 1.7911 | 1.6464 | 0.14467 | 1.9215e-05 | 0
[13 empty] | 13:36 | 0.93058 | 0.91146 | 0.91784 |  | 13:36 | 0 | 0.15298 | 3855.2037 | 13:36 | 1.7917 | 1.6469 | 0.14472 | 1.9223e-05 | 0
[13 empty] | 13:36 | 0.9193 | 0.91146 | 0.91784 |  | 13:36 | 0 | 0.15298 | 3855.2037 | 13:36 | 1.7922 | 1.6475 | 0.14476 | 1.9228e-05 | 0
[13 empty] | 13:36 | 0.90825 | 0.91146 | 0.91784 |  | 13:36 | 0 | 0.15298 | 3855.2037 | 13:36 | 1.7928 | 1.648 | 0.14481 | 1.9234e-05 | 0
[13 empty] | 13:36 | 0.89743 | 0.91146 | 0.91784 |  | 13:36 | 0 | 0.15298 | 3855.2037 | 13:36 | 1.7933 | 1.6485 | 0.14485 | 1.924e-05 | 0
[13 empty] | 13:36 | 0.88683 | 0.91146 | 0.91784 |  | 13:36 | 0 | 0.15298 | 3855.2037 | 13:36 | 1.7939 | 1.649 | 0.1449 | 1.9246e-05 | 0
[13 empty] | 13:37 | 0.87645 | 0.91146 | 0.91784 |  | 13:37 | 0 | 0.15298 | 3855.2037 | 13:37 | 1.7944 | 1.6494 | 0.14494 | 1.9251e-05 | 0
[13 empty] | 13:37 | 0.86628 | 0.91146 | 0.91784 |  | 13:37 | 0 | 0.15298 | 3855.2037 | 13:37 | 1.7949 | 1.6499 | 0.14498 | 1.9257e-05 | 0
[13 empty] | 13:37 | 0.85633 | 0.91146 | 0.91784 |  | 13:37 | 0 | 0.15298 | 3855.2037 | 13:37 | 1.7954 | 1.6504 | 0.14502 | 1.9263e-05 | 0
[13 empty] | 13:38 | 0.84657 | 0.91146 | 0.91784 |  | 13:38 | 0 | 0.15298 | 3855.2037 | 13:38 | 1.796 | 1.6509 | 0.14506 | 1.9269e-05 | 0
[13 empty] | 13:38 | 0.83702 | 0.91146 | 0.91784 |  | 13:38 | 0 | 0.15298 | 3855.2037 | 13:38 | 1.7965 | 1.6513 | 0.14511 | 1.9272e-05 | 0
[13 empty] | 13:38 | 0.82766 | 0.91146 | 0.91784 |  | 13:38 | 0 | 0.15298 | 3855.2037 | 13:38 | 1.797 | 1.6518 | 0.14515 | 1.9278e-05 | 0
[13 empty] | 13:38 | 0.8185 | 0.91146 | 0.91784 |  | 13:38 | 0 | 0.15298 | 3855.2037 | 13:38 | 1.7975 | 1.6523 | 0.14519 | 1.9284e-05 | 0
[13 empty] | 13:38 | 0.80952 | 0.91146 | 0.91784 |  | 13:38 | 0 | 0.15298 | 3855.2037 | 13:38 | 1.798 | 1.6527 | 0.14522 | 1.929e-05 | 0
[13 empty] | 13:39 | 0.80073 | 0.91146 | 0.91784 |  | 13:39 | 0 | 0.15298 | 3855.2037 | 13:39 | 1.7984 | 1.6532 | 0.14526 | 1.9293e-05 | 0
[13 empty] | 13:39 | 0.79211 | 0.91146 | 0.91784 |  | 13:39 | 0 | 0.15298 | 3855.2037 | 13:39 | 1.7989 | 1.6536 | 0.1453 | 1.9299e-05 | 0
[13 empty] | 13:39 | 0.78368 | 0.91146 | 0.91784 |  | 13:39 | 0 | 0.15298 | 3855.2037 | 13:39 | 1.7994 | 1.654 | 0.14534 | 1.9305e-05 | 0
[13 empty] | 13:40 | 0.77542 | 0.91146 | 0.91784 |  | 13:40 | 0 | 0.15298 | 3855.2037 | 13:40 | 1.7999 | 1.6545 | 0.14538 | 1.9309e-05 | 0
[13 empty] | 13:40 | 0.76733 | 0.91146 | 0.91784 |  | 13:40 | 0 | 0.15298 | 3855.2037 | 13:40 | 1.8003 | 1.6549 | 0.14542 | 1.9314e-05 | 0
[13 empty] | 13:40 | 0.7594 | 0.91146 | 0.91784 |  | 13:40 | 0 | 0.15298 | 3855.2037 | 13:40 | 1.8008 | 1.6553 | 0.14545 | 1.932e-05 | 0
[13 empty] | 13:40 | 0.75164 | 0.91146 | 0.91784 |  | 13:40 | 0 | 0.15298 | 3855.2037 | 13:40 | 1.8012 | 1.6557 | 0.14549 | 1.9324e-05 | 0
[13 empty] | 13:40 | 0.74403 | 0.91146 | 0.91784 |  | 13:40 | 0 | 0.15298 | 3855.2037 | 13:40 | 1.8017 | 1.6562 | 0.14553 | 1.933e-05 | 0
[13 empty] | 13:41 | 0.73658 | 0.91146 | 0.91784 |  | 13:41 | 0 | 0.15298 | 3855.2037 | 13:41 | 1.8021 | 1.6566 | 0.14556 | 1.9334e-05 | 0
[13 empty] | 13:41 | 0.72929 | 0.91146 | 0.91784 |  | 13:41 | 0 | 0.15298 | 3855.2037 | 13:41 | 1.8026 | 1.657 | 0.1456 | 1.9339e-05 | 0
[13 empty] | 13:41 | 1.1629 | 0.91146 | 0.91784 |  | 13:41 | 0 | 0.15298 | 3855.2037 | 13:41 | 1.8033 | 1.6576 | 0.14566 | 1.9347e-05 | 0
[13 empty] | 13:42 | 1.1468 | 0.91146 | 0.91784 |  | 13:42 | 0 | 0.15298 | 3855.2037 | 13:42 | 1.804 | 1.6583 | 0.14571 | 1.9355e-05 | 0
[13 empty] | 13:42 | 1.1311 | 0.91146 | 0.91784 |  | 13:42 | 0 | 0.15298 | 3855.2037 | 13:42 | 1.8047 | 1.6589 | 0.14577 | 1.936e-05 | 0
[13 empty] | 13:42 | 1.1157 | 0.91146 | 0.91784 |  | 13:42 | 0 | 0.15298 | 3855.2037 | 13:42 | 1.8053 | 1.6595 | 0.14582 | 1.9368e-05 | 0
[13 empty] | 13:42 | 1.1006 | 0.91146 | 0.91784 |  | 13:42 | 0 | 0.15298 | 3855.2037 | 13:42 | 1.806 | 1.6601 | 0.14588 | 1.9376e-05 | 0
[13 empty] | 13:42 | 1.0859 | 0.91146 | 0.91784 |  | 13:42 | 0 | 0.15298 | 3855.2037 | 13:42 | 1.8067 | 1.6607 | 0.14593 | 1.9383e-05 | 0
[13 empty] | 13:43 | 1.0714 | 0.91146 | 0.91784 |  | 13:43 | 0 | 0.15298 | 3855.2037 | 13:43 | 1.8073 | 1.6613 | 0.14598 | 1.9389e-05 | 0
[13 empty] | 13:43 | 1.0572 | 0.91146 | 0.91784 |  | 13:43 | 0 | 0.15298 | 3855.2037 | 13:43 | 1.808 | 1.6619 | 0.14603 | 1.9397e-05 | 0
[13 empty] | 13:43 | 1.0434 | 0.91146 | 0.91784 |  | 13:43 | 0 | 0.15298 | 3855.2037 | 13:43 | 1.8086 | 1.6625 | 0.14608 | 1.9402e-05 | 0
[13 empty] | 13:44 | 1.0298 | 0.91146 | 0.91784 |  | 13:44 | 0 | 0.15298 | 3855.2037 | 13:44 | 1.8092 | 1.663 | 0.14613 | 1.941e-05 | 0
[13 empty] | 13:44 | 1.0164 | 0.91146 | 0.91784 |  | 13:44 | 0 | 0.15298 | 3855.2037 | 13:44 | 1.8098 | 1.6636 | 0.14618 | 1.9416e-05 | 0
[13 empty] | 13:44 | 1.0034 | 0.91146 | 0.91784 |  | 13:44 | 0 | 0.15298 | 3855.2037 | 13:44 | 1.8104 | 1.6642 | 0.14623 | 1.9423e-05 | 0
[13 empty] | 13:44 | 0.99062 | 0.91146 | 0.91784 |  | 13:44 | 0 | 0.15298 | 3855.2037 | 13:44 | 1.811 | 1.6647 | 0.14628 | 1.9429e-05 | 0
[13 empty] | 13:44 | 0.97811 | 0.91146 | 0.91784 |  | 13:44 | 0 | 0.15298 | 3855.2037 | 13:44 | 1.8116 | 1.6653 | 0.14633 | 1.9435e-05 | 0
[13 empty] | 13:45 | 0.96585 | 0.91146 | 0.91784 |  | 13:45 | 0 | 0.15298 | 3855.2037 | 13:45 | 1.8122 | 1.6658 | 0.14638 | 1.9442e-05 | 0
[13 empty] | 13:45 | 0.95385 | 0.91146 | 0.91784 |  | 13:45 | 0 | 0.15298 | 3855.2037 | 13:45 | 1.8128 | 1.6663 | 0.14642 | 1.9448e-05 | 0
[13 empty] | 13:45 | 0.94209 | 0.91146 | 0.91784 |  | 13:45 | 0 | 0.15298 | 3855.2037 | 13:45 | 1.8134 | 1.6669 | 0.14647 | 1.9454e-05 | 0
[13 empty] | 13:46 | 0.93058 | 0.91146 | 0.91784 |  | 13:46 | 0 | 0.15298 | 3855.2037 | 13:46 | 1.8139 | 1.6674 | 0.14651 | 1.946e-05 | 0
[13 empty] | 13:46 | 0.9193 | 0.91146 | 0.91784 |  | 13:46 | 0 | 0.15298 | 3855.2037 | 13:46 | 1.8145 | 1.6679 | 0.14656 | 1.9467e-05 | 0
[13 empty] | 13:46 | 0.90825 | 0.91146 | 0.91784 |  | 13:46 | 0 | 0.15298 | 3855.2037 | 13:46 | 1.815 | 1.6684 | 0.1466 | 1.9473e-05 | 0
[13 empty] | 13:46 | 0.89743 | 0.91146 | 0.91784 |  | 13:46 | 0 | 0.15298 | 3855.2037 | 13:46 | 1.8156 | 1.6689 | 0.14665 | 1.9479e-05 | 0
[13 empty] | 13:46 | 0.88683 | 0.91146 | 0.91784 |  | 13:46 | 0 | 0.15298 | 3855.2037 | 13:46 | 1.8161 | 1.6694 | 0.14669 | 1.9484e-05 | 0
[13 empty] | 13:47 | 0.87645 | 0.91146 | 0.91784 |  | 13:47 | 0 | 0.15298 | 3855.2037 | 13:47 | 1.8166 | 1.6699 | 0.14673 | 1.949e-05 | 0
[13 empty] | 13:47 | 0.86628 | 0.91146 | 0.91784 |  | 13:47 | 0 | 0.15298 | 3855.2037 | 13:47 | 1.8172 | 1.6704 | 0.14678 | 1.9496e-05 | 0
[13 empty] | 13:47 | 0.85633 | 0.91146 | 0.91784 |  | 13:47 | 0 | 0.15298 | 3855.2037 | 13:47 | 1.8177 | 1.6708 | 0.14682 | 1.9502e-05 | 0
[13 empty] | 13:48 | 0.84657 | 0.91146 | 0.91784 |  | 13:48 | 0 | 0.15298 | 3855.2037 | 13:48 | 1.8182 | 1.6713 | 0.14686 | 1.9505e-05 | 0
[13 empty] | 13:48 | 0.83702 | 0.91146 | 0.91784 |  | 13:48 | 0 | 0.15298 | 3855.2037 | 13:48 | 1.8187 | 1.6718 | 0.1469 | 1.9511e-05 | 0
[13 empty] | 13:48 | 0.82766 | 0.91146 | 0.91784 |  | 13:48 | 0 | 0.15298 | 3855.2037 | 13:48 | 1.8192 | 1.6722 | 0.14694 | 1.9517e-05 | 0
[13 empty] | 13:48 | 0.8185 | 0.91146 | 0.91784 |  | 13:48 | 0 | 0.15298 | 3855.2037 | 13:48 | 1.8197 | 1.6727 | 0.14698 | 1.9523e-05 | 0
[13 empty] | 13:48 | 0.80952 | 0.91146 | 0.91784 |  | 13:48 | 0 | 0.15298 | 3855.2037 | 13:48 | 1.8202 | 1.6732 | 0.14702 | 1.9528e-05 | 0
[13 empty] | 13:49 | 0.80073 | 0.91146 | 0.91784 |  | 13:49 | 0 | 0.15298 | 3855.2037 | 13:49 | 1.8207 | 1.6736 | 0.14706 | 1.9532e-05 | 0
[13 empty] | 13:49 | 0.79211 | 0.91146 | 0.91784 |  | 13:49 | 0 | 0.15298 | 3855.2037 | 13:49 | 1.8211 | 1.674 | 0.1471 | 1.9538e-05 | 0
[13 empty] | 13:49 | 0.78368 | 0.91146 | 0.91784 |  | 13:49 | 0 | 0.15298 | 3855.2037 | 13:49 | 1.8216 | 1.6745 | 0.14714 | 1.9544e-05 | 0
[13 empty] | 13:50 | 0.77542 | 0.91146 | 0.91784 |  | 13:50 | 0 | 0.15298 | 3855.2037 | 13:50 | 1.8221 | 1.6749 | 0.14717 | 1.9547e-05 | 0
[13 empty] | 13:50 | 0.76733 | 0.91146 | 0.91784 |  | 13:50 | 0 | 0.15298 | 3855.2037 | 13:50 | 1.8226 | 1.6753 | 0.14721 | 1.9553e-05 | 0
[13 empty] | 13:50 | 0.7594 | 0.91146 | 0.91784 |  | 13:50 | 0 | 0.15298 | 3855.2037 | 13:50 | 1.823 | 1.6757 | 0.14725 | 1.9557e-05 | 0
[13 empty] | 13:50 | 0.75164 | 0.91146 | 0.91784 |  | 13:50 | 0 | 0.15298 | 3855.2037 | 13:50 | 1.8235 | 1.6762 | 0.14729 | 1.9563e-05 | 0
[13 empty] | 13:50 | 0.74403 | 0.91146 | 0.91784 |  | 13:50 | 0 | 0.15298 | 3855.2037 | 13:50 | 1.8239 | 1.6766 | 0.14732 | 1.9568e-05 | 0
[13 empty] | 13:51 | 0.73658 | 0.91146 | 0.91784 |  | 13:51 | 0 | 0.15298 | 3855.2037 | 13:51 | 1.8244 | 1.677 | 0.14736 | 1.9572e-05 | 0
[13 empty] | 13:51 | 0.72929 | 0.91146 | 0.91784 |  | 13:51 | 0 | 0.15298 | 3855.2037 | 13:51 | 1.8248 | 1.6774 | 0.14739 | 1.9578e-05 | 0
[13 empty] | 13:51 | 1.1629 | 0.91146 | 0.91784 |  | 13:51 | 0 | 0.15298 | 3855.2037 | 13:51 | 1.8255 | 1.678 | 0.14745 | 1.9586e-05 | 0
[13 empty] | 13:52 | 1.1468 | 0.91146 | 0.91784 |  | 13:52 | 0 | 0.15298 | 3855.2037 | 13:52 | 1.8262 | 1.6787 | 0.14751 | 1.9591e-05 | 0
[13 empty] | 13:52 | 1.1311 | 0.91146 | 0.91784 |  | 13:52 | 0 | 0.15298 | 3855.2037 | 13:52 | 1.8269 | 1.6793 | 0.14756 | 1.9599e-05 | 0
[13 empty] | 13:52 | 1.1157 | 0.91146 | 0.91784 |  | 13:52 | 0 | 0.15298 | 3855.2037 | 13:52 | 1.8276 | 1.6799 | 0.14762 | 1.9607e-05 | 0
[13 empty] | 13:52 | 1.1006 | 0.91146 | 0.91784 |  | 13:52 | 0 | 0.15298 | 3855.2037 | 13:52 | 1.8282 | 1.6805 | 0.14767 | 1.9614e-05 | 0
[13 empty] | 13:52 | 1.0859 | 0.91146 | 0.91784 |  | 13:52 | 0 | 0.15298 | 3855.2037 | 13:52 | 1.8289 | 1.6812 | 0.14772 | 1.962e-05 | 0
[13 empty] | 13:53 | 1.0714 | 0.91146 | 0.91784 |  | 13:53 | 0 | 0.15298 | 3855.2037 | 13:53 | 1.8295 | 1.6817 | 0.14778 | 1.9628e-05 | 0
[13 empty] | 13:53 | 1.0572 | 0.91146 | 0.91784 |  | 13:53 | 0 | 0.15298 | 3855.2037 | 13:53 | 1.8302 | 1.6823 | 0.14783 | 1.9635e-05 | 0
[13 empty] | 13:53 | 1.0434 | 0.91146 | 0.91784 |  | 13:53 | 0 | 0.15298 | 3855.2037 | 13:53 | 1.8308 | 1.6829 | 0.14788 | 1.9641e-05 | 0
[13 empty] | 13:54 | 1.0298 | 0.91146 | 0.91784 |  | 13:54 | 0 | 0.15298 | 3855.2037 | 13:54 | 1.8314 | 1.6835 | 0.14793 | 1.9649e-05 | 0
[13 empty] | 13:54 | 1.0164 | 0.91146 | 0.91784 |  | 13:54 | 0 | 0.15298 | 3855.2037 | 13:54 | 1.8321 | 1.6841 | 0.14798 | 1.9654e-05 | 0
[13 empty] | 13:54 | 1.0034 | 0.91146 | 0.91784 |  | 13:54 | 0 | 0.15298 | 3855.2037 | 13:54 | 1.8327 | 1.6846 | 0.14803 | 1.9662e-05 | 0
[13 empty] | 13:54 | 0.99062 | 0.91146 | 0.91784 |  | 13:54 | 0 | 0.15298 | 3855.2037 | 13:54 | 1.8333 | 1.6852 | 0.14808 | 1.9668e-05 | 0
[13 empty] | 13:54 | 0.97811 | 0.91146 | 0.91784 |  | 13:54 | 0 | 0.15298 | 3855.2037 | 13:54 | 1.8338 | 1.6857 | 0.14812 | 1.9673e-05 | 0
[13 empty] | 13:55 | 0.96585 | 0.91146 | 0.91784 |  | 13:55 | 0 | 0.15298 | 3855.2037 | 13:55 | 1.8344 | 1.6862 | 0.14817 | 1.9681e-05 | 0
[13 empty] | 13:55 | 0.95385 | 0.91146 | 0.91784 |  | 13:55 | 0 | 0.15298 | 3855.2037 | 13:55 | 1.835 | 1.6868 | 0.14822 | 1.9687e-05 | 0
[13 empty] | 13:55 | 0.94209 | 0.91146 | 0.91784 |  | 13:55 | 0 | 0.15298 | 3855.2037 | 13:55 | 1.8356 | 1.6873 | 0.14826 | 1.9693e-05 | 0
[13 empty] | 13:56 | 0.93058 | 0.91146 | 0.91784 |  | 13:56 | 0 | 0.15298 | 3855.2037 | 13:56 | 1.8361 | 1.6878 | 0.14831 | 1.9698e-05 | 0
[13 empty] | 13:56 | 0.9193 | 0.91146 | 0.91784 |  | 13:56 | 0 | 0.15298 | 3855.2037 | 13:56 | 1.8367 | 1.6883 | 0.14835 | 1.9704e-05 | 0
[13 empty] | 13:56 | 0.90825 | 0.91146 | 0.91784 |  | 13:56 | 0 | 0.15298 | 3855.2037 | 13:56 | 1.8372 | 1.6888 | 0.1484 | 1.971e-05 | 0
[13 empty] | 13:56 | 0.89743 | 0.91146 | 0.91784 |  | 13:56 | 0 | 0.15298 | 3855.2037 | 13:56 | 1.8378 | 1.6893 | 0.14844 | 1.9717e-05 | 0
[13 empty] | 13:56 | 0.88683 | 0.91146 | 0.91784 |  | 13:56 | 0 | 0.15298 | 3855.2037 | 13:56 | 1.8383 | 1.6898 | 0.14849 | 1.9723e-05 | 0
[13 empty] | 13:57 | 0.87645 | 0.91146 | 0.91784 |  | 13:57 | 0 | 0.15298 | 3855.2037 | 13:57 | 1.8389 | 1.6903 | 0.14853 | 1.9729e-05 | 0
[13 empty] | 13:57 | 0.86628 | 0.91146 | 0.91784 |  | 13:57 | 0 | 0.15298 | 3855.2037 | 13:57 | 1.8394 | 1.6908 | 0.14857 | 1.9733e-05 | 0
[13 empty] | 13:57 | 0.85633 | 0.91146 | 0.91784 |  | 13:57 | 0 | 0.15298 | 3855.2037 | 13:57 | 1.8399 | 1.6913 | 0.14861 | 1.9738e-05 | 0
[13 empty] | 13:58 | 0.84657 | 0.91146 | 0.91784 |  | 13:58 | 0 | 0.15298 | 3855.2037 | 13:58 | 1.8404 | 1.6917 | 0.14865 | 1.9744e-05 | 0
[13 empty] | 13:58 | 0.83702 | 0.91146 | 0.91784 |  | 13:58 | 0 | 0.15298 | 3855.2037 | 13:58 | 1.8409 | 1.6922 | 0.1487 | 1.975e-05 | 0
[13 empty] | 13:58 | 0.82766 | 0.91146 | 0.91784 |  | 13:58 | 0 | 0.15298 | 3855.2037 | 13:58 | 1.8414 | 1.6927 | 0.14874 | 1.9756e-05 | 0
[13 empty] | 13:58 | 0.8185 | 0.91146 | 0.91784 |  | 13:58 | 0 | 0.15298 | 3855.2037 | 13:58 | 1.8419 | 1.6931 | 0.14878 | 1.9761e-05 | 0
[13 empty] | 13:58 | 0.80952 | 0.91146 | 0.91784 |  | 13:58 | 0 | 0.15298 | 3855.2037 | 13:58 | 1.8424 | 1.6936 | 0.14882 | 1.9765e-05 | 0
[13 empty] | 13:59 | 0.80073 | 0.91146 | 0.91784 |  | 13:59 | 0 | 0.15298 | 3855.2037 | 13:59 | 1.8429 | 1.694 | 0.14885 | 1.9771e-05 | 0
[13 empty] | 13:59 | 0.79211 | 0.91146 | 0.91784 |  | 13:59 | 0 | 0.15298 | 3855.2037 | 13:59 | 1.8434 | 1.6945 | 0.14889 | 1.9777e-05 | 0
[13 empty] | 13:59 | 0.78368 | 0.91146 | 0.91784 |  | 13:59 | 0 | 0.15298 | 3855.2037 | 13:59 | 1.8439 | 1.6949 | 0.14893 | 1.9782e-05 | 0
[13 empty] | 14:00 | 0.77542 | 0.91146 | 0.91784 |  | 14:00 | 0 | 0.15298 | 3855.2037 | 14:00 | 1.8443 | 1.6953 | 0.14897 | 1.9786e-05 | 0
[13 empty] | 14:00 | 0.76733 | 0.91146 | 0.91784 |  | 14:00 | 0 | 0.15298 | 3855.2037 | 14:00 | 1.8448 | 1.6958 | 0.14901 | 1.9792e-05 | 0
[13 empty] | 14:00 | 0.7594 | 0.91146 | 0.91784 |  | 14:00 | 0 | 0.15298 | 3855.2037 | 14:00 | 1.8452 | 1.6962 | 0.14904 | 1.9796e-05 | 0
[13 empty] | 14:00 | 0.75164 | 0.91146 | 0.91784 |  | 14:00 | 0.75552 | 0.15298 | 3860.8569 | 14:00 | 1.8457 | 1.6966 | 0.14908 | 1.9801e-05 | 0
[13 empty] | 14:00 | 0.74403 | 0.91146 | 0.91784 |  | 14:00 | 0.74784 | 0.15298 | 3872.1442 | 14:00 | 1.8461 | 1.697 | 0.14912 | 1.9805e-05 | 0
[13 empty] | 14:01 | 0.73658 | 0.91146 | 0.91784 |  | 14:01 | 0.74031 | 0.15298 | 3883.2978 | 14:01 | 1.8466 | 1.6974 | 0.14915 | 1.9811e-05 | 0
[13 empty] | 14:01 | 0.72929 | 0.91146 | 0.91784 |  | 14:01 | 0.73294 | 0.15298 | 3894.3559 | 14:01 | 1.847 | 1.6978 | 0.14919 | 1.9815e-05 | 0
[13 empty] | 14:01 | 1.1629 | 0.91146 | 0.91784 |  | 14:01 | 0.94609 | 0.15298 | 3906.9418 | 14:01 | 1.8477 | 1.6985 | 0.14925 | 1.9822e-05 | 0
[13 empty] | 14:02 | 1.1468 | 0.91146 | 0.91784 |  | 14:02 | 1.1549 | 0.15298 | 3922.6982 | 14:02 | 1.8484 | 1.6991 | 0.1493 | 1.983e-05 | 0
[13 empty] | 14:02 | 1.1311 | 0.91146 | 0.91784 |  | 14:02 | 1.139 | 0.15298 | 3939.906 | 14:02 | 1.8491 | 1.6997 | 0.14936 | 1.9838e-05 | 0
[13 empty] | 14:02 | 1.1157 | 0.91146 | 0.91784 |  | 14:02 | 1.1234 | 0.15298 | 3956.8656 | 14:02 | 1.8498 | 1.7004 | 0.14941 | 1.9845e-05 | 0
[13 empty] | 14:02 | 1.1006 | 0.91146 | 0.91784 |  | 14:02 | 1.1082 | 0.15298 | 3973.615 | 14:02 | 1.8505 | 1.701 | 0.14947 | 1.9853e-05 | 0
[13 empty] | 14:02 | 1.0859 | 0.91146 | 0.91784 |  | 14:02 | 1.0933 | 0.15298 | 3990.1162 | 14:02 | 1.8511 | 1.7016 | 0.14952 | 1.9859e-05 | 0
[13 empty] | 14:03 | 1.0714 | 0.91146 | 0.91784 |  | 14:03 | 1.0786 | 0.15298 | 4006.4073 | 14:03 | 1.8518 | 1.7022 | 0.14957 | 1.9866e-05 | 0
[13 empty] | 14:03 | 1.0572 | 0.91146 | 0.91784 |  | 14:03 | 1.0643 | 0.15298 | 4022.4883 | 14:03 | 1.8524 | 1.7028 | 0.14962 | 1.9874e-05 | 0
[13 empty] | 14:03 | 1.0434 | 0.91146 | 0.91784 |  | 14:03 | 1.0503 | 0.15298 | 4038.3401 | 14:03 | 1.853 | 1.7033 | 0.14967 | 1.988e-05 | 0
[13 empty] | 14:04 | 1.0298 | 0.91146 | 0.91784 |  | 14:04 | 1.0366 | 0.15298 | 4054.001 | 14:04 | 1.8537 | 1.7039 | 0.14972 | 1.9887e-05 | 0
[13 empty] | 14:04 | 1.0164 | 0.91146 | 0.91784 |  | 14:04 | 1.0231 | 0.15298 | 4069.4327 | 14:04 | 1.8543 | 1.7045 | 0.14977 | 1.9893e-05 | 0
[13 empty] | 14:04 | 1.0034 | 0.91146 | 0.91784 |  | 14:04 | 1.0099 | 0.15298 | 4084.6924 | 14:04 | 1.8549 | 1.705 | 0.14982 | 1.9901e-05 | 0
[13 empty] | 14:04 | 0.99062 | 0.91146 | 0.91784 |  | 14:04 | 0.99701 | 0.15298 | 4099.7421 | 14:04 | 1.8555 | 1.7056 | 0.14987 | 1.9906e-05 | 0
[13 empty] | 14:04 | 0.97811 | 0.91146 | 0.91784 |  | 14:04 | 0.98437 | 0.15298 | 4114.6008 | 14:04 | 1.8561 | 1.7061 | 0.14992 | 1.9912e-05 | 0
[13 empty] | 14:05 | 0.96585 | 0.91146 | 0.91784 |  | 14:05 | 0.97198 | 0.15298 | 4129.2685 | 14:05 | 1.8567 | 1.7067 | 0.14997 | 1.9918e-05 | 0
[13 empty] | 14:05 | 0.95385 | 0.91146 | 0.91784 |  | 14:05 | 0.95985 | 0.15298 | 4143.7644 | 14:05 | 1.8572 | 1.7072 | 0.15001 | 1.9926e-05 | 0
[13 empty] | 14:05 | 0.94209 | 0.91146 | 0.91784 |  | 14:05 | 0.94797 | 0.15298 | 4158.0692 | 14:05 | 1.8578 | 1.7077 | 0.15006 | 1.9931e-05 | 0
[13 empty] | 14:06 | 0.93058 | 0.91146 | 0.91784 |  | 14:06 | 0.93634 | 0.15298 | 4172.2022 | 14:06 | 1.8584 | 1.7083 | 0.15011 | 1.9937e-05 | 0
[13 empty] | 14:06 | 0.9193 | 0.91146 | 0.91784 |  | 14:06 | 0.92494 | 0.15298 | 4186.1633 | 14:06 | 1.8589 | 1.7088 | 0.15015 | 1.9943e-05 | 0
[13 empty] | 14:06 | 0.90825 | 0.91146 | 0.91784 |  | 14:06 | 0.91377 | 0.15298 | 4199.9524 | 14:06 | 1.8595 | 1.7093 | 0.15019 | 1.9948e-05 | 0
[13 empty] | 14:06 | 0.89743 | 0.91146 | 0.91784 |  | 14:06 | 0.90284 | 0.15298 | 4213.5697 | 14:06 | 1.86 | 1.7098 | 0.15024 | 1.9954e-05 | 0
[13 empty] | 14:06 | 0.88683 | 0.91146 | 0.91784 |  | 14:06 | 0.89213 | 0.15298 | 4227.0342 | 14:06 | 1.8606 | 1.7103 | 0.15028 | 1.996e-05 | 0
[13 empty] | 14:07 | 0.87645 | 0.91146 | 0.91784 |  | 14:07 | 0.88164 | 0.15298 | 4240.346 | 14:07 | 1.8611 | 1.7107 | 0.15033 | 1.9966e-05 | 0
[13 empty] | 14:07 | 0.86628 | 0.91146 | 0.91784 |  | 14:07 | 0.87137 | 0.15298 | 4253.4858 | 14:07 | 1.8616 | 1.7112 | 0.15037 | 1.9971e-05 | 0
[13 empty] | 14:07 | 0.85633 | 0.91146 | 0.91784 |  | 14:07 | 0.8613 | 0.15298 | 4266.4919 | 14:07 | 1.8621 | 1.7117 | 0.15041 | 1.9977e-05 | 0
[13 empty] | 14:08 | 0.84657 | 0.91146 | 0.91784 |  | 14:08 | 0.85145 | 0.15298 | 4279.3262 | 14:08 | 1.8626 | 1.7122 | 0.15045 | 1.9983e-05 | 0
[13 empty] | 14:08 | 0.83702 | 0.91146 | 0.91784 |  | 14:08 | 0.8418 | 0.15298 | 4292.0268 | 14:08 | 1.8632 | 1.7126 | 0.15049 | 1.9989e-05 | 0
[13 empty] | 14:08 | 0.82766 | 0.91146 | 0.91784 |  | 14:08 | 0.83234 | 0.15298 | 4304.5936 | 14:08 | 1.8637 | 1.7131 | 0.15053 | 1.9994e-05 | 0
[13 empty] | 14:08 | 0.8185 | 0.91146 | 0.91784 |  | 14:08 | 0.82308 | 0.15298 | 4317.0077 | 14:08 | 1.8642 | 1.7136 | 0.15057 | 2e-05 | 0
[13 empty] | 14:09 | 0.80952 | 0.91146 | 0.91784 |  | 14:09 | 0.81401 | 0.15298 | 4329.2881 | 14:09 | 1.8646 | 1.714 | 0.15061 | 2.0004e-05 | 0
[13 empty] | 14:09 | 0.80073 | 0.91146 | 0.91784 |  | 14:09 | 0.80512 | 0.15298 | 4341.4157 | 14:09 | 1.8651 | 1.7145 | 0.15065 | 2.001e-05 | 0
[13 empty] | 14:09 | 0.79211 | 0.91146 | 0.91784 |  | 14:09 | 0.79642 | 0.15298 | 4353.4287 | 14:09 | 1.8656 | 1.7149 | 0.15069 | 2.0015e-05 | 0
[13 empty] | 14:09 | 0.78368 | 0.91146 | 0.91784 |  | 14:09 | 0.7879 | 0.15298 | 4365.3081 | 14:09 | 1.8661 | 1.7153 | 0.15073 | 2.0019e-05 | 0
[13 empty] | 14:09 | 0.77542 | 0.91146 | 0.91784 |  | 14:09 | 0.77955 | 0.15298 | 4377.0728 | 14:09 | 1.8665 | 1.7158 | 0.15076 | 2.0025e-05 | 0
[13 empty] | 14:10 | 0.76733 | 0.91146 | 0.91784 |  | 14:10 | 0.77137 | 0.15298 | 4388.7038 | 14:10 | 1.867 | 1.7162 | 0.1508 | 2.0031e-05 | 0
[13 empty] | 14:10 | 0.7594 | 0.91146 | 0.91784 |  | 14:10 | 0.76336 | 0.15298 | 4400.2203 | 14:10 | 1.8675 | 1.7166 | 0.15084 | 2.0034e-05 | 0
[13 empty] | 14:10 | 0.75164 | 0.91146 | 0.91784 |  | 14:10 | 0 | 0.15298 | 4405.9308 | 14:10 | 1.8679 | 1.717 | 0.15088 | 2.004e-05 | 0
[13 empty] | 14:11 | 0.74403 | 0.91146 | 0.91784 |  | 14:11 | 0 | 0.15298 | 4405.9308 | 14:11 | 1.8684 | 1.7174 | 0.15091 | 2.0044e-05 | 0
[13 empty] | 14:11 | 0.73658 | 0.91146 | 0.91784 |  | 14:11 | 0 | 0.15298 | 4405.9308 | 14:11 | 1.8688 | 1.7179 | 0.15095 | 2.005e-05 | 0
[13 empty] | 14:11 | 0.72929 | 0.91146 | 0.91784 |  | 14:11 | 0 | 0.15298 | 4405.9308 | 14:11 | 1.8693 | 1.7183 | 0.15098 | 2.0054e-05 | 0
[13 empty] | 14:11 | 1.1629 | 0.91146 | 0.91784 |  | 14:11 | 0 | 0.15298 | 4405.9308 | 14:11 | 1.87 | 1.7189 | 0.15104 | 2.0061e-05 | 0
[13 empty] | 14:11 | 1.1468 | 0.91146 | 0.91784 |  | 14:11 | 0 | 0.15298 | 4405.9308 | 14:11 | 1.8707 | 1.7195 | 0.1511 | 2.0069e-05 | 0
[13 empty] | 14:12 | 1.1311 | 0.91146 | 0.91784 |  | 14:12 | 0 | 0.15298 | 4405.9308 | 14:12 | 1.8713 | 1.7202 | 0.15115 | 2.0076e-05 | 0
[13 empty] | 14:12 | 1.1157 | 0.91146 | 0.91784 |  | 14:12 | 0 | 0.15298 | 4405.9308 | 14:12 | 1.872 | 1.7208 | 0.15121 | 2.0084e-05 | 0
[13 empty] | 14:12 | 1.1006 | 0.91146 | 0.91784 |  | 14:12 | 0 | 0.15298 | 4405.9308 | 14:12 | 1.8727 | 1.7214 | 0.15126 | 2.0092e-05 | 0
[13 empty] | 14:13 | 1.0859 | 0.91146 | 0.91784 |  | 14:13 | 0 | 0.15298 | 4405.9308 | 14:13 | 1.8733 | 1.722 | 0.15131 | 2.0097e-05 | 0
[13 empty] | 14:13 | 1.0714 | 0.91146 | 0.91784 |  | 14:13 | 0 | 0.15298 | 4405.9308 | 14:13 | 1.874 | 1.7226 | 0.15137 | 2.0105e-05 | 0
[13 empty] | 14:13 | 1.0572 | 0.91146 | 0.91784 |  | 14:13 | 0 | 0.15298 | 4405.9308 | 14:13 | 1.8746 | 1.7232 | 0.15142 | 2.0111e-05 | 0
[13 empty] | 14:13 | 1.0434 | 0.91146 | 0.91784 |  | 14:13 | 0 | 0.15298 | 4405.9308 | 14:13 | 1.8753 | 1.7238 | 0.15147 | 2.0118e-05 | 0
[13 empty] | 14:13 | 1.0298 | 0.91146 | 0.91784 |  | 14:13 | 0 | 0.15298 | 4405.9308 | 14:13 | 1.8759 | 1.7244 | 0.15152 | 2.0126e-05 | 0
[13 empty] | 14:14 | 1.0164 | 0.91146 | 0.91784 |  | 14:14 | 0 | 0.15298 | 4405.9308 | 14:14 | 1.8765 | 1.7249 | 0.15157 | 2.0132e-05 | 0
[13 empty] | 14:14 | 1.0034 | 0.91146 | 0.91784 |  | 14:14 | 0 | 0.15298 | 4405.9308 | 14:14 | 1.8771 | 1.7255 | 0.15162 | 2.0138e-05 | 0
[13 empty] | 14:14 | 0.99062 | 0.91146 | 0.91784 |  | 14:14 | 0 | 0.15298 | 4405.9308 | 14:14 | 1.8777 | 1.726 | 0.15167 | 2.0145e-05 | 0
[13 empty] | 14:15 | 0.97811 | 0.91146 | 0.91784 |  | 14:15 | 0 | 0.15298 | 4405.9308 | 14:15 | 1.8783 | 1.7266 | 0.15172 | 2.0151e-05 | 0
[13 empty] | 14:15 | 0.96585 | 0.91146 | 0.91784 |  | 14:15 | 0 | 0.15298 | 4405.9308 | 14:15 | 1.8789 | 1.7271 | 0.15176 | 2.0157e-05 | 0
[13 empty] | 14:15 | 0.95385 | 0.91146 | 0.91784 |  | 14:15 | 0 | 0.15298 | 4405.9308 | 14:15 | 1.8795 | 1.7276 | 0.15181 | 2.0164e-05 | 0
[13 empty] | 14:15 | 0.94209 | 0.91146 | 0.91784 |  | 14:15 | 0 | 0.15298 | 4405.9308 | 14:15 | 1.88 | 1.7282 | 0.15185 | 2.017e-05 | 0
[13 empty] | 14:15 | 0.93058 | 0.91146 | 0.91784 |  | 14:15 | 0 | 0.15298 | 4405.9308 | 14:15 | 1.8806 | 1.7287 | 0.1519 | 2.0176e-05 | 0
[13 empty] | 14:16 | 0.9193 | 0.91146 | 0.91784 |  | 14:16 | 0 | 0.15298 | 4405.9308 | 14:16 | 1.8812 | 1.7292 | 0.15194 | 2.0181e-05 | 0
[13 empty] | 14:16 | 0.90825 | 0.91146 | 0.91784 |  | 14:16 | 0 | 0.15298 | 4405.9308 | 14:16 | 1.8817 | 1.7297 | 0.15199 | 2.0187e-05 | 0
[13 empty] | 14:16 | 0.89743 | 0.91146 | 0.91784 |  | 14:16 | 0 | 0.15298 | 4405.9308 | 14:16 | 1.8823 | 1.7302 | 0.15203 | 2.0193e-05 | 0
[13 empty] | 14:17 | 0.88683 | 0.91146 | 0.91784 |  | 14:17 | 0 | 0.15298 | 4405.9308 | 14:17 | 1.8828 | 1.7307 | 0.15208 | 2.0199e-05 | 0
[13 empty] | 14:17 | 0.87645 | 0.91146 | 0.91784 |  | 14:17 | 0 | 0.15298 | 4405.9308 | 14:17 | 1.8833 | 1.7312 | 0.15212 | 2.0204e-05 | 0
[13 empty] | 14:17 | 0.86628 | 0.91146 | 0.91784 |  | 14:17 | 0 | 0.15298 | 4405.9308 | 14:17 | 1.8838 | 1.7317 | 0.15216 | 2.021e-05 | 0
[13 empty] | 14:17 | 0.85633 | 0.91146 | 0.91784 |  | 14:17 | 0 | 0.15298 | 4405.9308 | 14:17 | 1.8844 | 1.7321 | 0.1522 | 2.0216e-05 | 0
[13 empty] | 14:17 | 0.84657 | 0.91146 | 0.91784 |  | 14:17 | 0 | 0.15298 | 4405.9308 | 14:17 | 1.8849 | 1.7326 | 0.15224 | 2.0222e-05 | 0
[13 empty] | 14:18 | 0.83702 | 0.91146 | 0.91784 |  | 14:18 | 0 | 0.15298 | 4405.9308 | 14:18 | 1.8854 | 1.7331 | 0.15229 | 2.0227e-05 | 0
[13 empty] | 14:18 | 0.82766 | 0.91146 | 0.91784 |  | 14:18 | 0 | 0.15298 | 4405.9308 | 14:18 | 1.8859 | 1.7335 | 0.15233 | 2.0233e-05 | 0
[13 empty] | 14:18 | 0.8185 | 0.91146 | 0.91784 |  | 14:18 | 0 | 0.15298 | 4405.9308 | 14:18 | 1.8864 | 1.734 | 0.15237 | 2.0237e-05 | 0
[13 empty] | 14:19 | 0.80952 | 0.91146 | 0.91784 |  | 14:19 | 0 | 0.15298 | 4405.9308 | 14:19 | 1.8869 | 1.7344 | 0.15241 | 2.0243e-05 | 0
[13 empty] | 14:19 | 0.80073 | 0.91146 | 0.91784 |  | 14:19 | 0 | 0.15298 | 4405.9308 | 14:19 | 1.8873 | 1.7349 | 0.15244 | 2.0248e-05 | 0
[13 empty] | 14:19 | 0.79211 | 0.91146 | 0.91784 |  | 14:19 | 0 | 0.15298 | 4405.9308 | 14:19 | 1.8878 | 1.7353 | 0.15249 | 2.0254e-05 | 0
[13 empty] | 14:19 | 0.78368 | 0.91146 | 0.91784 |  | 14:19 | 0 | 0.15298 | 4405.9308 | 14:19 | 1.8883 | 1.7358 | 0.15252 | 2.0258e-05 | 0
[13 empty] | 14:19 | 0.77542 | 0.91146 | 0.91784 |  | 14:19 | 0 | 0.15298 | 4405.9308 | 14:19 | 1.8888 | 1.7362 | 0.15256 | 2.0264e-05 | 0
[13 empty] | 14:20 | 0.76733 | 0.91146 | 0.91784 |  | 14:20 | 0 | 0.15298 | 4405.9308 | 14:20 | 1.8892 | 1.7366 | 0.1526 | 2.0267e-05 | 0
[13 empty] | 14:20 | 0.7594 | 0.91146 | 0.91784 |  | 14:20 | 0 | 0.15298 | 4405.9308 | 14:20 | 1.8897 | 1.737 | 0.15264 | 2.0273e-05 | 0
[13 empty] | 14:20 | 0.75164 | 0.91146 | 0.91784 |  | 14:20 | 0 | 0.15298 | 4405.9308 | 14:20 | 1.8901 | 1.7375 | 0.15267 | 2.0279e-05 | 0
[13 empty] | 14:21 | 0.74403 | 0.91146 | 0.91784 |  | 14:21 | 0 | 0.15298 | 4405.9308 | 14:21 | 1.8906 | 1.7379 | 0.15271 | 2.0283e-05 | 0
[13 empty] | 14:21 | 0.73658 | 0.91146 | 0.91784 |  | 14:21 | 0 | 0.15298 | 4405.9308 | 14:21 | 1.891 | 1.7383 | 0.15274 | 2.0288e-05 | 0
[13 empty] | 14:21 | 0.72929 | 0.91146 | 0.91784 |  | 14:21 | 0 | 0.15298 | 4405.9308 | 14:21 | 1.8915 | 1.7387 | 0.15278 | 2.0292e-05 | 0
[13 empty] | 14:21 | 1.1629 | 0.91146 | 0.91784 |  | 14:21 | 0 | 0.15298 | 4405.9308 | 14:21 | 1.8922 | 1.7393 | 0.15284 | 2.03e-05 | 0
[13 empty] | 14:21 | 1.1468 | 0.91146 | 0.91784 |  | 14:21 | 0 | 0.15298 | 4405.9308 | 14:21 | 1.8929 | 1.74 | 0.15289 | 2.0308e-05 | 0
[13 empty] | 14:22 | 1.1311 | 0.91146 | 0.91784 |  | 14:22 | 0 | 0.15298 | 4405.9308 | 14:22 | 1.8936 | 1.7406 | 0.15295 | 2.0315e-05 | 0
[13 empty] | 14:22 | 1.1157 | 0.91146 | 0.91784 |  | 14:22 | 0 | 0.15298 | 4405.9308 | 14:22 | 1.8942 | 1.7412 | 0.153 | 2.0323e-05 | 0
[13 empty] | 14:22 | 1.1006 | 0.91146 | 0.91784 |  | 14:22 | 0 | 0.15298 | 4405.9308 | 14:22 | 1.8949 | 1.7418 | 0.15306 | 2.0329e-05 | 0
[13 empty] | 14:22 | 1.0859 | 0.91146 | 0.91784 |  | 14:22 | 0 | 0.15298 | 4405.9308 | 14:22 | 1.8956 | 1.7424 | 0.15311 | 2.0336e-05 | 0
[13 empty] | 14:23 | 1.0714 | 0.91146 | 0.91784 |  | 14:23 | 0 | 0.15298 | 4405.9308 | 14:23 | 1.8962 | 1.743 | 0.15316 | 2.0344e-05 | 0
[13 empty] | 14:23 | 1.0572 | 0.91146 | 0.91784 |  | 14:23 | 0 | 0.15298 | 4405.9308 | 14:23 | 1.8969 | 1.7436 | 0.15321 | 2.035e-05 | 0
[13 empty] | 14:23 | 1.0434 | 0.91146 | 0.91784 |  | 14:23 | 0 | 0.15298 | 4405.9308 | 14:23 | 1.8975 | 1.7442 | 0.15326 | 2.0357e-05 | 0
[13 empty] | 14:24 | 1.0298 | 0.91146 | 0.91784 |  | 14:24 | 0 | 0.15298 | 4405.9308 | 14:24 | 1.8981 | 1.7448 | 0.15332 | 2.0363e-05 | 0
[13 empty] | 14:24 | 1.0164 | 0.91146 | 0.91784 |  | 14:24 | 0 | 0.15298 | 4405.9308 | 14:24 | 1.8987 | 1.7453 | 0.15337 | 2.0371e-05 | 0
[13 empty] | 14:24 | 1.0034 | 0.91146 | 0.91784 |  | 14:24 | 0 | 0.15298 | 4405.9308 | 14:24 | 1.8993 | 1.7459 | 0.15341 | 2.0376e-05 | 0
[13 empty] | 14:24 | 0.99062 | 0.91146 | 0.91784 |  | 14:24 | 0 | 0.15298 | 4405.9308 | 14:24 | 1.8999 | 1.7465 | 0.15346 | 2.0384e-05 | 0
[13 empty] | 14:24 | 0.97811 | 0.91146 | 0.91784 |  | 14:24 | 0 | 0.15298 | 4405.9308 | 14:24 | 1.9005 | 1.747 | 0.15351 | 2.039e-05 | 0
[13 empty] | 14:25 | 0.96585 | 0.91146 | 0.91784 |  | 14:25 | 0 | 0.15298 | 4405.9308 | 14:25 | 1.9011 | 1.7475 | 0.15356 | 2.0395e-05 | 0
[13 empty] | 14:25 | 0.95385 | 0.91146 | 0.91784 |  | 14:25 | 0 | 0.15298 | 4405.9308 | 14:25 | 1.9017 | 1.7481 | 0.1536 | 2.0401e-05 | 0
[13 empty] | 14:25 | 0.94209 | 0.91146 | 0.91784 |  | 14:25 | 0 | 0.15298 | 4405.9308 | 14:25 | 1.9023 | 1.7486 | 0.15365 | 2.0409e-05 | 0
[13 empty] | 14:26 | 0.93058 | 0.91146 | 0.91784 |  | 14:26 | 0 | 0.15298 | 4405.9308 | 14:26 | 1.9028 | 1.7491 | 0.1537 | 2.0414e-05 | 0
[13 empty] | 14:26 | 0.9193 | 0.91146 | 0.91784 |  | 14:26 | 0 | 0.15298 | 4405.9308 | 14:26 | 1.9034 | 1.7496 | 0.15374 | 2.042e-05 | 0
[13 empty] | 14:26 | 0.90825 | 0.91146 | 0.91784 |  | 14:26 | 0 | 0.15298 | 4405.9308 | 14:26 | 1.9039 | 1.7501 | 0.15379 | 2.0426e-05 | 0
[13 empty] | 14:26 | 0.89743 | 0.91146 | 0.91784 |  | 14:26 | 0 | 0.15298 | 4405.9308 | 14:26 | 1.9045 | 1.7506 | 0.15383 | 2.0432e-05 | 0
[13 empty] | 14:26 | 0.88683 | 0.91146 | 0.91784 |  | 14:26 | 0 | 0.15298 | 4405.9308 | 14:26 | 1.905 | 1.7511 | 0.15387 | 2.0437e-05 | 0
[13 empty] | 14:27 | 0.87645 | 0.91146 | 0.91784 |  | 14:27 | 0 | 0.15298 | 4405.9308 | 14:27 | 1.9055 | 1.7516 | 0.15392 | 2.0443e-05 | 0
[13 empty] | 14:27 | 0.86628 | 0.91146 | 0.91784 |  | 14:27 | 0 | 0.15298 | 4405.9308 | 14:27 | 1.9061 | 1.7521 | 0.15396 | 2.0449e-05 | 0
[13 empty] | 14:27 | 0.85633 | 0.91146 | 0.91784 |  | 14:27 | 0 | 0.15298 | 4405.9308 | 14:27 | 1.9066 | 1.7526 | 0.154 | 2.0455e-05 | 0
[13 empty] | 14:28 | 0.84657 | 0.91146 | 0.91784 |  | 14:28 | 0 | 0.15298 | 4405.9308 | 14:28 | 1.9071 | 1.753 | 0.15404 | 2.046e-05 | 0
[13 empty] | 14:28 | 0.83702 | 0.91146 | 0.91784 |  | 14:28 | 0 | 0.15298 | 4405.9308 | 14:28 | 1.9076 | 1.7535 | 0.15408 | 2.0466e-05 | 0
[13 empty] | 14:28 | 0.82766 | 0.91146 | 0.91784 |  | 14:28 | 0 | 0.15298 | 4405.9308 | 14:28 | 1.9081 | 1.754 | 0.15412 | 2.047e-05 | 0
[13 empty] | 14:28 | 0.8185 | 0.91146 | 0.91784 |  | 14:28 | 0 | 0.15298 | 4405.9308 | 14:28 | 1.9086 | 1.7544 | 0.15416 | 2.0476e-05 | 0
[13 empty] | 14:28 | 0.80952 | 0.91146 | 0.91784 |  | 14:28 | 0 | 0.15298 | 4405.9308 | 14:28 | 1.9091 | 1.7549 | 0.1542 | 2.0481e-05 | 0
[13 empty] | 14:29 | 0.80073 | 0.91146 | 0.91784 |  | 14:29 | 0 | 0.15298 | 4405.9308 | 14:29 | 1.9096 | 1.7553 | 0.15424 | 2.0487e-05 | 0
[13 empty] | 14:29 | 0.79211 | 0.91146 | 0.91784 |  | 14:29 | 0 | 0.15298 | 4405.9308 | 14:29 | 1.9101 | 1.7558 | 0.15428 | 2.0491e-05 | 0
[13 empty] | 14:29 | 0.78368 | 0.91146 | 0.91784 |  | 14:29 | 0 | 0.15298 | 4405.9308 | 14:29 | 1.9105 | 1.7562 | 0.15432 | 2.0497e-05 | 0
[13 empty] | 14:30 | 0.77542 | 0.91146 | 0.91784 |  | 14:30 | 0 | 0.15298 | 4405.9308 | 14:30 | 1.911 | 1.7566 | 0.15436 | 2.0502e-05 | 0
[13 empty] | 14:30 | 0.76733 | 0.91146 | 0.91784 |  | 14:30 | 0 | 0.15298 | 4405.9308 | 14:30 | 1.9115 | 1.7571 | 0.15439 | 2.0506e-05 | 0
[13 empty] | 14:30 | 0.7594 | 0.91146 | 0.91784 |  | 14:30 | 0 | 0.15298 | 4405.9308 | 14:30 | 1.9119 | 1.7575 | 0.15443 | 2.0512e-05 | 0
[13 empty] | 14:30 | 0.75164 | 0.91146 | 0.91784 |  | 14:30 | 0 | 0.15298 | 4405.9308 | 14:30 | 1.9124 | 1.7579 | 0.15447 | 2.0516e-05 | 0
[13 empty] | 14:30 | 0.74403 | 0.91146 | 0.91784 |  | 14:30 | 0 | 0.15298 | 4405.9308 | 14:30 | 1.9128 | 1.7583 | 0.1545 | 2.0521e-05 | 0
[13 empty] | 14:31 | 0.73658 | 0.91146 | 0.91784 |  | 14:31 | 0 | 0.15298 | 4405.9308 | 14:31 | 1.9133 | 1.7587 | 0.15454 | 2.0527e-05 | 0
[13 empty] | 14:31 | 0.72929 | 0.91146 | 0.91784 |  | 14:31 | 0 | 0.15298 | 4405.9308 | 14:31 | 1.9137 | 1.7591 | 0.15457 | 2.0531e-05 | 0
[13 empty] | 14:31 | 1.1629 | 0.91146 | 0.91784 |  | 14:31 | 0 | 0.15298 | 4405.9308 | 14:31 | 1.9144 | 1.7598 | 0.15463 | 2.0539e-05 | 0
[13 empty] | 14:32 | 1.1468 | 0.91146 | 0.91784 |  | 14:32 | 0 | 0.15298 | 4405.9308 | 14:32 | 1.9151 | 1.7604 | 0.15469 | 2.0546e-05 | 0
[13 empty] | 14:32 | 1.1311 | 0.91146 | 0.91784 |  | 14:32 | 0 | 0.15298 | 4405.9308 | 14:32 | 1.9158 | 1.761 | 0.15474 | 2.0554e-05 | 0
[13 empty] | 14:32 | 1.1157 | 0.91146 | 0.91784 |  | 14:32 | 0 | 0.15298 | 4405.9308 | 14:32 | 1.9165 | 1.7617 | 0.1548 | 2.0562e-05 | 0
[13 empty] | 14:32 | 1.1006 | 0.91146 | 0.91784 |  | 14:32 | 0 | 0.15298 | 4405.9308 | 14:32 | 1.9171 | 1.7623 | 0.15485 | 2.0567e-05 | 0
[13 empty] | 14:32 | 1.0859 | 0.91146 | 0.91784 |  | 14:32 | 0 | 0.15298 | 4405.9308 | 14:32 | 1.9178 | 1.7629 | 0.1549 | 2.0575e-05 | 0
[13 empty] | 14:33 | 1.0714 | 0.91146 | 0.91784 |  | 14:33 | 0 | 0.15298 | 4405.9308 | 14:33 | 1.9184 | 1.7635 | 0.15496 | 2.0583e-05 | 0
[13 empty] | 14:33 | 1.0572 | 0.91146 | 0.91784 |  | 14:33 | 0 | 0.15298 | 4405.9308 | 14:33 | 1.9191 | 1.7641 | 0.15501 | 2.0588e-05 | 0
[13 empty] | 14:33 | 1.0434 | 0.91146 | 0.91784 |  | 14:33 | 0 | 0.15298 | 4405.9308 | 14:33 | 1.9197 | 1.7646 | 0.15506 | 2.0596e-05 | 0
[13 empty] | 14:34 | 1.0298 | 0.91146 | 0.91784 |  | 14:34 | 0 | 0.15298 | 4405.9308 | 14:34 | 1.9203 | 1.7652 | 0.15511 | 2.0602e-05 | 0
[13 empty] | 14:34 | 1.0164 | 0.91146 | 0.91784 |  | 14:34 | 0 | 0.15298 | 4405.9308 | 14:34 | 1.921 | 1.7658 | 0.15516 | 2.0609e-05 | 0
[13 empty] | 14:34 | 1.0034 | 0.91146 | 0.91784 |  | 14:34 | 0 | 0.15298 | 4405.9308 | 14:34 | 1.9216 | 1.7663 | 0.15521 | 2.0615e-05 | 0
[13 empty] | 14:34 | 0.99062 | 0.91146 | 0.91784 |  | 14:34 | 0 | 0.15298 | 4405.9308 | 14:34 | 1.9222 | 1.7669 | 0.15526 | 2.0621e-05 | 0
[13 empty] | 14:34 | 0.97811 | 0.91146 | 0.91784 |  | 14:34 | 0 | 0.15298 | 4405.9308 | 14:34 | 1.9228 | 1.7674 | 0.15531 | 2.0628e-05 | 0
[13 empty] | 14:35 | 0.96585 | 0.91146 | 0.91784 |  | 14:35 | 0 | 0.15298 | 4405.9308 | 14:35 | 1.9234 | 1.768 | 0.15535 | 2.0634e-05 | 0
[13 empty] | 14:35 | 0.95385 | 0.91146 | 0.91784 |  | 14:35 | 0 | 0.15298 | 4405.9308 | 14:35 | 1.9239 | 1.7685 | 0.1554 | 2.064e-05 | 0
[13 empty] | 14:35 | 0.94209 | 0.91146 | 0.91784 |  | 14:35 | 0 | 0.15298 | 4405.9308 | 14:35 | 1.9245 | 1.769 | 0.15545 | 2.0647e-05 | 0
[13 empty] | 14:36 | 0.93058 | 0.91146 | 0.91784 |  | 14:36 | 0 | 0.15298 | 4405.9308 | 14:36 | 1.9251 | 1.7695 | 0.15549 | 2.0653e-05 | 0
[13 empty] | 14:36 | 0.9193 | 0.91146 | 0.91784 |  | 14:36 | 0 | 0.15298 | 4405.9308 | 14:36 | 1.9256 | 1.7701 | 0.15554 | 2.0659e-05 | 0
[13 empty] | 14:36 | 0.90825 | 0.91146 | 0.91784 |  | 14:36 | 0 | 0.15298 | 4405.9308 | 14:36 | 1.9262 | 1.7706 | 0.15558 | 2.0665e-05 | 0
[13 empty] | 14:36 | 0.89743 | 0.91146 | 0.91784 |  | 14:36 | 0 | 0.15298 | 4405.9308 | 14:36 | 1.9267 | 1.7711 | 0.15562 | 2.067e-05 | 0
[13 empty] | 14:36 | 0.88683 | 0.91146 | 0.91784 |  | 14:36 | 0 | 0.15298 | 4405.9308 | 14:36 | 1.9272 | 1.7715 | 0.15567 | 2.0676e-05 | 0
[13 empty] | 14:37 | 0.87645 | 0.91146 | 0.91784 |  | 14:37 | 0 | 0.15298 | 4405.9308 | 14:37 | 1.9278 | 1.772 | 0.15571 | 2.0682e-05 | 0
[13 empty] | 14:37 | 0.86628 | 0.91146 | 0.91784 |  | 14:37 | 0 | 0.15298 | 4405.9308 | 14:37 | 1.9283 | 1.7725 | 0.15575 | 2.0688e-05 | 0
[13 empty] | 14:37 | 0.85633 | 0.91146 | 0.91784 |  | 14:37 | 0 | 0.15298 | 4405.9308 | 14:37 | 1.9288 | 1.773 | 0.15579 | 2.0693e-05 | 0
[13 empty] | 14:38 | 0.84657 | 0.91146 | 0.91784 |  | 14:38 | 0 | 0.15298 | 4405.9308 | 14:38 | 1.9293 | 1.7735 | 0.15584 | 2.0699e-05 | 0
[13 empty] | 14:38 | 0.83702 | 0.91146 | 0.91784 |  | 14:38 | 0 | 0.15298 | 4405.9308 | 14:38 | 1.9298 | 1.7739 | 0.15588 | 2.0705e-05 | 0
[13 empty] | 14:38 | 0.82766 | 0.91146 | 0.91784 |  | 14:38 | 0 | 0.15298 | 4405.9308 | 14:38 | 1.9303 | 1.7744 | 0.15592 | 2.0709e-05 | 0
[13 empty] | 14:38 | 0.8185 | 0.91146 | 0.91784 |  | 14:38 | 0 | 0.15298 | 4405.9308 | 14:38 | 1.9308 | 1.7749 | 0.15596 | 2.0714e-05 | 0
[13 empty] | 14:38 | 0.80952 | 0.91146 | 0.91784 |  | 14:38 | 0 | 0.15298 | 4405.9308 | 14:38 | 1.9313 | 1.7753 | 0.156 | 2.072e-05 | 0
[13 empty] | 14:39 | 0.80073 | 0.91146 | 0.91784 |  | 14:39 | 0 | 0.15298 | 4405.9308 | 14:39 | 1.9318 | 1.7757 | 0.15604 | 2.0726e-05 | 0
[13 empty] | 14:39 | 0.79211 | 0.91146 | 0.91784 |  | 14:39 | 0 | 0.15298 | 4405.9308 | 14:39 | 1.9323 | 1.7762 | 0.15608 | 2.073e-05 | 0
[13 empty] | 14:39 | 0.78368 | 0.91146 | 0.91784 |  | 14:39 | 0 | 0.15298 | 4405.9308 | 14:39 | 1.9328 | 1.7766 | 0.15611 | 2.0735e-05 | 0
[13 empty] | 14:40 | 0.77542 | 0.91146 | 0.91784 |  | 14:40 | 0 | 0.15298 | 4405.9308 | 14:40 | 1.9332 | 1.7771 | 0.15615 | 2.0741e-05 | 0
[13 empty] | 14:40 | 0.76733 | 0.91146 | 0.91784 |  | 14:40 | 0 | 0.15298 | 4405.9308 | 14:40 | 1.9337 | 1.7775 | 0.15619 | 2.0745e-05 | 0
[13 empty] | 14:40 | 0.7594 | 0.91146 | 0.91784 |  | 14:40 | 0 | 0.15298 | 4405.9308 | 14:40 | 1.9342 | 1.7779 | 0.15623 | 2.0751e-05 | 0
[13 empty] | 14:40 | 0.75164 | 0.91146 | 0.91784 |  | 14:40 | 0 | 0.15298 | 4405.9308 | 14:40 | 1.9346 | 1.7783 | 0.15626 | 2.0754e-05 | 0
[13 empty] | 14:40 | 0.74403 | 0.91146 | 0.91784 |  | 14:40 | 0 | 0.15298 | 4405.9308 | 14:40 | 1.9351 | 1.7787 | 0.1563 | 2.076e-05 | 0
[13 empty] | 14:41 | 0.73658 | 0.91146 | 0.91784 |  | 14:41 | 0 | 0.15298 | 4405.9308 | 14:41 | 1.9355 | 1.7791 | 0.15634 | 2.0764e-05 | 0
[13 empty] | 14:41 | 0.72929 | 0.91146 | 0.91784 |  | 14:41 | 0 | 0.15298 | 4405.9308 | 14:41 | 1.9359 | 1.7795 | 0.15637 | 2.077e-05 | 0
[13 empty] | 14:41 | 1.1629 | 0.91146 | 0.91784 |  | 14:41 | 0 | 0.15298 | 4405.9308 | 14:41 | 1.9366 | 1.7802 | 0.15643 | 2.0777e-05 | 0
[13 empty] | 14:42 | 1.1468 | 0.91146 | 0.91784 |  | 14:42 | 0 | 0.15298 | 4405.9308 | 14:42 | 1.9374 | 1.7808 | 0.15648 | 2.0785e-05 | 0
[13 empty] | 14:42 | 1.1311 | 0.91146 | 0.91784 |  | 14:42 | 0 | 0.15298 | 4405.9308 | 14:42 | 1.938 | 1.7815 | 0.15654 | 2.0793e-05 | 0
[13 empty] | 14:42 | 1.1157 | 0.91146 | 0.91784 |  | 14:42 | 0 | 0.15298 | 4405.9308 | 14:42 | 1.9387 | 1.7821 | 0.15659 | 2.0798e-05 | 0
[13 empty] | 14:42 | 1.1006 | 0.91146 | 0.91784 |  | 14:42 | 0 | 0.15298 | 4405.9308 | 14:42 | 1.9394 | 1.7827 | 0.15665 | 2.0806e-05 | 0
[13 empty] | 14:42 | 1.0859 | 0.91146 | 0.91784 |  | 14:42 | 0 | 0.15298 | 4405.9308 | 14:42 | 1.94 | 1.7833 | 0.1567 | 2.0814e-05 | 0
[13 empty] | 14:43 | 1.0714 | 0.91146 | 0.91784 |  | 14:43 | 0 | 0.15298 | 4405.9308 | 14:43 | 1.9407 | 1.7839 | 0.15675 | 2.0819e-05 | 0
[13 empty] | 14:43 | 1.0572 | 0.91146 | 0.91784 |  | 14:43 | 0 | 0.15298 | 4405.9308 | 14:43 | 1.9413 | 1.7845 | 0.15681 | 2.0827e-05 | 0
[13 empty] | 14:43 | 1.0434 | 0.91146 | 0.91784 |  | 14:43 | 0 | 0.15298 | 4405.9308 | 14:43 | 1.9419 | 1.7851 | 0.15685 | 2.0835e-05 | 0
[13 empty] | 14:44 | 1.0298 | 0.91146 | 0.91784 |  | 14:44 | 0 | 0.15298 | 4405.9308 | 14:44 | 1.9426 | 1.7856 | 0.15691 | 2.084e-05 | 0
[13 empty] | 14:44 | 1.0164 | 0.91146 | 0.91784 |  | 14:44 | 0 | 0.15298 | 4405.9308 | 14:44 | 1.9432 | 1.7862 | 0.15696 | 2.0848e-05 | 0
[13 empty] | 14:44 | 1.0034 | 0.91146 | 0.91784 |  | 14:44 | 0 | 0.15298 | 4405.9308 | 14:44 | 1.9438 | 1.7868 | 0.157 | 2.0854e-05 | 0
[13 empty] | 14:44 | 0.99062 | 0.91146 | 0.91784 |  | 14:44 | 0 | 0.15298 | 4405.9308 | 14:44 | 1.9444 | 1.7873 | 0.15705 | 2.0859e-05 | 0
[13 empty] | 14:44 | 0.97811 | 0.91146 | 0.91784 |  | 14:44 | 0 | 0.15298 | 4405.9308 | 14:44 | 1.945 | 1.7879 | 0.1571 | 2.0867e-05 | 0
[13 empty] | 14:45 | 0.96585 | 0.91146 | 0.91784 |  | 14:45 | 0 | 0.15298 | 4405.9308 | 14:45 | 1.9456 | 1.7884 | 0.15715 | 2.0873e-05 | 0
[13 empty] | 14:45 | 0.95385 | 0.91146 | 0.91784 |  | 14:45 | 0 | 0.15298 | 4405.9308 | 14:45 | 1.9461 | 1.7889 | 0.15719 | 2.0879e-05 | 0
[13 empty] | 14:45 | 0.94209 | 0.91146 | 0.91784 |  | 14:45 | 0 | 0.15298 | 4405.9308 | 14:45 | 1.9467 | 1.7895 | 0.15724 | 2.0884e-05 | 0
[13 empty] | 14:46 | 0.93058 | 0.91146 | 0.91784 |  | 14:46 | 0 | 0.15298 | 4405.9308 | 14:46 | 1.9473 | 1.79 | 0.15729 | 2.0892e-05 | 0
[13 empty] | 14:46 | 0.9193 | 0.91146 | 0.91784 |  | 14:46 | 0 | 0.15298 | 4405.9308 | 14:46 | 1.9478 | 1.7905 | 0.15733 | 2.0898e-05 | 0
[13 empty] | 14:46 | 0.90825 | 0.91146 | 0.91784 |  | 14:46 | 0 | 0.15298 | 4405.9308 | 14:46 | 1.9484 | 1.791 | 0.15738 | 2.0903e-05 | 0
[13 empty] | 14:46 | 0.89743 | 0.91146 | 0.91784 |  | 14:46 | 0 | 0.15298 | 4405.9308 | 14:46 | 1.9489 | 1.7915 | 0.15742 | 2.0909e-05 | 0
[13 empty] | 14:46 | 0.88683 | 0.91146 | 0.91784 |  | 14:46 | 0 | 0.15298 | 4405.9308 | 14:46 | 1.9495 | 1.792 | 0.15746 | 2.0915e-05 | 0
[13 empty] | 14:47 | 0.87645 | 0.91146 | 0.91784 |  | 14:47 | 0 | 0.15298 | 4405.9308 | 14:47 | 1.95 | 1.7925 | 0.15751 | 2.0921e-05 | 0
[13 empty] | 14:47 | 0.86628 | 0.91146 | 0.91784 |  | 14:47 | 0 | 0.15298 | 4405.9308 | 14:47 | 1.9505 | 1.793 | 0.15755 | 2.0926e-05 | 0
[13 empty] | 14:47 | 0.85633 | 0.91146 | 0.91784 |  | 14:47 | 0 | 0.15298 | 4405.9308 | 14:47 | 1.951 | 1.7934 | 0.15759 | 2.0932e-05 | 0
[13 empty] | 14:48 | 0.84657 | 0.91146 | 0.91784 |  | 14:48 | 0 | 0.15298 | 4405.9308 | 14:48 | 1.9516 | 1.7939 | 0.15763 | 2.0938e-05 | 0
[13 empty] | 14:48 | 0.83702 | 0.91146 | 0.91784 |  | 14:48 | 0 | 0.15298 | 4405.9308 | 14:48 | 1.9521 | 1.7944 | 0.15767 | 2.0942e-05 | 0
[13 empty] | 14:48 | 0.82766 | 0.91146 | 0.91784 |  | 14:48 | 0 | 0.15298 | 4405.9308 | 14:48 | 1.9526 | 1.7948 | 0.15771 | 2.0947e-05 | 0
[13 empty] | 14:48 | 0.8185 | 0.91146 | 0.91784 |  | 14:48 | 0 | 0.15298 | 4405.9308 | 14:48 | 1.9531 | 1.7953 | 0.15775 | 2.0953e-05 | 0
[13 empty] | 14:48 | 0.80952 | 0.91146 | 0.91784 |  | 14:48 | 0 | 0.15298 | 4405.9308 | 14:48 | 1.9536 | 1.7957 | 0.15779 | 2.0959e-05 | 0
[13 empty] | 14:49 | 0.80073 | 0.91146 | 0.91784 |  | 14:49 | 0 | 0.15298 | 4405.9308 | 14:49 | 1.954 | 1.7962 | 0.15783 | 2.0963e-05 | 0
[13 empty] | 14:49 | 0.79211 | 0.91146 | 0.91784 |  | 14:49 | 0 | 0.15298 | 4405.9308 | 14:49 | 1.9545 | 1.7966 | 0.15787 | 2.0968e-05 | 0
[13 empty] | 14:49 | 0.78368 | 0.91146 | 0.91784 |  | 14:49 | 0 | 0.15298 | 4405.9308 | 14:49 | 1.955 | 1.7971 | 0.15791 | 2.0974e-05 | 0
[13 empty] | 14:50 | 0.77542 | 0.91146 | 0.91784 |  | 14:50 | 0 | 0.15298 | 4405.9308 | 14:50 | 1.9555 | 1.7975 | 0.15795 | 2.0978e-05 | 0
[13 empty] | 14:50 | 0.76733 | 0.91146 | 0.91784 |  | 14:50 | 0 | 0.15298 | 4405.9308 | 14:50 | 1.9559 | 1.7979 | 0.15798 | 2.0984e-05 | 0
[13 empty] | 14:50 | 0.7594 | 0.91146 | 0.91784 |  | 14:50 | 0 | 0.15298 | 4405.9308 | 14:50 | 1.9564 | 1.7983 | 0.15802 | 2.0989e-05 | 0
[13 empty] | 14:50 | 0.75164 | 0.91146 | 0.91784 |  | 14:50 | 0 | 0.15298 | 4405.9308 | 14:50 | 1.9568 | 1.7988 | 0.15806 | 2.0993e-05 | 0
[13 empty] | 14:50 | 0.74403 | 0.91146 | 0.91784 |  | 14:50 | 0 | 0.15298 | 4405.9308 | 14:50 | 1.9573 | 1.7992 | 0.15809 | 2.0999e-05 | 0
[13 empty] | 14:51 | 0.73658 | 0.91146 | 0.91784 |  | 14:51 | 0 | 0.15298 | 4405.9308 | 14:51 | 1.9577 | 1.7996 | 0.15813 | 2.1003e-05 | 0
[13 empty] | 14:51 | 0.72929 | 0.91146 | 0.91784 |  | 14:51 | 0 | 0.15298 | 4405.9308 | 14:51 | 1.9582 | 1.8 | 0.15817 | 2.1008e-05 | 0
[13 empty] | 14:51 | 1.1629 | 0.91146 | 0.91784 |  | 14:51 | 0 | 0.15298 | 4405.9308 | 14:51 | 1.9589 | 1.8006 | 0.15822 | 2.1016e-05 | 0
[13 empty] | 14:52 | 1.1468 | 0.91146 | 0.91784 |  | 14:52 | 0 | 0.15298 | 4405.9308 | 14:52 | 1.9596 | 1.8013 | 0.15828 | 2.1024e-05 | 0
[13 empty] | 14:52 | 1.1311 | 0.91146 | 0.91784 |  | 14:52 | 0 | 0.15298 | 4405.9308 | 14:52 | 1.9603 | 1.8019 | 0.15833 | 2.1029e-05 | 0
[13 empty] | 14:52 | 1.1157 | 0.91146 | 0.91784 |  | 14:52 | 0 | 0.15298 | 4405.9308 | 14:52 | 1.9609 | 1.8025 | 0.15839 | 2.1037e-05 | 0
[13 empty] | 14:52 | 1.1006 | 0.91146 | 0.91784 |  | 14:52 | 0 | 0.15298 | 4405.9308 | 14:52 | 1.9616 | 1.8031 | 0.15844 | 2.1045e-05 | 0
[13 empty] | 14:52 | 1.0859 | 0.91146 | 0.91784 |  | 14:52 | 0 | 0.15298 | 4405.9308 | 14:52 | 1.9623 | 1.8037 | 0.1585 | 2.1052e-05 | 0
[13 empty] | 14:53 | 1.0714 | 0.91146 | 0.91784 |  | 14:53 | 0 | 0.15298 | 4405.9308 | 14:53 | 1.9629 | 1.8043 | 0.15855 | 2.1058e-05 | 0
[13 empty] | 14:53 | 1.0572 | 0.91146 | 0.91784 |  | 14:53 | 0 | 0.15298 | 4405.9308 | 14:53 | 1.9636 | 1.8049 | 0.1586 | 2.1066e-05 | 0
[13 empty] | 14:53 | 1.0434 | 0.91146 | 0.91784 |  | 14:53 | 0 | 0.15298 | 4405.9308 | 14:53 | 1.9642 | 1.8055 | 0.15865 | 2.1071e-05 | 0
[13 empty] | 14:54 | 1.0298 | 0.91146 | 0.91784 |  | 14:54 | 0 | 0.15298 | 4405.9308 | 14:54 | 1.9648 | 1.8061 | 0.1587 | 2.1079e-05 | 0
[13 empty] | 14:54 | 1.0164 | 0.91146 | 0.91784 |  | 14:54 | 0 | 0.15298 | 4405.9308 | 14:54 | 1.9654 | 1.8067 | 0.15875 | 2.1085e-05 | 0
[13 empty] | 14:54 | 1.0034 | 0.91146 | 0.91784 |  | 14:54 | 0 | 0.15298 | 4405.9308 | 14:54 | 1.966 | 1.8072 | 0.1588 | 2.1092e-05 | 0
[13 empty] | 14:54 | 0.99062 | 0.91146 | 0.91784 |  | 14:54 | 0 | 0.15298 | 4405.9308 | 14:54 | 1.9666 | 1.8078 | 0.15885 | 2.1098e-05 | 0
[13 empty] | 14:54 | 0.97811 | 0.91146 | 0.91784 |  | 14:54 | 0 | 0.15298 | 4405.9308 | 14:54 | 1.9672 | 1.8083 | 0.1589 | 2.1106e-05 | 0
[13 empty] | 14:55 | 0.96585 | 0.91146 | 0.91784 |  | 14:55 | 0 | 0.15298 | 4405.9308 | 14:55 | 1.9678 | 1.8088 | 0.15894 | 2.1112e-05 | 0
[13 empty] | 14:55 | 0.95385 | 0.91146 | 0.91784 |  | 14:55 | 0 | 0.15298 | 4405.9308 | 14:55 | 1.9684 | 1.8094 | 0.15899 | 2.1117e-05 | 0
[13 empty] | 14:55 | 0.94209 | 0.91146 | 0.91784 |  | 14:55 | 0 | 0.15298 | 4405.9308 | 14:55 | 1.969 | 1.8099 | 0.15904 | 2.1123e-05 | 0
[13 empty] | 14:56 | 0.93058 | 0.91146 | 0.91784 |  | 14:56 | 0 | 0.15298 | 4405.9308 | 14:56 | 1.9695 | 1.8104 | 0.15908 | 2.1129e-05 | 0
[13 empty] | 14:56 | 0.9193 | 0.91146 | 0.91784 |  | 14:56 | 0 | 0.15298 | 4405.9308 | 14:56 | 1.9701 | 1.8109 | 0.15913 | 2.1136e-05 | 0
[13 empty] | 14:56 | 0.90825 | 0.91146 | 0.91784 |  | 14:56 | 0 | 0.15298 | 4405.9308 | 14:56 | 1.9706 | 1.8114 | 0.15917 | 2.1142e-05 | 0
[13 empty] | 14:56 | 0.89743 | 0.91146 | 0.91784 |  | 14:56 | 0 | 0.15298 | 4405.9308 | 14:56 | 1.9712 | 1.8119 | 0.15922 | 2.1148e-05 | 0
[13 empty] | 14:56 | 0.88683 | 0.91146 | 0.91784 |  | 14:56 | 0 | 0.15298 | 4405.9308 | 14:56 | 1.9717 | 1.8124 | 0.15926 | 2.1154e-05 | 0
[13 empty] | 14:57 | 0.87645 | 0.91146 | 0.91784 |  | 14:57 | 0 | 0.15298 | 4405.9308 | 14:57 | 1.9722 | 1.8129 | 0.1593 | 2.1159e-05 | 0
[13 empty] | 14:57 | 0.86628 | 0.91146 | 0.91784 |  | 14:57 | 0 | 0.15298 | 4405.9308 | 14:57 | 1.9728 | 1.8134 | 0.15934 | 2.1165e-05 | 0
[13 empty] | 14:57 | 0.85633 | 0.91146 | 0.91784 |  | 14:57 | 0 | 0.15298 | 4405.9308 | 14:57 | 1.9733 | 1.8139 | 0.15939 | 2.1171e-05 | 0
[13 empty] | 14:58 | 0.84657 | 0.91146 | 0.91784 |  | 14:58 | 0 | 0.15298 | 4405.9308 | 14:58 | 1.9738 | 1.8143 | 0.15943 | 2.1175e-05 | 0
[13 empty] | 14:58 | 0.83702 | 0.91146 | 0.91784 |  | 14:58 | 0 | 0.15298 | 4405.9308 | 14:58 | 1.9743 | 1.8148 | 0.15947 | 2.118e-05 | 0
[13 empty] | 14:58 | 0.82766 | 0.91146 | 0.91784 |  | 14:58 | 0 | 0.15298 | 4405.9308 | 14:58 | 1.9748 | 1.8153 | 0.15951 | 2.1186e-05 | 0
[13 empty] | 14:58 | 0.8185 | 0.91146 | 0.91784 |  | 14:58 | 0 | 0.15298 | 4405.9308 | 14:58 | 1.9753 | 1.8157 | 0.15955 | 2.1192e-05 | 0
[13 empty] | 14:58 | 0.80952 | 0.91146 | 0.91784 |  | 14:58 | 0 | 0.15298 | 4405.9308 | 14:58 | 1.9758 | 1.8162 | 0.15959 | 2.1198e-05 | 0
[13 empty] | 14:59 | 0.80073 | 0.91146 | 0.91784 |  | 14:59 | 0 | 0.15298 | 4405.9308 | 14:59 | 1.9763 | 1.8166 | 0.15963 | 2.1201e-05 | 0
[13 empty] | 14:59 | 0.79211 | 0.91146 | 0.91784 |  | 14:59 | 0 | 0.15298 | 4405.9308 | 14:59 | 1.9767 | 1.8171 | 0.15967 | 2.1207e-05 | 0
[13 empty] | 14:59 | 0.78368 | 0.91146 | 0.91784 |  | 14:59 | 0 | 0.15298 | 4405.9308 | 14:59 | 1.9772 | 1.8175 | 0.1597 | 2.1213e-05 | 0
[13 empty] | 15:00 | 0.77542 | 0.91146 | 0.91784 |  | 15:00 | 0 | 0.15298 | 4405.9308 | 15:00 | 1.9777 | 1.8179 | 0.15974 | 2.1217e-05 | 0
[13 empty] | 15:00 | 0.76733 | 0.91146 | 0.91784 |  | 15:00 | 0 | 0.15298 | 4405.9308 | 15:00 | 1.9782 | 1.8184 | 0.15978 | 2.1222e-05 | 0
[13 empty] | 15:00 | 0.7594 | 0.91146 | 0.91784 |  | 15:00 | 0 | 0.15298 | 4405.9308 | 15:00 | 1.9786 | 1.8188 | 0.15982 | 2.1228e-05 | 0
[13 empty] | 15:00 | 0.75164 | 0.91146 | 0.91784 |  | 15:00 | 0.75552 | 0.15298 | 4411.603 | 15:00 | 1.9791 | 1.8192 | 0.15985 | 2.1232e-05 | 0
[13 empty] | 15:00 | 0.74403 | 0.91146 | 0.91784 |  | 15:00 | 0.74784 | 0.15298 | 4422.8903 | 15:00 | 1.9795 | 1.8196 | 0.15989 | 2.1238e-05 | 0
[13 empty] | 15:01 | 0.73658 | 0.91146 | 0.91784 |  | 15:01 | 0.74031 | 0.15298 | 4434.0439 | 15:01 | 1.98 | 1.82 | 0.15993 | 2.1241e-05 | 0
[13 empty] | 15:01 | 0.72929 | 0.91146 | 0.91784 |  | 15:01 | 0.73294 | 0.15298 | 4445.0829 | 15:01 | 1.9804 | 1.8204 | 0.15996 | 2.1247e-05 | 0
[13 empty] | 15:01 | 1.1629 | 0.91146 | 0.91784 |  | 15:01 | 0.94609 | 0.15298 | 4457.688 | 15:01 | 1.9811 | 1.8211 | 0.16002 | 2.1255e-05 | 0
[13 empty] | 15:02 | 1.1468 | 0.91146 | 0.91784 |  | 15:02 | 1.1549 | 0.15298 | 4473.4443 | 15:02 | 1.9818 | 1.8217 | 0.16007 | 2.1261e-05 | 0
[13 empty] | 15:02 | 1.1311 | 0.91146 | 0.91784 |  | 15:02 | 1.139 | 0.15298 | 4490.6521 | 15:02 | 1.9825 | 1.8223 | 0.16013 | 2.1268e-05 | 0
[13 empty] | 15:02 | 1.1157 | 0.91146 | 0.91784 |  | 15:02 | 1.1234 | 0.15298 | 4507.6117 | 15:02 | 1.9832 | 1.823 | 0.16018 | 2.1276e-05 | 0
[13 empty] | 15:02 | 1.1006 | 0.91146 | 0.91784 |  | 15:02 | 1.1082 | 0.15298 | 4524.342 | 15:02 | 1.9838 | 1.8236 | 0.16024 | 2.1283e-05 | 0
[13 empty] | 15:02 | 1.0859 | 0.91146 | 0.91784 |  | 15:02 | 1.0933 | 0.15298 | 4540.8623 | 15:02 | 1.9845 | 1.8242 | 0.16029 | 2.1291e-05 | 0
[13 empty] | 15:03 | 1.0714 | 0.91146 | 0.91784 |  | 15:03 | 1.0786 | 0.15298 | 4557.1534 | 15:03 | 1.9851 | 1.8248 | 0.16034 | 2.1297e-05 | 0
[13 empty] | 15:03 | 1.0572 | 0.91146 | 0.91784 |  | 15:03 | 1.0643 | 0.15298 | 4573.2153 | 15:03 | 1.9858 | 1.8254 | 0.1604 | 2.1304e-05 | 0
[13 empty] | 15:03 | 1.0434 | 0.91146 | 0.91784 |  | 15:03 | 1.0503 | 0.15298 | 4589.0863 | 15:03 | 1.9864 | 1.8259 | 0.16045 | 2.131e-05 | 0
[13 empty] | 15:04 | 1.0298 | 0.91146 | 0.91784 |  | 15:04 | 1.0366 | 0.15298 | 4604.728 | 15:04 | 1.987 | 1.8265 | 0.1605 | 2.1318e-05 | 0
[13 empty] | 15:04 | 1.0164 | 0.91146 | 0.91784 |  | 15:04 | 1.0231 | 0.15298 | 4620.1788 | 15:04 | 1.9877 | 1.8271 | 0.16055 | 2.1324e-05 | 0
[13 empty] | 15:04 | 1.0034 | 0.91146 | 0.91784 |  | 15:04 | 1.0099 | 0.15298 | 4635.4195 | 15:04 | 1.9883 | 1.8276 | 0.1606 | 2.1331e-05 | 0
[13 empty] | 15:04 | 0.99062 | 0.91146 | 0.91784 |  | 15:04 | 0.99701 | 0.15298 | 4650.4882 | 15:04 | 1.9889 | 1.8282 | 0.16064 | 2.1337e-05 | 0
[13 empty] | 15:04 | 0.97811 | 0.91146 | 0.91784 |  | 15:04 | 0.98437 | 0.15298 | 4665.347 | 15:04 | 1.9894 | 1.8287 | 0.16069 | 2.1343e-05 | 0
[13 empty] | 15:05 | 0.96585 | 0.91146 | 0.91784 |  | 15:05 | 0.97198 | 0.15298 | 4680.0147 | 15:05 | 1.99 | 1.8293 | 0.16074 | 2.135e-05 | 0
[13 empty] | 15:05 | 0.95385 | 0.91146 | 0.91784 |  | 15:05 | 0.95985 | 0.15298 | 4694.5105 | 15:05 | 1.9906 | 1.8298 | 0.16079 | 2.1356e-05 | 0
[13 empty] | 15:05 | 0.94209 | 0.91146 | 0.91784 |  | 15:05 | 0.94797 | 0.15298 | 4708.8153 | 15:05 | 1.9912 | 1.8303 | 0.16083 | 2.1362e-05 | 0
[13 empty] | 15:06 | 0.93058 | 0.91146 | 0.91784 |  | 15:06 | 0.93634 | 0.15298 | 4722.9483 | 15:06 | 1.9917 | 1.8308 | 0.16088 | 2.1368e-05 | 0
[13 empty] | 15:06 | 0.9193 | 0.91146 | 0.91784 |  | 15:06 | 0.92494 | 0.15298 | 4736.9094 | 15:06 | 1.9923 | 1.8313 | 0.16092 | 2.1373e-05 | 0
[13 empty] | 15:06 | 0.90825 | 0.91146 | 0.91784 |  | 15:06 | 0.91377 | 0.15298 | 4750.6986 | 15:06 | 1.9928 | 1.8319 | 0.16097 | 2.1381e-05 | 0
[13 empty] | 15:06 | 0.89743 | 0.91146 | 0.91784 |  | 15:06 | 0.90284 | 0.15298 | 4764.3159 | 15:06 | 1.9934 | 1.8324 | 0.16101 | 2.1387e-05 | 0
[13 empty] | 15:06 | 0.88683 | 0.91146 | 0.91784 |  | 15:06 | 0.89213 | 0.15298 | 4777.7804 | 15:06 | 1.9939 | 1.8329 | 0.16105 | 2.1392e-05 | 0
[13 empty] | 15:07 | 0.87645 | 0.91146 | 0.91784 |  | 15:07 | 0.88164 | 0.15298 | 4791.0921 | 15:07 | 1.9944 | 1.8333 | 0.1611 | 2.1398e-05 | 0
[13 empty] | 15:07 | 0.86628 | 0.91146 | 0.91784 |  | 15:07 | 0.87137 | 0.15298 | 4804.2319 | 15:07 | 1.995 | 1.8338 | 0.16114 | 2.1402e-05 | 0
[13 empty] | 15:07 | 0.85633 | 0.91146 | 0.91784 |  | 15:07 | 0.8613 | 0.15298 | 4817.219 | 15:07 | 1.9955 | 1.8343 | 0.16118 | 2.1408e-05 | 0
[13 empty] | 15:08 | 0.84657 | 0.91146 | 0.91784 |  | 15:08 | 0.85145 | 0.15298 | 4830.0723 | 15:08 | 1.996 | 1.8348 | 0.16122 | 2.1413e-05 | 0
[13 empty] | 15:08 | 0.83702 | 0.91146 | 0.91784 |  | 15:08 | 0.8418 | 0.15298 | 4842.7729 | 15:08 | 1.9965 | 1.8352 | 0.16126 | 2.1419e-05 | 0
[13 empty] | 15:08 | 0.82766 | 0.91146 | 0.91784 |  | 15:08 | 0.83234 | 0.15298 | 4855.3207 | 15:08 | 1.997 | 1.8357 | 0.1613 | 2.1425e-05 | 0
[13 empty] | 15:08 | 0.8185 | 0.91146 | 0.91784 |  | 15:08 | 0.82308 | 0.15298 | 4867.7347 | 15:08 | 1.9975 | 1.8362 | 0.16134 | 2.1431e-05 | 0
[13 empty] | 15:08 | 0.80952 | 0.91146 | 0.91784 |  | 15:08 | 0.81401 | 0.15298 | 4880.0151 | 15:08 | 1.998 | 1.8366 | 0.16138 | 2.1434e-05 | 0
[13 empty] | 15:09 | 0.80073 | 0.91146 | 0.91784 |  | 15:09 | 0.80512 | 0.15298 | 4892.1618 | 15:09 | 1.9985 | 1.8371 | 0.16142 | 2.144e-05 | 0
[13 empty] | 15:09 | 0.79211 | 0.91146 | 0.91784 |  | 15:09 | 0.79642 | 0.15298 | 4904.1749 | 15:09 | 1.999 | 1.8375 | 0.16146 | 2.1446e-05 | 0
[13 empty] | 15:09 | 0.78368 | 0.91146 | 0.91784 |  | 15:09 | 0.7879 | 0.15298 | 4916.0542 | 15:09 | 1.9995 | 1.8379 | 0.1615 | 2.1452e-05 | 0
[13 empty] | 15:10 | 0.77542 | 0.91146 | 0.91784 |  | 15:10 | 0.77955 | 0.15298 | 4927.8189 | 15:10 | 1.9999 | 1.8384 | 0.16154 | 2.1455e-05 | 0
[13 empty] | 15:10 | 0.76733 | 0.91146 | 0.91784 |  | 15:10 | 0.77137 | 0.15298 | 4939.45 | 15:10 | 2.0004 | 1.8388 | 0.16157 | 2.1461e-05 | 0
[13 empty] | 15:10 | 0.7594 | 0.91146 | 0.91784 |  | 15:10 | 0.76336 | 0.15298 | 4950.9664 | 15:10 | 2.0008 | 1.8392 | 0.16161 | 2.1465e-05 | 0
[13 empty] | 15:10 | 0.75164 | 0.91146 | 0.91784 |  | 15:10 | 0 | 0.15298 | 4956.6769 | 15:10 | 2.0013 | 1.8396 | 0.16165 | 2.1471e-05 | 0
[13 empty] | 15:10 | 0.74403 | 0.91146 | 0.91784 |  | 15:10 | 0 | 0.15298 | 4956.6769 | 15:10 | 2.0017 | 1.84 | 0.16168 | 2.1474e-05 | 0
[13 empty] | 15:11 | 0.73658 | 0.91146 | 0.91784 |  | 15:11 | 0 | 0.15298 | 4956.6769 | 15:11 | 2.0022 | 1.8405 | 0.16172 | 2.148e-05 | 0
[13 empty] | 15:11 | 0.72929 | 0.91146 | 0.91784 |  | 15:11 | 0 | 0.15298 | 4956.6769 | 15:11 | 2.0026 | 1.8409 | 0.16176 | 2.1484e-05 | 0
[13 empty] | 15:11 | 1.1629 | 0.91146 | 0.91784 |  | 15:11 | 0 | 0.15298 | 4956.6769 | 15:11 | 2.0033 | 1.8415 | 0.16181 | 2.1492e-05 | 0
[13 empty] | 15:12 | 1.1468 | 0.91146 | 0.91784 |  | 15:12 | 0 | 0.15298 | 4956.6769 | 15:12 | 2.004 | 1.8421 | 0.16187 | 2.1499e-05 | 0
[13 empty] | 15:12 | 1.1311 | 0.91146 | 0.91784 |  | 15:12 | 0 | 0.15298 | 4956.6769 | 15:12 | 2.0047 | 1.8428 | 0.16193 | 2.1507e-05 | 0
[13 empty] | 15:12 | 1.1157 | 0.91146 | 0.91784 |  | 15:12 | 0 | 0.15298 | 4956.6769 | 15:12 | 2.0054 | 1.8434 | 0.16198 | 2.1515e-05 | 0
[13 empty] | 15:12 | 1.1006 | 0.91146 | 0.91784 |  | 15:12 | 0 | 0.15298 | 4956.6769 | 15:12 | 2.0061 | 1.844 | 0.16203 | 2.1522e-05 | 0
[13 empty] | 15:12 | 1.0859 | 0.91146 | 0.91784 |  | 15:12 | 0 | 0.15298 | 4956.6769 | 15:12 | 2.0067 | 1.8446 | 0.16209 | 2.1528e-05 | 0
[13 empty] | 15:13 | 1.0714 | 0.91146 | 0.91784 |  | 15:13 | 0 | 0.15298 | 4956.6769 | 15:13 | 2.0074 | 1.8452 | 0.16214 | 2.1536e-05 | 0
[13 empty] | 15:13 | 1.0572 | 0.91146 | 0.91784 |  | 15:13 | 0 | 0.15298 | 4956.6769 | 15:13 | 2.008 | 1.8458 | 0.16219 | 2.1543e-05 | 0
[13 empty] | 15:13 | 1.0434 | 0.91146 | 0.91784 |  | 15:13 | 0 | 0.15298 | 4956.6769 | 15:13 | 2.0086 | 1.8464 | 0.16224 | 2.1549e-05 | 0
[13 empty] | 15:14 | 1.0298 | 0.91146 | 0.91784 |  | 15:14 | 0 | 0.15298 | 4956.6769 | 15:14 | 2.0093 | 1.8469 | 0.16229 | 2.1557e-05 | 0
[13 empty] | 15:14 | 1.0164 | 0.91146 | 0.91784 |  | 15:14 | 0 | 0.15298 | 4956.6769 | 15:14 | 2.0099 | 1.8475 | 0.16234 | 2.1562e-05 | 0
[13 empty] | 15:14 | 1.0034 | 0.91146 | 0.91784 |  | 15:14 | 0 | 0.15298 | 4956.6769 | 15:14 | 2.0105 | 1.8481 | 0.16239 | 2.157e-05 | 0
[13 empty] | 15:14 | 0.99062 | 0.91146 | 0.91784 |  | 15:14 | 0 | 0.15298 | 4956.6769 | 15:14 | 2.0111 | 1.8486 | 0.16244 | 2.1576e-05 | 0
[13 empty] | 15:14 | 0.97811 | 0.91146 | 0.91784 |  | 15:14 | 0 | 0.15298 | 4956.6769 | 15:14 | 2.0117 | 1.8492 | 0.16249 | 2.1581e-05 | 0
[13 empty] | 15:15 | 0.96585 | 0.91146 | 0.91784 |  | 15:15 | 0 | 0.15298 | 4956.6769 | 15:15 | 2.0123 | 1.8497 | 0.16253 | 2.1589e-05 | 0
[13 empty] | 15:15 | 0.95385 | 0.91146 | 0.91784 |  | 15:15 | 0 | 0.15298 | 4956.6769 | 15:15 | 2.0128 | 1.8502 | 0.16258 | 2.1595e-05 | 0
[13 empty] | 15:15 | 0.94209 | 0.91146 | 0.91784 |  | 15:15 | 0 | 0.15298 | 4956.6769 | 15:15 | 2.0134 | 1.8507 | 0.16263 | 2.1601e-05 | 0
[13 empty] | 15:16 | 0.93058 | 0.91146 | 0.91784 |  | 15:16 | 0 | 0.15298 | 4956.6769 | 15:16 | 2.014 | 1.8513 | 0.16267 | 2.1606e-05 | 0
[13 empty] | 15:16 | 0.9193 | 0.91146 | 0.91784 |  | 15:16 | 0 | 0.15298 | 4956.6769 | 15:16 | 2.0145 | 1.8518 | 0.16272 | 2.1612e-05 | 0
[13 empty] | 15:16 | 0.90825 | 0.91146 | 0.91784 |  | 15:16 | 0 | 0.15298 | 4956.6769 | 15:16 | 2.0151 | 1.8523 | 0.16276 | 2.1618e-05 | 0
[13 empty] | 15:16 | 0.89743 | 0.91146 | 0.91784 |  | 15:16 | 0 | 0.15298 | 4956.6769 | 15:16 | 2.0156 | 1.8528 | 0.16281 | 2.1623e-05 | 0
[13 empty] | 15:16 | 0.88683 | 0.91146 | 0.91784 |  | 15:16 | 0 | 0.15298 | 4956.6769 | 15:16 | 2.0162 | 1.8533 | 0.16285 | 2.1629e-05 | 0
[13 empty] | 15:17 | 0.87645 | 0.91146 | 0.91784 |  | 15:17 | 0 | 0.15298 | 4956.6769 | 15:17 | 2.0167 | 1.8538 | 0.16289 | 2.1635e-05 | 0
[13 empty] | 15:17 | 0.86628 | 0.91146 | 0.91784 |  | 15:17 | 0 | 0.15298 | 4956.6769 | 15:17 | 2.0172 | 1.8543 | 0.16293 | 2.1641e-05 | 0
[13 empty] | 15:17 | 0.85633 | 0.91146 | 0.91784 |  | 15:17 | 0 | 0.15298 | 4956.6769 | 15:17 | 2.0177 | 1.8547 | 0.16298 | 2.1646e-05 | 0
[13 empty] | 15:18 | 0.84657 | 0.91146 | 0.91784 |  | 15:18 | 0 | 0.15298 | 4956.6769 | 15:18 | 2.0182 | 1.8552 | 0.16302 | 2.1652e-05 | 0
[13 empty] | 15:18 | 0.83702 | 0.91146 | 0.91784 |  | 15:18 | 0 | 0.15298 | 4956.6769 | 15:18 | 2.0188 | 1.8557 | 0.16306 | 2.1658e-05 | 0
[13 empty] | 15:18 | 0.82766 | 0.91146 | 0.91784 |  | 15:18 | 0 | 0.15298 | 4956.6769 | 15:18 | 2.0193 | 1.8561 | 0.1631 | 2.1664e-05 | 0
[13 empty] | 15:18 | 0.8185 | 0.91146 | 0.91784 |  | 15:18 | 0 | 0.15298 | 4956.6769 | 15:18 | 2.0198 | 1.8566 | 0.16314 | 2.1669e-05 | 0
[13 empty] | 15:18 | 0.80952 | 0.91146 | 0.91784 |  | 15:18 | 0 | 0.15298 | 4956.6769 | 15:18 | 2.0202 | 1.857 | 0.16318 | 2.1673e-05 | 0
[13 empty] | 15:19 | 0.80073 | 0.91146 | 0.91784 |  | 15:19 | 0 | 0.15298 | 4956.6769 | 15:19 | 2.0207 | 1.8575 | 0.16322 | 2.1679e-05 | 0
[13 empty] | 15:19 | 0.79211 | 0.91146 | 0.91784 |  | 15:19 | 0 | 0.15298 | 4956.6769 | 15:19 | 2.0212 | 1.8579 | 0.16326 | 2.1685e-05 | 0
[13 empty] | 15:19 | 0.78368 | 0.91146 | 0.91784 |  | 15:19 | 0 | 0.15298 | 4956.6769 | 15:19 | 2.0217 | 1.8584 | 0.16329 | 2.1688e-05 | 0
[13 empty] | 15:20 | 0.77542 | 0.91146 | 0.91784 |  | 15:20 | 0 | 0.15298 | 4956.6769 | 15:20 | 2.0221 | 1.8588 | 0.16333 | 2.1694e-05 | 0
[13 empty] | 15:20 | 0.76733 | 0.91146 | 0.91784 |  | 15:20 | 0 | 0.15298 | 4956.6769 | 15:20 | 2.0226 | 1.8592 | 0.16337 | 2.17e-05 | 0
[13 empty] | 15:20 | 0.7594 | 0.91146 | 0.91784 |  | 15:20 | 0 | 0.15298 | 4956.6769 | 15:20 | 2.0231 | 1.8596 | 0.16341 | 2.1704e-05 | 0
[13 empty] | 15:20 | 0.75164 | 0.91146 | 0.91784 |  | 15:20 | 0 | 0.15298 | 4956.6769 | 15:20 | 2.0235 | 1.8601 | 0.16344 | 2.1709e-05 | 0
[13 empty] | 15:20 | 0.74403 | 0.91146 | 0.91784 |  | 15:20 | 0 | 0.15298 | 4956.6769 | 15:20 | 2.024 | 1.8605 | 0.16348 | 2.1713e-05 | 0
[13 empty] | 15:21 | 0.73658 | 0.91146 | 0.91784 |  | 15:21 | 0 | 0.15298 | 4956.6769 | 15:21 | 2.0244 | 1.8609 | 0.16352 | 2.1719e-05 | 0
[13 empty] | 15:21 | 0.72929 | 0.91146 | 0.91784 |  | 15:21 | 0 | 0.15298 | 4956.6769 | 15:21 | 2.0249 | 1.8613 | 0.16355 | 2.1723e-05 | 0
[13 empty] | 15:21 | 1.1629 | 0.91146 | 0.91784 |  | 15:21 | 0 | 0.15298 | 4956.6769 | 15:21 | 2.0256 | 1.8619 | 0.16361 | 2.173e-05 | 0
[13 empty] | 15:22 | 1.1468 | 0.91146 | 0.91784 |  | 15:22 | 0 | 0.15298 | 4956.6769 | 15:22 | 2.0263 | 1.8626 | 0.16367 | 2.1738e-05 | 0
[13 empty] | 15:22 | 1.1311 | 0.91146 | 0.91784 |  | 15:22 | 0 | 0.15298 | 4956.6769 | 15:22 | 2.0269 | 1.8632 | 0.16372 | 2.1746e-05 | 0
[13 empty] | 15:22 | 1.1157 | 0.91146 | 0.91784 |  | 15:22 | 0 | 0.15298 | 4956.6769 | 15:22 | 2.0276 | 1.8638 | 0.16378 | 2.1753e-05 | 0
[13 empty] | 15:22 | 1.1006 | 0.91146 | 0.91784 |  | 15:22 | 0 | 0.15298 | 4956.6769 | 15:22 | 2.0283 | 1.8644 | 0.16383 | 2.1761e-05 | 0
[13 empty] | 15:22 | 1.0859 | 0.91146 | 0.91784 |  | 15:22 | 0 | 0.15298 | 4956.6769 | 15:22 | 2.0289 | 1.865 | 0.16388 | 2.1767e-05 | 0
[13 empty] | 15:23 | 1.0714 | 0.91146 | 0.91784 |  | 15:23 | 0 | 0.15298 | 4956.6769 | 15:23 | 2.0296 | 1.8656 | 0.16393 | 2.1774e-05 | 0
[13 empty] | 15:23 | 1.0572 | 0.91146 | 0.91784 |  | 15:23 | 0 | 0.15298 | 4956.6769 | 15:23 | 2.0302 | 1.8662 | 0.16399 | 2.1782e-05 | 0
[13 empty] | 15:23 | 1.0434 | 0.91146 | 0.91784 |  | 15:23 | 0 | 0.15298 | 4956.6769 | 15:23 | 2.0309 | 1.8668 | 0.16404 | 2.1788e-05 | 0
[13 empty] | 15:24 | 1.0298 | 0.91146 | 0.91784 |  | 15:24 | 0 | 0.15298 | 4956.6769 | 15:24 | 2.0315 | 1.8674 | 0.16409 | 2.1795e-05 | 0
[13 empty] | 15:24 | 1.0164 | 0.91146 | 0.91784 |  | 15:24 | 0 | 0.15298 | 4956.6769 | 15:24 | 2.0321 | 1.8679 | 0.16414 | 2.1801e-05 | 0
[13 empty] | 15:24 | 1.0034 | 0.91146 | 0.91784 |  | 15:24 | 0 | 0.15298 | 4956.6769 | 15:24 | 2.0327 | 1.8685 | 0.16419 | 2.1807e-05 | 0
[13 empty] | 15:24 | 0.99062 | 0.91146 | 0.91784 |  | 15:24 | 0 | 0.15298 | 4956.6769 | 15:24 | 2.0333 | 1.869 | 0.16423 | 2.1814e-05 | 0
[13 empty] | 15:24 | 0.97811 | 0.91146 | 0.91784 |  | 15:24 | 0 | 0.15298 | 4956.6769 | 15:24 | 2.0339 | 1.8696 | 0.16428 | 2.182e-05 | 0
[13 empty] | 15:25 | 0.96585 | 0.91146 | 0.91784 |  | 15:25 | 0 | 0.15298 | 4956.6769 | 15:25 | 2.0345 | 1.8701 | 0.16433 | 2.1826e-05 | 0
[13 empty] | 15:25 | 0.95385 | 0.91146 | 0.91784 |  | 15:25 | 0 | 0.15298 | 4956.6769 | 15:25 | 2.0351 | 1.8707 | 0.16438 | 2.1834e-05 | 0
[13 empty] | 15:25 | 0.94209 | 0.91146 | 0.91784 |  | 15:25 | 0 | 0.15298 | 4956.6769 | 15:25 | 2.0356 | 1.8712 | 0.16442 | 2.1839e-05 | 0
[13 empty] | 15:26 | 0.93058 | 0.91146 | 0.91784 |  | 15:26 | 0 | 0.15298 | 4956.6769 | 15:26 | 2.0362 | 1.8717 | 0.16447 | 2.1845e-05 | 0
[13 empty] | 15:26 | 0.9193 | 0.91146 | 0.91784 |  | 15:26 | 0 | 0.15298 | 4956.6769 | 15:26 | 2.0368 | 1.8722 | 0.16451 | 2.1851e-05 | 0
[13 empty] | 15:26 | 0.90825 | 0.91146 | 0.91784 |  | 15:26 | 0 | 0.15298 | 4956.6769 | 15:26 | 2.0373 | 1.8727 | 0.16456 | 2.1856e-05 | 0
[13 empty] | 15:26 | 0.89743 | 0.91146 | 0.91784 |  | 15:26 | 0 | 0.15298 | 4956.6769 | 15:26 | 2.0379 | 1.8732 | 0.1646 | 2.1862e-05 | 0
[13 empty] | 15:26 | 0.88683 | 0.91146 | 0.91784 |  | 15:26 | 0 | 0.15298 | 4956.6769 | 15:26 | 2.0384 | 1.8737 | 0.16465 | 2.1868e-05 | 0
[13 empty] | 15:27 | 0.87645 | 0.91146 | 0.91784 |  | 15:27 | 0 | 0.15298 | 4956.6769 | 15:27 | 2.0389 | 1.8742 | 0.16469 | 2.1874e-05 | 0
[13 empty] | 15:27 | 0.86628 | 0.91146 | 0.91784 |  | 15:27 | 0 | 0.15298 | 4956.6769 | 15:27 | 2.0394 | 1.8747 | 0.16473 | 2.1879e-05 | 0
[13 empty] | 15:27 | 0.85633 | 0.91146 | 0.91784 |  | 15:27 | 0 | 0.15298 | 4956.6769 | 15:27 | 2.04 | 1.8752 | 0.16477 | 2.1885e-05 | 0
[13 empty] | 15:28 | 0.84657 | 0.91146 | 0.91784 |  | 15:28 | 0 | 0.15298 | 4956.6769 | 15:28 | 2.0405 | 1.8756 | 0.16481 | 2.1891e-05 | 0
[13 empty] | 15:28 | 0.83702 | 0.91146 | 0.91784 |  | 15:28 | 0 | 0.15298 | 4956.6769 | 15:28 | 2.041 | 1.8761 | 0.16485 | 2.1897e-05 | 0
[13 empty] | 15:28 | 0.82766 | 0.91146 | 0.91784 |  | 15:28 | 0 | 0.15298 | 4956.6769 | 15:28 | 2.0415 | 1.8766 | 0.1649 | 2.1902e-05 | 0
[13 empty] | 15:28 | 0.8185 | 0.91146 | 0.91784 |  | 15:28 | 0 | 0.15298 | 4956.6769 | 15:28 | 2.042 | 1.877 | 0.16494 | 2.1906e-05 | 0
[13 empty] | 15:28 | 0.80952 | 0.91146 | 0.91784 |  | 15:28 | 0 | 0.15298 | 4956.6769 | 15:28 | 2.0425 | 1.8775 | 0.16497 | 2.1912e-05 | 0
[13 empty] | 15:29 | 0.80073 | 0.91146 | 0.91784 |  | 15:29 | 0 | 0.15298 | 4956.6769 | 15:29 | 2.0429 | 1.8779 | 0.16501 | 2.1918e-05 | 0
[13 empty] | 15:29 | 0.79211 | 0.91146 | 0.91784 |  | 15:29 | 0 | 0.15298 | 4956.6769 | 15:29 | 2.0434 | 1.8783 | 0.16505 | 2.1923e-05 | 0
[13 empty] | 15:29 | 0.78368 | 0.91146 | 0.91784 |  | 15:29 | 0 | 0.15298 | 4956.6769 | 15:29 | 2.0439 | 1.8788 | 0.16509 | 2.1927e-05 | 0
[13 empty] | 15:30 | 0.77542 | 0.91146 | 0.91784 |  | 15:30 | 0 | 0.15298 | 4956.6769 | 15:30 | 2.0444 | 1.8792 | 0.16513 | 2.1933e-05 | 0
[13 empty] | 15:30 | 0.76733 | 0.91146 | 0.91784 |  | 15:30 | 0 | 0.15298 | 4956.6769 | 15:30 | 2.0448 | 1.8796 | 0.16517 | 2.1939e-05 | 0
[13 empty] | 15:30 | 0.7594 | 0.91146 | 0.91784 |  | 15:30 | 0 | 0.15298 | 4956.6769 | 15:30 | 2.0453 | 1.8801 | 0.1652 | 2.1942e-05 | 0
[13 empty] | 15:30 | 0.75164 | 0.91146 | 0.91784 |  | 15:30 | 0 | 0.15298 | 4956.6769 | 15:30 | 2.0457 | 1.8805 | 0.16524 | 2.1948e-05 | 0
[13 empty] | 15:30 | 0.74403 | 0.91146 | 0.91784 |  | 15:30 | 0 | 0.15298 | 4956.6769 | 15:30 | 2.0462 | 1.8809 | 0.16528 | 2.1952e-05 | 0
[13 empty] | 15:31 | 0.73658 | 0.91146 | 0.91784 |  | 15:31 | 0 | 0.15298 | 4956.6769 | 15:31 | 2.0466 | 1.8813 | 0.16531 | 2.1958e-05 | 0
[13 empty] | 15:31 | 0.72929 | 0.91146 | 0.91784 |  | 15:31 | 0 | 0.15298 | 4956.6769 | 15:31 | 2.0471 | 1.8817 | 0.16535 | 2.1961e-05 | 0
[13 empty] | 15:31 | 1.1629 | 0.91146 | 0.91784 |  | 15:31 | 0 | 0.15298 | 4956.6769 | 15:31 | 2.0478 | 1.8824 | 0.16541 | 2.1969e-05 | 0
[13 empty] | 15:32 | 1.1468 | 0.91146 | 0.91784 |  | 15:32 | 0 | 0.15298 | 4956.6769 | 15:32 | 2.0485 | 1.883 | 0.16546 | 2.1977e-05 | 0
[13 empty] | 15:32 | 1.1311 | 0.91146 | 0.91784 |  | 15:32 | 0 | 0.15298 | 4956.6769 | 15:32 | 2.0492 | 1.8836 | 0.16552 | 2.1984e-05 | 0
[13 empty] | 15:32 | 1.1157 | 0.91146 | 0.91784 |  | 15:32 | 0 | 0.15298 | 4956.6769 | 15:32 | 2.0498 | 1.8842 | 0.16557 | 2.1992e-05 | 0
[13 empty] | 15:32 | 1.1006 | 0.91146 | 0.91784 |  | 15:32 | 0 | 0.15298 | 4956.6769 | 15:32 | 2.0505 | 1.8849 | 0.16562 | 2.1998e-05 | 0
[13 empty] | 15:32 | 1.0859 | 0.91146 | 0.91784 |  | 15:32 | 0 | 0.15298 | 4956.6769 | 15:32 | 2.0512 | 1.8855 | 0.16568 | 2.2005e-05 | 0
[13 empty] | 15:33 | 1.0714 | 0.91146 | 0.91784 |  | 15:33 | 0 | 0.15298 | 4956.6769 | 15:33 | 2.0518 | 1.8861 | 0.16573 | 2.2013e-05 | 0
[13 empty] | 15:33 | 1.0572 | 0.91146 | 0.91784 |  | 15:33 | 0 | 0.15298 | 4956.6769 | 15:33 | 2.0525 | 1.8867 | 0.16578 | 2.2019e-05 | 0
[13 empty] | 15:33 | 1.0434 | 0.91146 | 0.91784 |  | 15:33 | 0 | 0.15298 | 4956.6769 | 15:33 | 2.0531 | 1.8872 | 0.16583 | 2.2026e-05 | 0
[13 empty] | 15:34 | 1.0298 | 0.91146 | 0.91784 |  | 15:34 | 0 | 0.15298 | 4956.6769 | 15:34 | 2.0537 | 1.8878 | 0.16588 | 2.2032e-05 | 0
[13 empty] | 15:34 | 1.0164 | 0.91146 | 0.91784 |  | 15:34 | 0 | 0.15298 | 4956.6769 | 15:34 | 2.0543 | 1.8884 | 0.16593 | 2.204e-05 | 0
[13 empty] | 15:34 | 1.0034 | 0.91146 | 0.91784 |  | 15:34 | 0 | 0.15298 | 4956.6769 | 15:34 | 2.0549 | 1.8889 | 0.16598 | 2.2046e-05 | 0
[13 empty] | 15:34 | 0.99062 | 0.91146 | 0.91784 |  | 15:34 | 0 | 0.15298 | 4956.6769 | 15:34 | 2.0555 | 1.8895 | 0.16603 | 2.2053e-05 | 0
[13 empty] | 15:34 | 0.97811 | 0.91146 | 0.91784 |  | 15:34 | 0 | 0.15298 | 4956.6769 | 15:34 | 2.0561 | 1.89 | 0.16608 | 2.2059e-05 | 0
[13 empty] | 15:35 | 0.96585 | 0.91146 | 0.91784 |  | 15:35 | 0 | 0.15298 | 4956.6769 | 15:35 | 2.0567 | 1.8906 | 0.16613 | 2.2065e-05 | 0
[13 empty] | 15:35 | 0.95385 | 0.91146 | 0.91784 |  | 15:35 | 0 | 0.15298 | 4956.6769 | 15:35 | 2.0573 | 1.8911 | 0.16617 | 2.2072e-05 | 0
[13 empty] | 15:35 | 0.94209 | 0.91146 | 0.91784 |  | 15:35 | 0 | 0.15298 | 4956.6769 | 15:35 | 2.0579 | 1.8916 | 0.16622 | 2.2078e-05 | 0
[13 empty] | 15:36 | 0.93058 | 0.91146 | 0.91784 |  | 15:36 | 0 | 0.15298 | 4956.6769 | 15:36 | 2.0584 | 1.8921 | 0.16626 | 2.2084e-05 | 0
[13 empty] | 15:36 | 0.9193 | 0.91146 | 0.91784 |  | 15:36 | 0 | 0.15298 | 4956.6769 | 15:36 | 2.059 | 1.8927 | 0.16631 | 2.2089e-05 | 0
[13 empty] | 15:36 | 0.90825 | 0.91146 | 0.91784 |  | 15:36 | 0 | 0.15298 | 4956.6769 | 15:36 | 2.0595 | 1.8931 | 0.16635 | 2.2095e-05 | 0
[13 empty] | 15:36 | 0.89743 | 0.91146 | 0.91784 |  | 15:36 | 0 | 0.15298 | 4956.6769 | 15:36 | 2.0601 | 1.8937 | 0.1664 | 2.2101e-05 | 0
[13 empty] | 15:36 | 0.88683 | 0.91146 | 0.91784 |  | 15:36 | 0 | 0.15298 | 4956.6769 | 15:36 | 2.0606 | 1.8941 | 0.16644 | 2.2107e-05 | 0
[13 empty] | 15:37 | 0.87645 | 0.91146 | 0.91784 |  | 15:37 | 0 | 0.15298 | 4956.6769 | 15:37 | 2.0611 | 1.8946 | 0.16648 | 2.2112e-05 | 0
[13 empty] | 15:37 | 0.86628 | 0.91146 | 0.91784 |  | 15:37 | 0 | 0.15298 | 4956.6769 | 15:37 | 2.0617 | 1.8951 | 0.16652 | 2.2118e-05 | 0
[13 empty] | 15:37 | 0.85633 | 0.91146 | 0.91784 |  | 15:37 | 0 | 0.15298 | 4956.6769 | 15:37 | 2.0622 | 1.8956 | 0.16657 | 2.2124e-05 | 0
[13 empty] | 15:38 | 0.84657 | 0.91146 | 0.91784 |  | 15:38 | 0 | 0.15298 | 4956.6769 | 15:38 | 2.0627 | 1.8961 | 0.16661 | 2.213e-05 | 0
[13 empty] | 15:38 | 0.83702 | 0.91146 | 0.91784 |  | 15:38 | 0 | 0.15298 | 4956.6769 | 15:38 | 2.0632 | 1.8965 | 0.16665 | 2.2135e-05 | 0
[13 empty] | 15:38 | 0.82766 | 0.91146 | 0.91784 |  | 15:38 | 0 | 0.15298 | 4956.6769 | 15:38 | 2.0637 | 1.897 | 0.16669 | 2.2141e-05 | 0
[13 empty] | 15:38 | 0.8185 | 0.91146 | 0.91784 |  | 15:38 | 0 | 0.15298 | 4956.6769 | 15:38 | 2.0642 | 1.8974 | 0.16673 | 2.2145e-05 | 0
[13 empty] | 15:39 | 0.80952 | 0.91146 | 0.91784 |  | 15:39 | 0 | 0.15298 | 4956.6769 | 15:39 | 2.0647 | 1.8979 | 0.16677 | 2.2151e-05 | 0
[13 empty] | 15:39 | 0.80073 | 0.91146 | 0.91784 |  | 15:39 | 0 | 0.15298 | 4956.6769 | 15:39 | 2.0652 | 1.8983 | 0.16681 | 2.2156e-05 | 0
[13 empty] | 15:39 | 0.79211 | 0.91146 | 0.91784 |  | 15:39 | 0 | 0.15298 | 4956.6769 | 15:39 | 2.0657 | 1.8988 | 0.16685 | 2.216e-05 | 0
[13 empty] | 15:39 | 0.78368 | 0.91146 | 0.91784 |  | 15:39 | 0 | 0.15298 | 4956.6769 | 15:39 | 2.0661 | 1.8992 | 0.16689 | 2.2166e-05 | 0
[13 empty] | 15:39 | 0.77542 | 0.91146 | 0.91784 |  | 15:39 | 0 | 0.15298 | 4956.6769 | 15:39 | 2.0666 | 1.8997 | 0.16692 | 2.2172e-05 | 0
[13 empty] | 15:40 | 0.76733 | 0.91146 | 0.91784 |  | 15:40 | 0 | 0.15298 | 4956.6769 | 15:40 | 2.0671 | 1.9001 | 0.16696 | 2.2175e-05 | 0
[13 empty] | 15:40 | 0.7594 | 0.91146 | 0.91784 |  | 15:40 | 0 | 0.15298 | 4956.6769 | 15:40 | 2.0675 | 1.9005 | 0.167 | 2.2181e-05 | 0
[13 empty] | 15:40 | 0.75164 | 0.91146 | 0.91784 |  | 15:40 | 0 | 0.15298 | 4956.6769 | 15:40 | 2.068 | 1.9009 | 0.16703 | 2.2187e-05 | 0
[13 empty] | 15:41 | 0.74403 | 0.91146 | 0.91784 |  | 15:41 | 0 | 0.15298 | 4956.6769 | 15:41 | 2.0684 | 1.9013 | 0.16707 | 2.2191e-05 | 0
[13 empty] | 15:41 | 0.73658 | 0.91146 | 0.91784 |  | 15:41 | 0 | 0.15298 | 4956.6769 | 15:41 | 2.0689 | 1.9017 | 0.16711 | 2.2196e-05 | 0
[13 empty] | 15:41 | 0.72929 | 0.91146 | 0.91784 |  | 15:41 | 0 | 0.15298 | 4956.6769 | 15:41 | 2.0693 | 1.9021 | 0.16714 | 2.22e-05 | 0
[13 empty] | 15:41 | 1.1629 | 0.91146 | 0.91784 |  | 15:41 | 0 | 0.15298 | 4956.6769 | 15:41 | 2.07 | 1.9028 | 0.1672 | 2.2208e-05 | 0
[13 empty] | 15:41 | 1.1468 | 0.91146 | 0.91784 |  | 15:41 | 0 | 0.15298 | 4956.6769 | 15:41 | 2.0707 | 1.9034 | 0.16726 | 2.2215e-05 | 0
[13 empty] | 15:42 | 1.1311 | 0.91146 | 0.91784 |  | 15:42 | 0 | 0.15298 | 4956.6769 | 15:42 | 2.0714 | 1.9041 | 0.16731 | 2.2223e-05 | 0
[13 empty] | 15:42 | 1.1157 | 0.91146 | 0.91784 |  | 15:42 | 0 | 0.15298 | 4956.6769 | 15:42 | 2.0721 | 1.9047 | 0.16737 | 2.2231e-05 | 0
[13 empty] | 15:42 | 1.1006 | 0.91146 | 0.91784 |  | 15:42 | 0 | 0.15298 | 4956.6769 | 15:42 | 2.0727 | 1.9053 | 0.16742 | 2.2236e-05 | 0
[13 empty] | 15:43 | 1.0859 | 0.91146 | 0.91784 |  | 15:43 | 0 | 0.15298 | 4956.6769 | 15:43 | 2.0734 | 1.9059 | 0.16747 | 2.2244e-05 | 0
[13 empty] | 15:43 | 1.0714 | 0.91146 | 0.91784 |  | 15:43 | 0 | 0.15298 | 4956.6769 | 15:43 | 2.074 | 1.9065 | 0.16753 | 2.2252e-05 | 0
[13 empty] | 15:43 | 1.0572 | 0.91146 | 0.91784 |  | 15:43 | 0 | 0.15298 | 4956.6769 | 15:43 | 2.0747 | 1.9071 | 0.16758 | 2.2258e-05 | 0
[13 empty] | 15:43 | 1.0434 | 0.91146 | 0.91784 |  | 15:43 | 0 | 0.15298 | 4956.6769 | 15:43 | 2.0753 | 1.9077 | 0.16763 | 2.2265e-05 | 0
[13 empty] | 15:43 | 1.0298 | 0.91146 | 0.91784 |  | 15:43 | 0 | 0.15298 | 4956.6769 | 15:43 | 2.0759 | 1.9082 | 0.16768 | 2.2271e-05 | 0
[13 empty] | 15:44 | 1.0164 | 0.91146 | 0.91784 |  | 15:44 | 0 | 0.15298 | 4956.6769 | 15:44 | 2.0766 | 1.9088 | 0.16773 | 2.2279e-05 | 0
[13 empty] | 15:44 | 1.0034 | 0.91146 | 0.91784 |  | 15:44 | 0 | 0.15298 | 4956.6769 | 15:44 | 2.0772 | 1.9094 | 0.16778 | 2.2284e-05 | 0
[13 empty] | 15:44 | 0.99062 | 0.91146 | 0.91784 |  | 15:44 | 0 | 0.15298 | 4956.6769 | 15:44 | 2.0777 | 1.9099 | 0.16783 | 2.2292e-05 | 0
[13 empty] | 15:45 | 0.97811 | 0.91146 | 0.91784 |  | 15:45 | 0 | 0.15298 | 4956.6769 | 15:45 | 2.0783 | 1.9104 | 0.16787 | 2.2298e-05 | 0
[13 empty] | 15:45 | 0.96585 | 0.91146 | 0.91784 |  | 15:45 | 0 | 0.15298 | 4956.6769 | 15:45 | 2.0789 | 1.911 | 0.16792 | 2.2303e-05 | 0
[13 empty] | 15:45 | 0.95385 | 0.91146 | 0.91784 |  | 15:45 | 0 | 0.15298 | 4956.6769 | 15:45 | 2.0796 | 1.9116 | 0.16797 | 2.2309e-05 | 0
[13 empty] | 15:45 | 0.94209 | 0.91146 | 0.91784 |  | 15:45 | 0 | 0.15298 | 4956.6769 | 15:45 | 2.08 | 1.912 | 0.16801 | 2.2317e-05 | 0
[13 empty] | 15:45 | 0.93058 | 0.91146 | 0.91784 |  | 15:45 | 0 | 0.15298 | 4956.6769 | 15:45 | 2.0806 | 1.9125 | 0.16806 | 2.2322e-05 | 0
[13 empty] | 15:46 | 0.9193 | 0.91146 | 0.91784 |  | 15:46 | 0 | 0.15298 | 4956.6769 | 15:46 | 2.0812 | 1.9131 | 0.1681 | 2.2328e-05 | 0
[13 empty] | 15:46 | 0.90825 | 0.91146 | 0.91784 |  | 15:46 | 0 | 0.15298 | 4956.6769 | 15:46 | 2.0818 | 1.9137 | 0.16815 | 2.2334e-05 | 0
[13 empty] | 15:46 | 0.89743 | 0.91146 | 0.91784 |  | 15:46 | 0 | 0.15298 | 4956.6769 | 15:46 | 2.0823 | 1.9141 | 0.16819 | 2.234e-05 | 0
[13 empty] | 15:47 | 0.88683 | 0.91146 | 0.91784 |  | 15:47 | 0 | 0.15298 | 4956.6769 | 15:47 | 2.0829 | 1.9146 | 0.16824 | 2.2345e-05 | 0
[13 empty] | 15:47 | 0.87645 | 0.91146 | 0.91784 |  | 15:47 | 0 | 0.15298 | 4956.6769 | 15:47 | 2.0833 | 1.915 | 0.16828 | 2.2351e-05 | 0
[13 empty] | 15:47 | 0.86628 | 0.91146 | 0.91784 |  | 15:47 | 0 | 0.15298 | 4956.6769 | 15:47 | 2.0839 | 1.9156 | 0.16832 | 2.2357e-05 | 0
[13 empty] | 15:47 | 0.85633 | 0.91146 | 0.91784 |  | 15:47 | 0 | 0.15298 | 4956.6769 | 15:47 | 2.0844 | 1.916 | 0.16836 | 2.2363e-05 | 0
[13 empty] | 15:47 | 0.84657 | 0.91146 | 0.91784 |  | 15:47 | 0 | 0.15298 | 4956.6769 | 15:47 | 2.085 | 1.9165 | 0.1684 | 2.2368e-05 | 0
[13 empty] | 15:48 | 0.83702 | 0.91146 | 0.91784 |  | 15:48 | 0 | 0.15298 | 4956.6769 | 15:48 | 2.0854 | 1.9169 | 0.16845 | 2.2374e-05 | 0
[13 empty] | 15:48 | 0.82766 | 0.91146 | 0.91784 |  | 15:48 | 0 | 0.15298 | 4956.6769 | 15:48 | 2.086 | 1.9175 | 0.16849 | 2.2378e-05 | 0
[13 empty] | 15:48 | 0.8185 | 0.91146 | 0.91784 |  | 15:48 | 0 | 0.15298 | 4956.6769 | 15:48 | 2.0864 | 1.9179 | 0.16853 | 2.2384e-05 | 0
[13 empty] | 15:49 | 0.80952 | 0.91146 | 0.91784 |  | 15:49 | 0 | 0.15298 | 4956.6769 | 15:49 | 2.0868 | 1.9183 | 0.16856 | 2.2389e-05 | 0
[13 empty] | 15:49 | 0.80073 | 0.91146 | 0.91784 |  | 15:49 | 0 | 0.15298 | 4956.6769 | 15:49 | 2.0875 | 1.9188 | 0.1686 | 2.2395e-05 | 0
[13 empty] | 15:49 | 0.79211 | 0.91146 | 0.91784 |  | 15:49 | 0 | 0.15298 | 4956.6769 | 15:49 | 2.0879 | 1.9192 | 0.16864 | 2.2399e-05 | 0
[13 empty] | 15:49 | 0.78368 | 0.91146 | 0.91784 |  | 15:49 | 0 | 0.15298 | 4956.6769 | 15:49 | 2.0883 | 1.9196 | 0.16868 | 2.2405e-05 | 0
[13 empty] | 15:49 | 0.77542 | 0.91146 | 0.91784 |  | 15:49 | 0 | 0.15298 | 4956.6769 | 15:49 | 2.0889 | 1.9202 | 0.16872 | 2.241e-05 | 0
[13 empty] | 15:50 | 0.76733 | 0.91146 | 0.91784 |  | 15:50 | 0 | 0.15298 | 4956.6769 | 15:50 | 2.0893 | 1.9206 | 0.16876 | 2.2414e-05 | 0
[13 empty] | 15:50 | 0.7594 | 0.91146 | 0.91784 |  | 15:50 | 0 | 0.15298 | 4956.6769 | 15:50 | 2.0898 | 1.9209 | 0.16879 | 2.242e-05 | 0
[13 empty] | 15:50 | 0.75164 | 0.91146 | 0.91784 |  | 15:50 | 0 | 0.15298 | 4956.6769 | 15:50 | 2.0902 | 1.9213 | 0.16883 | 2.2424e-05 | 0
[13 empty] | 15:51 | 0.74403 | 0.91146 | 0.91784 |  | 15:51 | 0 | 0.15298 | 4956.6769 | 15:51 | 2.0906 | 1.9217 | 0.16887 | 2.2429e-05 | 0
[13 empty] | 15:51 | 0.73658 | 0.91146 | 0.91784 |  | 15:51 | 0 | 0.15298 | 4956.6769 | 15:51 | 2.0912 | 1.9223 | 0.1689 | 2.2433e-05 | 0
[13 empty] | 15:51 | 0.72929 | 0.91146 | 0.91784 |  | 15:51 | 0 | 0.15298 | 4956.6769 | 15:51 | 2.0916 | 1.9227 | 0.16894 | 2.2439e-05 | 0
[13 empty] | 15:51 | 1.1629 | 0.91146 | 0.91784 |  | 15:51 | 0 | 0.15298 | 4956.6769 | 15:51 | 2.0922 | 1.9232 | 0.169 | 2.2447e-05 | 0
[13 empty] | 15:51 | 1.1468 | 0.91146 | 0.91784 |  | 15:51 | 0 | 0.15298 | 4956.6769 | 15:51 | 2.0929 | 1.9238 | 0.16905 | 2.2454e-05 | 0
[13 empty] | 15:52 | 1.1311 | 0.91146 | 0.91784 |  | 15:52 | 0 | 0.15298 | 4956.6769 | 15:52 | 2.0937 | 1.9246 | 0.16911 | 2.2462e-05 | 0
[13 empty] | 15:52 | 1.1157 | 0.91146 | 0.91784 |  | 15:52 | 0 | 0.15298 | 4956.6769 | 15:52 | 2.0943 | 1.9251 | 0.16916 | 2.2468e-05 | 0
[13 empty] | 15:52 | 1.1006 | 0.91146 | 0.91784 |  | 15:52 | 0 | 0.15298 | 4956.6769 | 15:52 | 2.0949 | 1.9257 | 0.16922 | 2.2475e-05 | 0
[13 empty] | 15:52 | 1.0859 | 0.91146 | 0.91784 |  | 15:52 | 0 | 0.15298 | 4956.6769 | 15:52 | 2.0956 | 1.9263 | 0.16927 | 2.2483e-05 | 0
[13 empty] | 15:53 | 1.0714 | 0.91146 | 0.91784 |  | 15:53 | 0 | 0.15298 | 4956.6769 | 15:53 | 2.0962 | 1.9269 | 0.16932 | 2.2489e-05 | 0
[13 empty] | 15:53 | 1.0572 | 0.91146 | 0.91784 |  | 15:53 | 0 | 0.15298 | 4956.6769 | 15:53 | 2.0968 | 1.9274 | 0.16937 | 2.2496e-05 | 0
[13 empty] | 15:53 | 1.0434 | 0.91146 | 0.91784 |  | 15:53 | 0 | 0.15298 | 4956.6769 | 15:53 | 2.0976 | 1.9282 | 0.16942 | 2.2504e-05 | 0
[13 empty] | 15:54 | 1.0298 | 0.91146 | 0.91784 |  | 15:54 | 0 | 0.15298 | 4956.6769 | 15:54 | 2.0983 | 1.9288 | 0.16947 | 2.251e-05 | 0
[13 empty] | 15:54 | 1.0164 | 0.91146 | 0.91784 |  | 15:54 | 0 | 0.15298 | 4956.6769 | 15:54 | 2.0987 | 1.9291 | 0.16952 | 2.2517e-05 | 0
[13 empty] | 15:54 | 1.0034 | 0.91146 | 0.91784 |  | 15:54 | 0 | 0.15298 | 4956.6769 | 15:54 | 2.0993 | 1.9297 | 0.16957 | 2.2523e-05 | 0
[13 empty] | 15:54 | 0.99062 | 0.91146 | 0.91784 |  | 15:54 | 0 | 0.15298 | 4956.6769 | 15:54 | 2.0999 | 1.9303 | 0.16962 | 2.2529e-05 | 0
[13 empty] | 15:54 | 0.97811 | 0.91146 | 0.91784 |  | 15:54 | 0 | 0.15298 | 4956.6769 | 15:54 | 2.1006 | 1.9309 | 0.16967 | 2.2536e-05 | 0
[13 empty] | 15:55 | 0.96585 | 0.91146 | 0.91784 |  | 15:55 | 0 | 0.15298 | 4956.6769 | 15:55 | 2.1012 | 1.9314 | 0.16972 | 2.2542e-05 | 0
[13 empty] | 15:55 | 0.95385 | 0.91146 | 0.91784 |  | 15:55 | 0 | 0.15298 | 4956.6769 | 15:55 | 2.1018 | 1.932 | 0.16976 | 2.2548e-05 | 0
[13 empty] | 15:55 | 0.94209 | 0.91146 | 0.91784 |  | 15:55 | 0 | 0.15298 | 4956.6769 | 15:55 | 2.1022 | 1.9324 | 0.16981 | 2.2554e-05 | 0
[13 empty] | 15:56 | 0.93058 | 0.91146 | 0.91784 |  | 15:56 | 0 | 0.15298 | 4956.6769 | 15:56 | 2.1028 | 1.933 | 0.16986 | 2.2561e-05 | 0
[13 empty] | 15:56 | 0.9193 | 0.91146 | 0.91784 |  | 15:56 | 0 | 0.15298 | 4956.6769 | 15:56 | 2.1035 | 1.9335 | 0.1699 | 2.2567e-05 | 0
[13 empty] | 15:56 | 0.90825 | 0.91146 | 0.91784 |  | 15:56 | 0 | 0.15298 | 4956.6769 | 15:56 | 2.1041 | 1.9341 | 0.16994 | 2.2573e-05 | 0
[13 empty] | 15:56 | 0.89743 | 0.91146 | 0.91784 |  | 15:56 | 0 | 0.15298 | 4956.6769 | 15:56 | 2.1045 | 1.9345 | 0.16999 | 2.2578e-05 | 0
[13 empty] | 15:56 | 0.88683 | 0.91146 | 0.91784 |  | 15:56 | 0 | 0.15298 | 4956.6769 | 15:56 | 2.1051 | 1.9351 | 0.17003 | 2.2584e-05 | 0
[13 empty] | 15:57 | 0.87645 | 0.91146 | 0.91784 |  | 15:57 | 0 | 0.15298 | 4956.6769 | 15:57 | 2.1055 | 1.9355 | 0.17007 | 2.259e-05 | 0
[13 empty] | 15:57 | 0.86628 | 0.91146 | 0.91784 |  | 15:57 | 0 | 0.15298 | 4956.6769 | 15:57 | 2.1062 | 1.936 | 0.17012 | 2.2596e-05 | 0
[13 empty] | 15:57 | 0.85633 | 0.91146 | 0.91784 |  | 15:57 | 0 | 0.15298 | 4956.6769 | 15:57 | 2.1066 | 1.9364 | 0.17016 | 2.2601e-05 | 0
[13 empty] | 15:58 | 0.84657 | 0.91146 | 0.91784 |  | 15:58 | 0 | 0.15298 | 4956.6769 | 15:58 | 2.1072 | 1.937 | 0.1702 | 2.2607e-05 | 0
[13 empty] | 15:58 | 0.83702 | 0.91146 | 0.91784 |  | 15:58 | 0 | 0.15298 | 4956.6769 | 15:58 | 2.1076 | 1.9374 | 0.17024 | 2.2611e-05 | 0
[13 empty] | 15:58 | 0.82766 | 0.91146 | 0.91784 |  | 15:58 | 0 | 0.15298 | 4956.6769 | 15:58 | 2.1082 | 1.9379 | 0.17028 | 2.2617e-05 | 0
[13 empty] | 15:58 | 0.8185 | 0.91146 | 0.91784 |  | 15:58 | 0 | 0.15298 | 4956.6769 | 15:58 | 2.1087 | 1.9383 | 0.17032 | 2.2622e-05 | 0
[13 empty] | 15:58 | 0.80952 | 0.91146 | 0.91784 |  | 15:58 | 0 | 0.15298 | 4956.6769 | 15:58 | 2.1091 | 1.9387 | 0.17036 | 2.2628e-05 | 0
[13 empty] | 15:59 | 0.80073 | 0.91146 | 0.91784 |  | 15:59 | 0 | 0.15298 | 4956.6769 | 15:59 | 2.1097 | 1.9393 | 0.1704 | 2.2634e-05 | 0
[13 empty] | 15:59 | 0.79211 | 0.91146 | 0.91784 |  | 15:59 | 0 | 0.15298 | 4956.6769 | 15:59 | 2.1101 | 1.9397 | 0.17044 | 2.2638e-05 | 0
[13 empty] | 15:59 | 0.78368 | 0.91146 | 0.91784 |  | 15:59 | 0 | 0.15298 | 4956.6769 | 15:59 | 2.1105 | 1.94 | 0.17048 | 2.2643e-05 | 0
[13 empty] | 16:00 | 0.77542 | 0.91146 | 0.91784 |  | 16:00 | 0 | 0.15298 | 4956.6769 | 16:00 | 2.1111 | 1.9406 | 0.17051 | 2.2649e-05 | 0
[13 empty] | 16:00 | 0.76733 | 0.91146 | 0.91784 |  | 16:00 | 0 | 0.15298 | 4956.6769 | 16:00 | 2.1116 | 1.941 | 0.17055 | 2.2653e-05 | 0
[13 empty] | 16:00 | 0.7594 | 0.91146 | 0.91784 |  | 16:00 | 0 | 0.15298 | 4956.6769 | 16:00 | 2.112 | 1.9414 | 0.17059 | 2.2659e-05 | 0
[13 empty] | 16:00 | 0.75164 | 0.91146 | 0.91784 |  | 16:00 | 0.75552 | 0.15298 | 4962.3492 | 16:00 | 2.1124 | 1.9418 | 0.17063 | 2.2662e-05 | 0
[13 empty] | 16:00 | 0.74403 | 0.91146 | 0.91784 |  | 16:00 | 0.74784 | 0.15298 | 4973.6173 | 16:00 | 2.1128 | 1.9421 | 0.17066 | 2.2668e-05 | 0
[13 empty] | 16:01 | 0.73658 | 0.91146 | 0.91784 |  | 16:01 | 0.74031 | 0.15298 | 4984.79 | 16:01 | 2.1132 | 1.9425 | 0.1707 | 2.2672e-05 | 0
[13 empty] | 16:01 | 0.72929 | 0.91146 | 0.91784 |  | 16:01 | 0.73294 | 0.15298 | 4995.829 | 16:01 | 2.1138 | 1.9431 | 0.17073 | 2.2678e-05 | 0
[13 empty] | 16:01 | 1.1629 | 0.91146 | 0.91784 |  | 16:01 | 0.94609 | 0.15298 | 5008.4341 | 16:01 | 2.1145 | 1.9437 | 0.17079 | 2.2685e-05 | 0
[13 empty] | 16:01 | 1.1468 | 0.91146 | 0.91784 |  | 16:01 | 1.1549 | 0.15298 | 5024.1904 | 16:01 | 2.1151 | 1.9442 | 0.17085 | 2.2693e-05 | 0
[13 empty] | 16:02 | 1.1311 | 0.91146 | 0.91784 |  | 16:02 | 1.139 | 0.15298 | 5041.3791 | 16:02 | 2.1159 | 1.945 | 0.1709 | 2.2699e-05 | 0
[13 empty] | 16:02 | 1.1157 | 0.91146 | 0.91784 |  | 16:02 | 1.1234 | 0.15298 | 5058.3578 | 16:02 | 2.1166 | 1.9456 | 0.17096 | 2.2706e-05 | 0
[13 empty] | 16:02 | 1.1006 | 0.91146 | 0.91784 |  | 16:02 | 1.1082 | 0.15298 | 5075.0882 | 16:02 | 2.1172 | 1.9461 | 0.17101 | 2.2714e-05 | 0
[13 empty] | 16:02 | 1.0859 | 0.91146 | 0.91784 |  | 16:02 | 1.0933 | 0.15298 | 5091.6084 | 16:02 | 2.1178 | 1.9467 | 0.17106 | 2.2722e-05 | 0
[13 empty] | 16:03 | 1.0714 | 0.91146 | 0.91784 |  | 16:03 | 1.0786 | 0.15298 | 5107.8995 | 16:03 | 2.1184 | 1.9473 | 0.17112 | 2.2727e-05 | 0
[13 empty] | 16:03 | 1.0572 | 0.91146 | 0.91784 |  | 16:03 | 1.0643 | 0.15298 | 5123.9615 | 16:03 | 2.1191 | 1.9479 | 0.17117 | 2.2735e-05 | 0
[13 empty] | 16:03 | 1.0434 | 0.91146 | 0.91784 |  | 16:03 | 1.0503 | 0.15298 | 5139.8324 | 16:03 | 2.1199 | 1.9486 | 0.17122 | 2.2743e-05 | 0
[13 empty] | 16:04 | 1.0298 | 0.91146 | 0.91784 |  | 16:04 | 1.0366 | 0.15298 | 5155.4741 | 16:04 | 2.1205 | 1.9492 | 0.17127 | 2.2748e-05 | 0
[13 empty] | 16:04 | 1.0164 | 0.91146 | 0.91784 |  | 16:04 | 1.0231 | 0.15298 | 5170.9249 | 16:04 | 2.1209 | 1.9496 | 0.17132 | 2.2754e-05 | 0
[13 empty] | 16:04 | 1.0034 | 0.91146 | 0.91784 |  | 16:04 | 1.0099 | 0.15298 | 5186.1656 | 16:04 | 2.1215 | 1.9502 | 0.17137 | 2.2762e-05 | 0
[13 empty] | 16:04 | 0.99062 | 0.91146 | 0.91784 |  | 16:04 | 0.99701 | 0.15298 | 5201.2153 | 16:04 | 2.1222 | 1.9507 | 0.17142 | 2.2767e-05 | 0
[13 empty] | 16:04 | 0.97811 | 0.91146 | 0.91784 |  | 16:04 | 0.98437 | 0.15298 | 5216.074 | 16:04 | 2.1228 | 1.9513 | 0.17147 | 2.2775e-05 | 0
[13 empty] | 16:05 | 0.96585 | 0.91146 | 0.91784 |  | 16:05 | 0.97198 | 0.15298 | 5230.7608 | 16:05 | 2.1234 | 1.9519 | 0.17151 | 2.2781e-05 | 0
[13 empty] | 16:05 | 0.95385 | 0.91146 | 0.91784 |  | 16:05 | 0.95985 | 0.15298 | 5245.2375 | 16:05 | 2.124 | 1.9524 | 0.17156 | 2.2787e-05 | 0
[13 empty] | 16:05 | 0.94209 | 0.91146 | 0.91784 |  | 16:05 | 0.94797 | 0.15298 | 5259.5615 | 16:05 | 2.1245 | 1.9528 | 0.1716 | 2.2792e-05 | 0
[13 empty] | 16:05 | 0.93058 | 0.91146 | 0.91784 |  | 16:05 | 0.93634 | 0.15298 | 5273.6944 | 16:05 | 2.1251 | 1.9534 | 0.17165 | 2.2798e-05 | 0
[13 empty] | 16:06 | 0.9193 | 0.91146 | 0.91784 |  | 16:06 | 0.92494 | 0.15298 | 5287.6364 | 16:06 | 2.1257 | 1.954 | 0.17169 | 2.2806e-05 | 0
[13 empty] | 16:06 | 0.90825 | 0.91146 | 0.91784 |  | 16:06 | 0.91377 | 0.15298 | 5301.4447 | 16:06 | 2.1261 | 1.9544 | 0.17174 | 2.2811e-05 | 0
[13 empty] | 16:06 | 0.89743 | 0.91146 | 0.91784 |  | 16:06 | 0.90284 | 0.15298 | 5315.062 | 16:06 | 2.1267 | 1.9549 | 0.17178 | 2.2817e-05 | 0
[13 empty] | 16:06 | 0.88683 | 0.91146 | 0.91784 |  | 16:06 | 0.89213 | 0.15298 | 5328.5265 | 16:06 | 2.1274 | 1.9555 | 0.17183 | 2.2823e-05 | 0
[13 empty] | 16:07 | 0.87645 | 0.91146 | 0.91784 |  | 16:07 | 0.88164 | 0.15298 | 5341.8191 | 16:07 | 2.1278 | 1.9559 | 0.17187 | 2.2829e-05 | 0
[13 empty] | 16:07 | 0.86628 | 0.91146 | 0.91784 |  | 16:07 | 0.87137 | 0.15298 | 5354.978 | 16:07 | 2.1284 | 1.9565 | 0.17191 | 2.2834e-05 | 0
[13 empty] | 16:07 | 0.85633 | 0.91146 | 0.91784 |  | 16:07 | 0.8613 | 0.15298 | 5367.9651 | 16:07 | 2.1288 | 1.9568 | 0.17195 | 2.284e-05 | 0
[13 empty] | 16:08 | 0.84657 | 0.91146 | 0.91784 |  | 16:08 | 0.85145 | 0.15298 | 5380.8184 | 16:08 | 2.1294 | 1.9574 | 0.17199 | 2.2844e-05 | 0
[13 empty] | 16:08 | 0.83702 | 0.91146 | 0.91784 |  | 16:08 | 0.8418 | 0.15298 | 5393.519 | 16:08 | 2.1299 | 1.9578 | 0.17204 | 2.285e-05 | 0
[13 empty] | 16:08 | 0.82766 | 0.91146 | 0.91784 |  | 16:08 | 0.83234 | 0.15298 | 5406.0668 | 16:08 | 2.1305 | 1.9584 | 0.17208 | 2.2855e-05 | 0
[13 empty] | 16:08 | 0.8185 | 0.91146 | 0.91784 |  | 16:08 | 0.82308 | 0.15298 | 5418.4809 | 16:08 | 2.1309 | 1.9588 | 0.17212 | 2.2861e-05 | 0
[13 empty] | 16:08 | 0.80952 | 0.91146 | 0.91784 |  | 16:08 | 0.81401 | 0.15298 | 5430.7613 | 16:08 | 2.1313 | 1.9591 | 0.17216 | 2.2867e-05 | 0
[13 empty] | 16:09 | 0.80073 | 0.91146 | 0.91784 |  | 16:09 | 0.80512 | 0.15298 | 5442.908 | 16:09 | 2.1319 | 1.9597 | 0.17219 | 2.2871e-05 | 0
[13 empty] | 16:09 | 0.79211 | 0.91146 | 0.91784 |  | 16:09 | 0.79642 | 0.15298 | 5454.921 | 16:09 | 2.1323 | 1.9601 | 0.17223 | 2.2876e-05 | 0
[13 empty] | 16:09 | 0.78368 | 0.91146 | 0.91784 |  | 16:09 | 0.7879 | 0.15298 | 5466.8003 | 16:09 | 2.1328 | 1.9605 | 0.17227 | 2.2882e-05 | 0
[13 empty] | 16:10 | 0.77542 | 0.91146 | 0.91784 |  | 16:10 | 0.77955 | 0.15298 | 5478.565 | 16:10 | 2.1334 | 1.961 | 0.17231 | 2.2886e-05 | 0
[13 empty] | 16:10 | 0.76733 | 0.91146 | 0.91784 |  | 16:10 | 0.77137 | 0.15298 | 5490.1961 | 16:10 | 2.1338 | 1.9614 | 0.17235 | 2.2892e-05 | 0
[13 empty] | 16:10 | 0.7594 | 0.91146 | 0.91784 |  | 16:10 | 0.76336 | 0.15298 | 5501.6934 | 16:10 | 2.1342 | 1.9618 | 0.17238 | 2.2897e-05 | 0
[13 empty] | 16:10 | 0.75164 | 0.91146 | 0.91784 |  | 16:10 | 0 | 0.15298 | 5507.423 | 16:10 | 2.1346 | 1.9622 | 0.17242 | 2.2901e-05 | 0
[13 empty] | 16:10 | 0.74403 | 0.91146 | 0.91784 |  | 16:10 | 0 | 0.15298 | 5507.423 | 16:10 | 2.1351 | 1.9626 | 0.17246 | 2.2907e-05 | 0
[13 empty] | 16:11 | 0.73658 | 0.91146 | 0.91784 |  | 16:11 | 0 | 0.15298 | 5507.423 | 16:11 | 2.1355 | 1.963 | 0.17249 | 2.2911e-05 | 0
[13 empty] | 16:11 | 0.72929 | 0.91146 | 0.91784 |  | 16:11 | 0 | 0.15298 | 5507.423 | 16:11 | 2.1361 | 1.9635 | 0.17253 | 2.2916e-05 | 0
[13 empty] | 16:11 | 1.1629 | 0.91146 | 0.91784 |  | 16:11 | 0 | 0.15298 | 5507.423 | 16:11 | 2.1367 | 1.9641 | 0.17259 | 2.2924e-05 | 0
[13 empty] | 16:12 | 1.1468 | 0.91146 | 0.91784 |  | 16:12 | 0 | 0.15298 | 5507.423 | 16:12 | 2.1373 | 1.9647 | 0.17264 | 2.2932e-05 | 0
[13 empty] | 16:12 | 1.1311 | 0.91146 | 0.91784 |  | 16:12 | 0 | 0.15298 | 5507.423 | 16:12 | 2.1382 | 1.9654 | 0.1727 | 2.2937e-05 | 0
[13 empty] | 16:12 | 1.1157 | 0.91146 | 0.91784 |  | 16:12 | 0 | 0.15298 | 5507.423 | 16:12 | 2.1388 | 1.966 | 0.17275 | 2.2945e-05 | 0
[13 empty] | 16:12 | 1.1006 | 0.91146 | 0.91784 |  | 16:12 | 0 | 0.15298 | 5507.423 | 16:12 | 2.1394 | 1.9666 | 0.17281 | 2.2953e-05 | 0
[13 empty] | 16:12 | 1.0859 | 0.91146 | 0.91784 |  | 16:12 | 0 | 0.15298 | 5507.423 | 16:12 | 2.14 | 1.9672 | 0.17286 | 2.296e-05 | 0
[13 empty] | 16:13 | 1.0714 | 0.91146 | 0.91784 |  | 16:13 | 0 | 0.15298 | 5507.423 | 16:13 | 2.1407 | 1.9677 | 0.17291 | 2.2966e-05 | 0
[13 empty] | 16:13 | 1.0572 | 0.91146 | 0.91784 |  | 16:13 | 0 | 0.15298 | 5507.423 | 16:13 | 2.1413 | 1.9683 | 0.17296 | 2.2974e-05 | 0
[13 empty] | 16:13 | 1.0434 | 0.91146 | 0.91784 |  | 16:13 | 0 | 0.15298 | 5507.423 | 16:13 | 2.1419 | 1.9689 | 0.17301 | 2.2979e-05 | 0
[13 empty] | 16:14 | 1.0298 | 0.91146 | 0.91784 |  | 16:14 | 0 | 0.15298 | 5507.423 | 16:14 | 2.1425 | 1.9694 | 0.17306 | 2.2987e-05 | 0
[13 empty] | 16:14 | 1.0164 | 0.91146 | 0.91784 |  | 16:14 | 0 | 0.15298 | 5507.423 | 16:14 | 2.1432 | 1.97 | 0.17311 | 2.2993e-05 | 0
[13 empty] | 16:14 | 1.0034 | 0.91146 | 0.91784 |  | 16:14 | 0 | 0.15298 | 5507.423 | 16:14 | 2.1438 | 1.9706 | 0.17316 | 2.3e-05 | 0
[13 empty] | 16:14 | 0.99062 | 0.91146 | 0.91784 |  | 16:14 | 0 | 0.15298 | 5507.423 | 16:14 | 2.1444 | 1.9712 | 0.17321 | 2.3006e-05 | 0
[13 empty] | 16:14 | 0.97811 | 0.91146 | 0.91784 |  | 16:14 | 0 | 0.15298 | 5507.423 | 16:14 | 2.145 | 1.9717 | 0.17326 | 2.3012e-05 | 0
[13 empty] | 16:15 | 0.96585 | 0.91146 | 0.91784 |  | 16:15 | 0 | 0.15298 | 5507.423 | 16:15 | 2.1456 | 1.9723 | 0.17331 | 2.302e-05 | 0
[13 empty] | 16:15 | 0.95385 | 0.91146 | 0.91784 |  | 16:15 | 0 | 0.15298 | 5507.423 | 16:15 | 2.1463 | 1.9729 | 0.17335 | 2.3025e-05 | 0
[13 empty] | 16:15 | 0.94209 | 0.91146 | 0.91784 |  | 16:15 | 0 | 0.15298 | 5507.423 | 16:15 | 2.1467 | 1.9733 | 0.1734 | 2.3031e-05 | 0
[13 empty] | 16:16 | 0.93058 | 0.91146 | 0.91784 |  | 16:16 | 0 | 0.15298 | 5507.423 | 16:16 | 2.1473 | 1.9738 | 0.17345 | 2.3037e-05 | 0
[13 empty] | 16:16 | 0.9193 | 0.91146 | 0.91784 |  | 16:16 | 0 | 0.15298 | 5507.423 | 16:16 | 2.1479 | 1.9744 | 0.17349 | 2.3042e-05 | 0
[13 empty] | 16:16 | 0.90825 | 0.91146 | 0.91784 |  | 16:16 | 0 | 0.15298 | 5507.423 | 16:16 | 2.1484 | 1.9748 | 0.17353 | 2.305e-05 | 0
[13 empty] | 16:16 | 0.89743 | 0.91146 | 0.91784 |  | 16:16 | 0 | 0.15298 | 5507.423 | 16:16 | 2.149 | 1.9754 | 0.17358 | 2.3056e-05 | 0
[13 empty] | 16:16 | 0.88683 | 0.91146 | 0.91784 |  | 16:16 | 0 | 0.15298 | 5507.423 | 16:16 | 2.1496 | 1.9759 | 0.17362 | 2.3062e-05 | 0
[13 empty] | 16:17 | 0.87645 | 0.91146 | 0.91784 |  | 16:17 | 0 | 0.15298 | 5507.423 | 16:17 | 2.15 | 1.9763 | 0.17367 | 2.3067e-05 | 0
[13 empty] | 16:17 | 0.86628 | 0.91146 | 0.91784 |  | 16:17 | 0 | 0.15298 | 5507.423 | 16:17 | 2.1506 | 1.9769 | 0.17371 | 2.3073e-05 | 0
[13 empty] | 16:17 | 0.85633 | 0.91146 | 0.91784 |  | 16:17 | 0 | 0.15298 | 5507.423 | 16:17 | 2.151 | 1.9773 | 0.17375 | 2.3077e-05 | 0
[13 empty] | 16:18 | 0.84657 | 0.91146 | 0.91784 |  | 16:18 | 0 | 0.15298 | 5507.423 | 16:18 | 2.1517 | 1.9779 | 0.17379 | 2.3083e-05 | 0
[13 empty] | 16:18 | 0.83702 | 0.91146 | 0.91784 |  | 16:18 | 0 | 0.15298 | 5507.423 | 16:18 | 2.1521 | 1.9782 | 0.17383 | 2.3088e-05 | 0
[13 empty] | 16:18 | 0.82766 | 0.91146 | 0.91784 |  | 16:18 | 0 | 0.15298 | 5507.423 | 16:18 | 2.1527 | 1.9788 | 0.17387 | 2.3094e-05 | 0
[13 empty] | 16:18 | 0.8185 | 0.91146 | 0.91784 |  | 16:18 | 0 | 0.15298 | 5507.423 | 16:18 | 2.1531 | 1.9792 | 0.17391 | 2.31e-05 | 0
[13 empty] | 16:18 | 0.80952 | 0.91146 | 0.91784 |  | 16:18 | 0 | 0.15298 | 5507.423 | 16:18 | 2.1535 | 1.9796 | 0.17395 | 2.3105e-05 | 0
[13 empty] | 16:19 | 0.80073 | 0.91146 | 0.91784 |  | 16:19 | 0 | 0.15298 | 5507.423 | 16:19 | 2.1542 | 1.9801 | 0.17399 | 2.3109e-05 | 0
[13 empty] | 16:19 | 0.79211 | 0.91146 | 0.91784 |  | 16:19 | 0 | 0.15298 | 5507.423 | 16:19 | 2.1546 | 1.9805 | 0.17403 | 2.3115e-05 | 0
[13 empty] | 16:19 | 0.78368 | 0.91146 | 0.91784 |  | 16:19 | 0 | 0.15298 | 5507.423 | 16:19 | 2.155 | 1.9809 | 0.17407 | 2.3121e-05 | 0
[13 empty] | 16:20 | 0.77542 | 0.91146 | 0.91784 |  | 16:20 | 0 | 0.15298 | 5507.423 | 16:20 | 2.1556 | 1.9815 | 0.1741 | 2.3125e-05 | 0
[13 empty] | 16:20 | 0.76733 | 0.91146 | 0.91784 |  | 16:20 | 0 | 0.15298 | 5507.423 | 16:20 | 2.156 | 1.9819 | 0.17414 | 2.313e-05 | 0
[13 empty] | 16:20 | 0.7594 | 0.91146 | 0.91784 |  | 16:20 | 0 | 0.15298 | 5507.423 | 16:20 | 2.1564 | 1.9822 | 0.17418 | 2.3134e-05 | 0
[13 empty] | 16:20 | 0.75164 | 0.91146 | 0.91784 |  | 16:20 | 0 | 0.15298 | 5507.423 | 16:20 | 2.1569 | 1.9826 | 0.17422 | 2.314e-05 | 0
[13 empty] | 16:20 | 0.74403 | 0.91146 | 0.91784 |  | 16:20 | 0 | 0.15298 | 5507.423 | 16:20 | 2.1573 | 1.983 | 0.17425 | 2.3146e-05 | 0
[13 empty] | 16:21 | 0.73658 | 0.91146 | 0.91784 |  | 16:21 | 0 | 0.15298 | 5507.423 | 16:21 | 2.1577 | 1.9834 | 0.17429 | 2.3149e-05 | 0
[13 empty] | 16:21 | 0.72929 | 0.91146 | 0.91784 |  | 16:21 | 0 | 0.15298 | 5507.423 | 16:21 | 2.1583 | 1.984 | 0.17432 | 2.3155e-05 | 0
[13 empty] | 16:21 | 1.1629 | 0.91146 | 0.91784 |  | 16:21 | 0 | 0.15298 | 5507.423 | 16:21 | 2.1589 | 1.9845 | 0.17438 | 2.3161e-05 | 0
[13 empty] | 16:22 | 1.1468 | 0.91146 | 0.91784 |  | 16:22 | 0 | 0.15298 | 5507.423 | 16:22 | 2.1596 | 1.9851 | 0.17444 | 2.3169e-05 | 0
[13 empty] | 16:22 | 1.1311 | 0.91146 | 0.91784 |  | 16:22 | 0 | 0.15298 | 5507.423 | 16:22 | 2.1604 | 1.9859 | 0.17449 | 2.3176e-05 | 0
[13 empty] | 16:22 | 1.1157 | 0.91146 | 0.91784 |  | 16:22 | 0 | 0.15298 | 5507.423 | 16:22 | 2.161 | 1.9864 | 0.17455 | 2.3184e-05 | 0
[13 empty] | 16:22 | 1.1006 | 0.91146 | 0.91784 |  | 16:22 | 0 | 0.15298 | 5507.423 | 16:22 | 2.1616 | 1.987 | 0.1746 | 2.3191e-05 | 0
[13 empty] | 16:22 | 1.0859 | 0.91146 | 0.91784 |  | 16:22 | 0 | 0.15298 | 5507.423 | 16:22 | 2.1623 | 1.9876 | 0.17465 | 2.3197e-05 | 0
[13 empty] | 16:23 | 1.0714 | 0.91146 | 0.91784 |  | 16:23 | 0 | 0.15298 | 5507.423 | 16:23 | 2.1629 | 1.9882 | 0.17471 | 2.3205e-05 | 0
[13 empty] | 16:23 | 1.0572 | 0.91146 | 0.91784 |  | 16:23 | 0 | 0.15298 | 5507.423 | 16:23 | 2.1635 | 1.9887 | 0.17476 | 2.3212e-05 | 0
[13 empty] | 16:23 | 1.0434 | 0.91146 | 0.91784 |  | 16:23 | 0 | 0.15298 | 5507.423 | 16:23 | 2.1641 | 1.9893 | 0.17481 | 2.3218e-05 | 0
[13 empty] | 16:24 | 1.0298 | 0.91146 | 0.91784 |  | 16:24 | 0 | 0.15298 | 5507.423 | 16:24 | 2.1648 | 1.9899 | 0.17486 | 2.3226e-05 | 0
[13 empty] | 16:24 | 1.0164 | 0.91146 | 0.91784 |  | 16:24 | 0 | 0.15298 | 5507.423 | 16:24 | 2.1654 | 1.9905 | 0.17491 | 2.3232e-05 | 0
[13 empty] | 16:24 | 1.0034 | 0.91146 | 0.91784 |  | 16:24 | 0 | 0.15298 | 5507.423 | 16:24 | 2.166 | 1.991 | 0.17496 | 2.3239e-05 | 0
[13 empty] | 16:24 | 0.99062 | 0.91146 | 0.91784 |  | 16:24 | 0 | 0.15298 | 5507.423 | 16:24 | 2.1666 | 1.9916 | 0.17501 | 2.3245e-05 | 0
[13 empty] | 16:25 | 0.97811 | 0.91146 | 0.91784 |  | 16:25 | 0 | 0.15298 | 5507.423 | 16:25 | 2.1673 | 1.9922 | 0.17506 | 2.3251e-05 | 0
[13 empty] | 16:25 | 0.96585 | 0.91146 | 0.91784 |  | 16:25 | 0 | 0.15298 | 5507.423 | 16:25 | 2.1679 | 1.9927 | 0.1751 | 2.3258e-05 | 0
[13 empty] | 16:25 | 0.95385 | 0.91146 | 0.91784 |  | 16:25 | 0 | 0.15298 | 5507.423 | 16:25 | 2.1685 | 1.9933 | 0.17515 | 2.3264e-05 | 0
[13 empty] | 16:25 | 0.94209 | 0.91146 | 0.91784 |  | 16:25 | 0 | 0.15298 | 5507.423 | 16:25 | 2.1689 | 1.9937 | 0.1752 | 2.327e-05 | 0
[13 empty] | 16:26 | 0.93058 | 0.91146 | 0.91784 |  | 16:26 | 0 | 0.15298 | 5507.423 | 16:26 | 2.1695 | 1.9943 | 0.17524 | 2.3275e-05 | 0
[13 empty] | 16:26 | 0.9193 | 0.91146 | 0.91784 |  | 16:26 | 0 | 0.15298 | 5507.423 | 16:26 | 2.1702 | 1.9948 | 0.17528 | 2.3281e-05 | 0
[13 empty] | 16:26 | 0.90825 | 0.91146 | 0.91784 |  | 16:26 | 0 | 0.15298 | 5507.423 | 16:26 | 2.1706 | 1.9952 | 0.17533 | 2.3287e-05 | 0
[13 empty] | 16:26 | 0.89743 | 0.91146 | 0.91784 |  | 16:26 | 0 | 0.15298 | 5507.423 | 16:26 | 2.1712 | 1.9958 | 0.17537 | 2.3293e-05 | 0
[13 empty] | 16:26 | 0.88683 | 0.91146 | 0.91784 |  | 16:26 | 0 | 0.15298 | 5507.423 | 16:26 | 2.1718 | 1.9964 | 0.17542 | 2.3298e-05 | 0
[13 empty] | 16:27 | 0.87645 | 0.91146 | 0.91784 |  | 16:27 | 0 | 0.15298 | 5507.423 | 16:27 | 2.1722 | 1.9968 | 0.17546 | 2.3304e-05 | 0
[13 empty] | 16:27 | 0.86628 | 0.91146 | 0.91784 |  | 16:27 | 0 | 0.15298 | 5507.423 | 16:27 | 2.1729 | 1.9973 | 0.1755 | 2.331e-05 | 0
[13 empty] | 16:27 | 0.85633 | 0.91146 | 0.91784 |  | 16:27 | 0 | 0.15298 | 5507.423 | 16:27 | 2.1733 | 1.9977 | 0.17554 | 2.3316e-05 | 0
[13 empty] | 16:27 | 0.84657 | 0.91146 | 0.91784 |  | 16:27 | 0 | 0.15298 | 5507.423 | 16:27 | 2.1739 | 1.9983 | 0.17558 | 2.3321e-05 | 0
[13 empty] | 16:28 | 0.83702 | 0.91146 | 0.91784 |  | 16:28 | 0 | 0.15298 | 5507.423 | 16:28 | 2.1743 | 1.9987 | 0.17563 | 2.3327e-05 | 0
[13 empty] | 16:28 | 0.82766 | 0.91146 | 0.91784 |  | 16:28 | 0 | 0.15298 | 5507.423 | 16:28 | 2.1749 | 1.9992 | 0.17567 | 2.3333e-05 | 0
[13 empty] | 16:28 | 0.8185 | 0.91146 | 0.91784 |  | 16:28 | 0 | 0.15298 | 5507.423 | 16:28 | 2.1754 | 1.9996 | 0.17571 | 2.3338e-05 | 0
[13 empty] | 16:29 | 0.80952 | 0.91146 | 0.91784 |  | 16:29 | 0 | 0.15298 | 5507.423 | 16:29 | 2.1758 | 2 | 0.17575 | 2.3342e-05 | 0
[13 empty] | 16:29 | 0.80073 | 0.91146 | 0.91784 |  | 16:29 | 0 | 0.15298 | 5507.423 | 16:29 | 2.1764 | 2.0006 | 0.17579 | 2.3348e-05 | 0
[13 empty] | 16:29 | 0.79211 | 0.91146 | 0.91784 |  | 16:29 | 0 | 0.15298 | 5507.423 | 16:29 | 2.1768 | 2.001 | 0.17583 | 2.3354e-05 | 0
[13 empty] | 16:29 | 0.78368 | 0.91146 | 0.91784 |  | 16:29 | 0 | 0.15298 | 5507.423 | 16:29 | 2.1772 | 2.0013 | 0.17586 | 2.3358e-05 | 0
[13 empty] | 16:30 | 0.77542 | 0.91146 | 0.91784 |  | 16:30 | 0 | 0.15298 | 5507.423 | 16:30 | 2.1776 | 2.0017 | 0.1759 | 2.3363e-05 | 0
[13 empty] | 16:30 | 0.76733 | 0.91146 | 0.91784 |  | 16:30 | 0 | 0.15298 | 5507.423 | 16:30 | 2.1783 | 2.0023 | 0.17594 | 2.3369e-05 | 0
[13 empty] | 16:30 | 0.7594 | 0.91146 | 0.91784 |  | 16:30 | 0 | 0.15298 | 5507.423 | 16:30 | 2.1787 | 2.0027 | 0.17598 | 2.3373e-05 | 0
[13 empty] | 16:30 | 0.75164 | 0.91146 | 0.91784 |  | 16:30 | 0 | 0.15298 | 5507.423 | 16:30 | 2.1791 | 2.0031 | 0.17601 | 2.3379e-05 | 0
[13 empty] | 16:30 | 0.74403 | 0.91146 | 0.91784 |  | 16:30 | 0 | 0.15298 | 5507.423 | 16:30 | 2.1795 | 2.0034 | 0.17605 | 2.3382e-05 | 0
[13 empty] | 16:31 | 0.73658 | 0.91146 | 0.91784 |  | 16:31 | 0 | 0.15298 | 5507.423 | 16:31 | 2.1799 | 2.0038 | 0.17609 | 2.3388e-05 | 0
[13 empty] | 16:31 | 0.72929 | 0.91146 | 0.91784 |  | 16:31 | 0 | 0.15298 | 5507.423 | 16:31 | 2.1805 | 2.0044 | 0.17612 | 2.3392e-05 | 0
[13 empty] | 16:31 | 1.1629 | 0.91146 | 0.91784 |  | 16:31 | 0 | 0.15298 | 5507.423 | 16:31 | 2.1812 | 2.005 | 0.17618 | 2.34e-05 | 0
[13 empty] | 16:31 | 1.1468 | 0.91146 | 0.91784 |  | 16:31 | 0 | 0.15298 | 5507.423 | 16:31 | 2.1818 | 2.0055 | 0.17623 | 2.3407e-05 | 0
[13 empty] | 16:32 | 1.1311 | 0.91146 | 0.91784 |  | 16:32 | 0 | 0.15298 | 5507.423 | 16:32 | 2.1826 | 2.0063 | 0.17629 | 2.3415e-05 | 0
[13 empty] | 16:32 | 1.1157 | 0.91146 | 0.91784 |  | 16:32 | 0 | 0.15298 | 5507.423 | 16:32 | 2.1832 | 2.0069 | 0.17634 | 2.3423e-05 | 0
[13 empty] | 16:32 | 1.1006 | 0.91146 | 0.91784 |  | 16:32 | 0 | 0.15298 | 5507.423 | 16:32 | 2.1839 | 2.0075 | 0.1764 | 2.343e-05 | 0
[13 empty] | 16:33 | 1.0859 | 0.91146 | 0.91784 |  | 16:33 | 0 | 0.15298 | 5507.423 | 16:33 | 2.1845 | 2.008 | 0.17645 | 2.3436e-05 | 0
[13 empty] | 16:33 | 1.0714 | 0.91146 | 0.91784 |  | 16:33 | 0 | 0.15298 | 5507.423 | 16:33 | 2.1851 | 2.0086 | 0.1765 | 2.3444e-05 | 0
[13 empty] | 16:33 | 1.0572 | 0.91146 | 0.91784 |  | 16:33 | 0 | 0.15298 | 5507.423 | 16:33 | 2.1858 | 2.0092 | 0.17656 | 2.3451e-05 | 0
[13 empty] | 16:33 | 1.0434 | 0.91146 | 0.91784 |  | 16:33 | 0 | 0.15298 | 5507.423 | 16:33 | 2.1864 | 2.0097 | 0.1766 | 2.3457e-05 | 0
[13 empty] | 16:34 | 1.0298 | 0.91146 | 0.91784 |  | 16:34 | 0 | 0.15298 | 5507.423 | 16:34 | 2.187 | 2.0103 | 0.17666 | 2.3465e-05 | 0
[13 empty] | 16:34 | 1.0164 | 0.91146 | 0.91784 |  | 16:34 | 0 | 0.15298 | 5507.423 | 16:34 | 2.1876 | 2.0109 | 0.17671 | 2.347e-05 | 0
[13 empty] | 16:34 | 1.0034 | 0.91146 | 0.91784 |  | 16:34 | 0 | 0.15298 | 5507.423 | 16:34 | 2.1882 | 2.0115 | 0.17675 | 2.3476e-05 | 0
[13 empty] | 16:34 | 0.99062 | 0.91146 | 0.91784 |  | 16:34 | 0 | 0.15298 | 5507.423 | 16:34 | 2.1889 | 2.012 | 0.1768 | 2.3484e-05 | 0
[13 empty] | 16:34 | 0.97811 | 0.91146 | 0.91784 |  | 16:34 | 0 | 0.15298 | 5507.423 | 16:34 | 2.1895 | 2.0126 | 0.17685 | 2.3489e-05 | 0
[13 empty] | 16:35 | 0.96585 | 0.91146 | 0.91784 |  | 16:35 | 0 | 0.15298 | 5507.423 | 16:35 | 2.1901 | 2.0132 | 0.1769 | 2.3495e-05 | 0
[13 empty] | 16:35 | 0.95385 | 0.91146 | 0.91784 |  | 16:35 | 0 | 0.15298 | 5507.423 | 16:35 | 2.1907 | 2.0138 | 0.17694 | 2.3503e-05 | 0
[13 empty] | 16:35 | 0.94209 | 0.91146 | 0.91784 |  | 16:35 | 0 | 0.15298 | 5507.423 | 16:35 | 2.1912 | 2.0141 | 0.17699 | 2.3508e-05 | 0
[13 empty] | 16:35 | 0.93058 | 0.91146 | 0.91784 |  | 16:35 | 0 | 0.15298 | 5507.423 | 16:35 | 2.1918 | 2.0147 | 0.17704 | 2.3514e-05 | 0
[13 empty] | 16:36 | 0.9193 | 0.91146 | 0.91784 |  | 16:36 | 0 | 0.15298 | 5507.423 | 16:36 | 2.1924 | 2.0153 | 0.17708 | 2.352e-05 | 0
[13 empty] | 16:36 | 0.90825 | 0.91146 | 0.91784 |  | 16:36 | 0 | 0.15298 | 5507.423 | 16:36 | 2.1928 | 2.0157 | 0.17713 | 2.3526e-05 | 0
[13 empty] | 16:36 | 0.89743 | 0.91146 | 0.91784 |  | 16:36 | 0 | 0.15298 | 5507.423 | 16:36 | 2.1934 | 2.0162 | 0.17717 | 2.3531e-05 | 0
[13 empty] | 16:36 | 0.88683 | 0.91146 | 0.91784 |  | 16:36 | 0 | 0.15298 | 5507.423 | 16:36 | 2.194 | 2.0168 | 0.17721 | 2.3537e-05 | 0
[13 empty] | 16:37 | 0.87645 | 0.91146 | 0.91784 |  | 16:37 | 0 | 0.15298 | 5507.423 | 16:37 | 2.1945 | 2.0172 | 0.17726 | 2.3543e-05 | 0
[13 empty] | 16:37 | 0.86628 | 0.91146 | 0.91784 |  | 16:37 | 0 | 0.15298 | 5507.423 | 16:37 | 2.1951 | 2.0178 | 0.1773 | 2.3549e-05 | 0
[13 empty] | 16:37 | 0.85633 | 0.91146 | 0.91784 |  | 16:37 | 0 | 0.15298 | 5507.423 | 16:37 | 2.1955 | 2.0181 | 0.17734 | 2.3554e-05 | 0
[13 empty] | 16:38 | 0.84657 | 0.91146 | 0.91784 |  | 16:38 | 0 | 0.15298 | 5507.423 | 16:38 | 2.1961 | 2.0187 | 0.17738 | 2.356e-05 | 0
[13 empty] | 16:38 | 0.83702 | 0.91146 | 0.91784 |  | 16:38 | 0 | 0.15298 | 5507.423 | 16:38 | 2.1965 | 2.0191 | 0.17742 | 2.3566e-05 | 0
[13 empty] | 16:38 | 0.82766 | 0.91146 | 0.91784 |  | 16:38 | 0 | 0.15298 | 5507.423 | 16:38 | 2.1972 | 2.0197 | 0.17746 | 2.3571e-05 | 0
[13 empty] | 16:38 | 0.8185 | 0.91146 | 0.91784 |  | 16:38 | 0 | 0.15298 | 5507.423 | 16:38 | 2.1976 | 2.0201 | 0.1775 | 2.3575e-05 | 0
[13 empty] | 16:38 | 0.80952 | 0.91146 | 0.91784 |  | 16:38 | 0 | 0.15298 | 5507.423 | 16:38 | 2.198 | 2.0204 | 0.17754 | 2.3581e-05 | 0
[13 empty] | 16:39 | 0.80073 | 0.91146 | 0.91784 |  | 16:39 | 0 | 0.15298 | 5507.423 | 16:39 | 2.1986 | 2.021 | 0.17758 | 2.3587e-05 | 0
[13 empty] | 16:39 | 0.79211 | 0.91146 | 0.91784 |  | 16:39 | 0 | 0.15298 | 5507.423 | 16:39 | 2.199 | 2.0214 | 0.17762 | 2.3592e-05 | 0
[13 empty] | 16:39 | 0.78368 | 0.91146 | 0.91784 |  | 16:39 | 0 | 0.15298 | 5507.423 | 16:39 | 2.1995 | 2.0218 | 0.17766 | 2.3596e-05 | 0
[13 empty] | 16:40 | 0.77542 | 0.91146 | 0.91784 |  | 16:40 | 0 | 0.15298 | 5507.423 | 16:40 | 2.1999 | 2.0222 | 0.1777 | 2.3602e-05 | 0
[13 empty] | 16:40 | 0.76733 | 0.91146 | 0.91784 |  | 16:40 | 0 | 0.15298 | 5507.423 | 16:40 | 2.2005 | 2.0227 | 0.17773 | 2.3608e-05 | 0
[13 empty] | 16:40 | 0.7594 | 0.91146 | 0.91784 |  | 16:40 | 0 | 0.15298 | 5507.423 | 16:40 | 2.2009 | 2.0231 | 0.17777 | 2.3612e-05 | 0
[13 empty] | 16:40 | 0.75164 | 0.91146 | 0.91784 |  | 16:40 | 0 | 0.15298 | 5507.423 | 16:40 | 2.2013 | 2.0235 | 0.17781 | 2.3617e-05 | 0
[13 empty] | 16:40 | 0.74403 | 0.91146 | 0.91784 |  | 16:40 | 0 | 0.15298 | 5507.423 | 16:40 | 2.2017 | 2.0239 | 0.17784 | 2.3621e-05 | 0
[13 empty] | 16:41 | 0.73658 | 0.91146 | 0.91784 |  | 16:41 | 0 | 0.15298 | 5507.423 | 16:41 | 2.2022 | 2.0243 | 0.17788 | 2.3627e-05 | 0
[13 empty] | 16:41 | 0.72929 | 0.91146 | 0.91784 |  | 16:41 | 0 | 0.15298 | 5507.423 | 16:41 | 2.2028 | 2.0248 | 0.17791 | 2.3631e-05 | 0
[13 empty] | 16:41 | 1.1629 | 0.91146 | 0.91784 |  | 16:41 | 0 | 0.15298 | 5507.423 | 16:41 | 2.2034 | 2.0254 | 0.17797 | 2.3638e-05 | 0
[13 empty] | 16:42 | 1.1468 | 0.91146 | 0.91784 |  | 16:42 | 0 | 0.15298 | 5507.423 | 16:42 | 2.204 | 2.026 | 0.17803 | 2.3646e-05 | 0
[13 empty] | 16:42 | 1.1311 | 0.91146 | 0.91784 |  | 16:42 | 0 | 0.15298 | 5507.423 | 16:42 | 2.2049 | 2.0267 | 0.17808 | 2.3654e-05 | 0
[13 empty] | 16:42 | 1.1157 | 0.91146 | 0.91784 |  | 16:42 | 0 | 0.15298 | 5507.423 | 16:42 | 2.2055 | 2.0273 | 0.17814 | 2.3661e-05 | 0
[13 empty] | 16:42 | 1.1006 | 0.91146 | 0.91784 |  | 16:42 | 0 | 0.15298 | 5507.423 | 16:42 | 2.2061 | 2.0279 | 0.17819 | 2.3667e-05 | 0
[13 empty] | 16:42 | 1.0859 | 0.91146 | 0.91784 |  | 16:42 | 0 | 0.15298 | 5507.423 | 16:42 | 2.2067 | 2.0285 | 0.17825 | 2.3675e-05 | 0
[13 empty] | 16:43 | 1.0714 | 0.91146 | 0.91784 |  | 16:43 | 0 | 0.15298 | 5507.423 | 16:43 | 2.2074 | 2.029 | 0.1783 | 2.3682e-05 | 0
[13 empty] | 16:43 | 1.0572 | 0.91146 | 0.91784 |  | 16:43 | 0 | 0.15298 | 5507.423 | 16:43 | 2.208 | 2.0296 | 0.17835 | 2.3688e-05 | 0
[13 empty] | 16:43 | 1.0434 | 0.91146 | 0.91784 |  | 16:43 | 0 | 0.15298 | 5507.423 | 16:43 | 2.2086 | 2.0302 | 0.1784 | 2.3696e-05 | 0
[13 empty] | 16:44 | 1.0298 | 0.91146 | 0.91784 |  | 16:44 | 0 | 0.15298 | 5507.423 | 16:44 | 2.2092 | 2.0308 | 0.17845 | 2.3701e-05 | 0
[13 empty] | 16:44 | 1.0164 | 0.91146 | 0.91784 |  | 16:44 | 0 | 0.15298 | 5507.423 | 16:44 | 2.2099 | 2.0313 | 0.1785 | 2.3709e-05 | 0
[13 empty] | 16:44 | 1.0034 | 0.91146 | 0.91784 |  | 16:44 | 0 | 0.15298 | 5507.423 | 16:44 | 2.2105 | 2.0319 | 0.17855 | 2.3715e-05 | 0
[13 empty] | 16:44 | 0.99062 | 0.91146 | 0.91784 |  | 16:44 | 0 | 0.15298 | 5507.423 | 16:44 | 2.2111 | 2.0325 | 0.1786 | 2.3722e-05 | 0
[13 empty] | 16:44 | 0.97811 | 0.91146 | 0.91784 |  | 16:44 | 0 | 0.15298 | 5507.423 | 16:44 | 2.2117 | 2.033 | 0.17865 | 2.3728e-05 | 0
[13 empty] | 16:45 | 0.96585 | 0.91146 | 0.91784 |  | 16:45 | 0 | 0.15298 | 5507.423 | 16:45 | 2.2123 | 2.0336 | 0.17869 | 2.3734e-05 | 0
[13 empty] | 16:45 | 0.95385 | 0.91146 | 0.91784 |  | 16:45 | 0 | 0.15298 | 5507.423 | 16:45 | 2.213 | 2.0342 | 0.17874 | 2.3741e-05 | 0
[13 empty] | 16:45 | 0.94209 | 0.91146 | 0.91784 |  | 16:45 | 0 | 0.15298 | 5507.423 | 16:45 | 2.2134 | 2.0346 | 0.17879 | 2.3747e-05 | 0
[13 empty] | 16:46 | 0.93058 | 0.91146 | 0.91784 |  | 16:46 | 0 | 0.15298 | 5507.423 | 16:46 | 2.214 | 2.0351 | 0.17883 | 2.3753e-05 | 0
[13 empty] | 16:46 | 0.9193 | 0.91146 | 0.91784 |  | 16:46 | 0 | 0.15298 | 5507.423 | 16:46 | 2.2146 | 2.0357 | 0.17888 | 2.3759e-05 | 0
[13 empty] | 16:46 | 0.90825 | 0.91146 | 0.91784 |  | 16:46 | 0 | 0.15298 | 5507.423 | 16:46 | 2.215 | 2.0361 | 0.17892 | 2.3764e-05 | 0
[13 empty] | 16:46 | 0.89743 | 0.91146 | 0.91784 |  | 16:46 | 0 | 0.15298 | 5507.423 | 16:46 | 2.2157 | 2.0367 | 0.17897 | 2.377e-05 | 0
[13 empty] | 16:46 | 0.88683 | 0.91146 | 0.91784 |  | 16:46 | 0 | 0.15298 | 5507.423 | 16:46 | 2.2163 | 2.0372 | 0.17901 | 2.3776e-05 | 0
[13 empty] | 16:47 | 0.87645 | 0.91146 | 0.91784 |  | 16:47 | 0 | 0.15298 | 5507.423 | 16:47 | 2.2167 | 2.0376 | 0.17905 | 2.3782e-05 | 0
[13 empty] | 16:47 | 0.86628 | 0.91146 | 0.91784 |  | 16:47 | 0 | 0.15298 | 5507.423 | 16:47 | 2.2173 | 2.0382 | 0.17909 | 2.3787e-05 | 0
[13 empty] | 16:47 | 0.85633 | 0.91146 | 0.91784 |  | 16:47 | 0 | 0.15298 | 5507.423 | 16:47 | 2.2177 | 2.0386 | 0.17914 | 2.3793e-05 | 0
[13 empty] | 16:48 | 0.84657 | 0.91146 | 0.91784 |  | 16:48 | 0 | 0.15298 | 5507.423 | 16:48 | 2.2184 | 2.0392 | 0.17918 | 2.3799e-05 | 0
[13 empty] | 16:48 | 0.83702 | 0.91146 | 0.91784 |  | 16:48 | 0 | 0.15298 | 5507.423 | 16:48 | 2.2188 | 2.0395 | 0.17922 | 2.3804e-05 | 0
[13 empty] | 16:48 | 0.82766 | 0.91146 | 0.91784 |  | 16:48 | 0 | 0.15298 | 5507.423 | 16:48 | 2.2194 | 2.0401 | 0.17926 | 2.381e-05 | 0
[13 empty] | 16:48 | 0.8185 | 0.91146 | 0.91784 |  | 16:48 | 0 | 0.15298 | 5507.423 | 16:48 | 2.2198 | 2.0405 | 0.1793 | 2.3814e-05 | 0
[13 empty] | 16:48 | 0.80952 | 0.91146 | 0.91784 |  | 16:48 | 0 | 0.15298 | 5507.423 | 16:48 | 2.2202 | 2.0409 | 0.17934 | 2.382e-05 | 0
[13 empty] | 16:49 | 0.80073 | 0.91146 | 0.91784 |  | 16:49 | 0 | 0.15298 | 5507.423 | 16:49 | 2.2208 | 2.0414 | 0.17938 | 2.3825e-05 | 0
[13 empty] | 16:49 | 0.79211 | 0.91146 | 0.91784 |  | 16:49 | 0 | 0.15298 | 5507.423 | 16:49 | 2.2213 | 2.0418 | 0.17942 | 2.3831e-05 | 0
[13 empty] | 16:49 | 0.78368 | 0.91146 | 0.91784 |  | 16:49 | 0 | 0.15298 | 5507.423 | 16:49 | 2.2217 | 2.0422 | 0.17945 | 2.3835e-05 | 0
[13 empty] | 16:50 | 0.77542 | 0.91146 | 0.91784 |  | 16:50 | 0 | 0.15298 | 5507.423 | 16:50 | 2.2221 | 2.0426 | 0.17949 | 2.3841e-05 | 0
[13 empty] | 16:50 | 0.76733 | 0.91146 | 0.91784 |  | 16:50 | 0 | 0.15298 | 5507.423 | 16:50 | 2.2227 | 2.0432 | 0.17953 | 2.3845e-05 | 0
[13 empty] | 16:50 | 0.7594 | 0.91146 | 0.91784 |  | 16:50 | 0 | 0.15298 | 5507.423 | 16:50 | 2.2231 | 2.0435 | 0.17957 | 2.385e-05 | 0
[13 empty] | 16:50 | 0.75164 | 0.91146 | 0.91784 |  | 16:50 | 0 | 0.15298 | 5507.423 | 16:50 | 2.2236 | 2.0439 | 0.1796 | 2.3856e-05 | 0
[13 empty] | 16:50 | 0.74403 | 0.91146 | 0.91784 |  | 16:50 | 0 | 0.15298 | 5507.423 | 16:50 | 2.224 | 2.0443 | 0.17964 | 2.386e-05 | 0
[13 empty] | 16:51 | 0.73658 | 0.91146 | 0.91784 |  | 16:51 | 0 | 0.15298 | 5507.423 | 16:51 | 2.2244 | 2.0447 | 0.17968 | 2.3866e-05 | 0
[13 empty] | 16:51 | 0.72929 | 0.91146 | 0.91784 |  | 16:51 | 0 | 0.15298 | 5507.423 | 16:51 | 2.225 | 2.0453 | 0.17971 | 2.3869e-05 | 0
[13 empty] | 16:51 | 1.1629 | 0.91146 | 0.91784 |  | 16:51 | 0 | 0.15298 | 5507.423 | 16:51 | 2.2256 | 2.0458 | 0.17977 | 2.3877e-05 | 0
[13 empty] | 16:52 | 1.1468 | 0.91146 | 0.91784 |  | 16:52 | 0 | 0.15298 | 5507.423 | 16:52 | 2.2263 | 2.0464 | 0.17982 | 2.3885e-05 | 0
[13 empty] | 16:52 | 1.1311 | 0.91146 | 0.91784 |  | 16:52 | 0 | 0.15298 | 5507.423 | 16:52 | 2.2271 | 2.0472 | 0.17988 | 2.3892e-05 | 0
[13 empty] | 16:52 | 1.1157 | 0.91146 | 0.91784 |  | 16:52 | 0 | 0.15298 | 5507.423 | 16:52 | 2.2277 | 2.0478 | 0.17993 | 2.39e-05 | 0
[13 empty] | 16:52 | 1.1006 | 0.91146 | 0.91784 |  | 16:52 | 0 | 0.15298 | 5507.423 | 16:52 | 2.2283 | 2.0483 | 0.17999 | 2.3906e-05 | 0
[13 empty] | 16:52 | 1.0859 | 0.91146 | 0.91784 |  | 16:52 | 0 | 0.15298 | 5507.423 | 16:52 | 2.229 | 2.0489 | 0.18004 | 2.3913e-05 | 0
[13 empty] | 16:53 | 1.0714 | 0.91146 | 0.91784 |  | 16:53 | 0 | 0.15298 | 5507.423 | 16:53 | 2.2296 | 2.0495 | 0.18009 | 2.3921e-05 | 0
[13 empty] | 16:53 | 1.0572 | 0.91146 | 0.91784 |  | 16:53 | 0 | 0.15298 | 5507.423 | 16:53 | 2.2302 | 2.05 | 0.18015 | 2.3927e-05 | 0
[13 empty] | 16:53 | 1.0434 | 0.91146 | 0.91784 |  | 16:53 | 0 | 0.15298 | 5507.423 | 16:53 | 2.2308 | 2.0506 | 0.1802 | 2.3934e-05 | 0
[13 empty] | 16:54 | 1.0298 | 0.91146 | 0.91784 |  | 16:54 | 0 | 0.15298 | 5507.423 | 16:54 | 2.2315 | 2.0512 | 0.18025 | 2.394e-05 | 0
[13 empty] | 16:54 | 1.0164 | 0.91146 | 0.91784 |  | 16:54 | 0 | 0.15298 | 5507.423 | 16:54 | 2.2321 | 2.0518 | 0.1803 | 2.3948e-05 | 0
[13 empty] | 16:54 | 1.0034 | 0.91146 | 0.91784 |  | 16:54 | 0 | 0.15298 | 5507.423 | 16:54 | 2.2327 | 2.0523 | 0.18034 | 2.3953e-05 | 0
[13 empty] | 16:54 | 0.99062 | 0.91146 | 0.91784 |  | 16:54 | 0 | 0.15298 | 5507.423 | 16:54 | 2.2333 | 2.0529 | 0.18039 | 2.3961e-05 | 0
[13 empty] | 16:55 | 0.97811 | 0.91146 | 0.91784 |  | 16:55 | 0 | 0.15298 | 5507.423 | 16:55 | 2.2339 | 2.0535 | 0.18044 | 2.3967e-05 | 0
[13 empty] | 16:55 | 0.96585 | 0.91146 | 0.91784 |  | 16:55 | 0 | 0.15298 | 5507.423 | 16:55 | 2.2346 | 2.0541 | 0.18049 | 2.3973e-05 | 0
[13 empty] | 16:55 | 0.95385 | 0.91146 | 0.91784 |  | 16:55 | 0 | 0.15298 | 5507.423 | 16:55 | 2.2352 | 2.0546 | 0.18054 | 2.3978e-05 | 0
[13 empty] | 16:55 | 0.94209 | 0.91146 | 0.91784 |  | 16:55 | 0 | 0.15298 | 5507.423 | 16:55 | 2.2356 | 2.055 | 0.18058 | 2.3986e-05 | 0
[13 empty] | 16:56 | 0.93058 | 0.91146 | 0.91784 |  | 16:56 | 0 | 0.15298 | 5507.423 | 16:56 | 2.2362 | 2.0556 | 0.18063 | 2.3992e-05 | 0
[13 empty] | 16:56 | 0.9193 | 0.91146 | 0.91784 |  | 16:56 | 0 | 0.15298 | 5507.423 | 16:56 | 2.2369 | 2.0562 | 0.18067 | 2.3997e-05 | 0
[13 empty] | 16:56 | 0.90825 | 0.91146 | 0.91784 |  | 16:56 | 0 | 0.15298 | 5507.423 | 16:56 | 2.2373 | 2.0565 | 0.18072 | 2.4003e-05 | 0
[13 empty] | 16:56 | 0.89743 | 0.91146 | 0.91784 |  | 16:56 | 0 | 0.15298 | 5507.423 | 16:56 | 2.2379 | 2.0571 | 0.18076 | 2.4009e-05 | 0
[13 empty] | 16:56 | 0.88683 | 0.91146 | 0.91784 |  | 16:56 | 0 | 0.15298 | 5507.423 | 16:56 | 2.2385 | 2.0577 | 0.1808 | 2.4015e-05 | 0
[13 empty] | 16:57 | 0.87645 | 0.91146 | 0.91784 |  | 16:57 | 0 | 0.15298 | 5507.423 | 16:57 | 2.2389 | 2.0581 | 0.18085 | 2.402e-05 | 0
[13 empty] | 16:57 | 0.86628 | 0.91146 | 0.91784 |  | 16:57 | 0 | 0.15298 | 5507.423 | 16:57 | 2.2395 | 2.0586 | 0.18089 | 2.4026e-05 | 0
[13 empty] | 16:57 | 0.85633 | 0.91146 | 0.91784 |  | 16:57 | 0 | 0.15298 | 5507.423 | 16:57 | 2.24 | 2.059 | 0.18093 | 2.4032e-05 | 0
[13 empty] | 16:58 | 0.84657 | 0.91146 | 0.91784 |  | 16:58 | 0 | 0.15298 | 5507.423 | 16:58 | 2.2406 | 2.0596 | 0.18097 | 2.4037e-05 | 0
[13 empty] | 16:58 | 0.83702 | 0.91146 | 0.91784 |  | 16:58 | 0 | 0.15298 | 5507.423 | 16:58 | 2.241 | 2.06 | 0.18101 | 2.4043e-05 | 0
[13 empty] | 16:58 | 0.82766 | 0.91146 | 0.91784 |  | 16:58 | 0 | 0.15298 | 5507.423 | 16:58 | 2.2416 | 2.0605 | 0.18105 | 2.4047e-05 | 0
[13 empty] | 16:58 | 0.8185 | 0.91146 | 0.91784 |  | 16:58 | 0 | 0.15298 | 5507.423 | 16:58 | 2.242 | 2.0609 | 0.18109 | 2.4053e-05 | 0
[13 empty] | 16:59 | 0.80952 | 0.91146 | 0.91784 |  | 16:59 | 0 | 0.15298 | 5507.423 | 16:59 | 2.2425 | 2.0613 | 0.18113 | 2.4058e-05 | 0
[13 empty] | 16:59 | 0.80073 | 0.91146 | 0.91784 |  | 16:59 | 0 | 0.15298 | 5507.423 | 16:59 | 2.2431 | 2.0619 | 0.18117 | 2.4064e-05 | 0
[13 empty] | 16:59 | 0.79211 | 0.91146 | 0.91784 |  | 16:59 | 0 | 0.15298 | 5507.423 | 16:59 | 2.2435 | 2.0623 | 0.18121 | 2.4068e-05 | 0
[13 empty] | 16:59 | 0.78368 | 0.91146 | 0.91784 |  | 16:59 | 0 | 0.15298 | 5507.423 | 16:59 | 2.2439 | 2.0626 | 0.18125 | 2.4074e-05 | 0
[13 empty] | 17:00 | 0.77542 | 0.91146 | 0.91784 |  | 17:00 | 0 | 0.15298 | 5507.423 | 17:00 | 2.2443 | 2.063 | 0.18129 | 2.408e-05 | 0
[13 empty] | 17:00 | 0.76733 | 0.91146 | 0.91784 |  | 17:00 | 0 | 0.15298 | 5507.423 | 17:00 | 2.245 | 2.0636 | 0.18132 | 2.4083e-05 | 0
[13 empty] | 17:00 | 0.7594 | 0.91146 | 0.91784 |  | 17:00 | 0 | 0.15298 | 5507.423 | 17:00 | 2.2454 | 2.064 | 0.18136 | 2.4089e-05 | 0
[13 empty] | 17:00 | 0.75164 | 0.91146 | 0 |  | 17:00 | 0 | 0 | 5507.423 | 17:00 | 2.2458 | 2.0644 | 0.1814 | 2.4093e-05 | 0
[13 empty] | 17:00 | 0.74403 | 0.91146 | 0 |  | 17:00 | 0 | 0 | 5507.423 | 17:00 | 2.2462 | 2.0647 | 0.18143 | 2.4099e-05 | 0
[13 empty] | 17:01 | 0.73658 | 0.91146 | 0 |  | 17:01 | 0 | 0 | 5507.423 | 17:01 | 2.2466 | 2.0651 | 0.18147 | 2.4102e-05 | 0
[13 empty] | 17:01 | 0.72929 | 0.91146 | 0 |  | 17:01 | 0 | 0 | 5507.423 | 17:01 | 2.2472 | 2.0657 | 0.18151 | 2.4108e-05 | 0
[13 empty] | 17:01 | 1.1629 | 0.91146 | 0 |  | 17:01 | 0 | 0 | 5507.423 | 17:01 | 2.2479 | 2.0663 | 0.18156 | 2.4116e-05 | 0
[13 empty] | 17:02 | 1.1468 | 0.91146 | 0 |  | 17:02 | 0 | 0 | 5507.423 | 17:02 | 2.2485 | 2.0668 | 0.18162 | 2.4123e-05 | 0
[13 empty] | 17:02 | 1.1311 | 0.91146 | 0 |  | 17:02 | 0 | 0 | 5507.423 | 17:02 | 2.2493 | 2.0676 | 0.18168 | 2.4131e-05 | 0
[13 empty] | 17:02 | 1.1157 | 0.91146 | 0 |  | 17:02 | 0 | 0 | 5507.423 | 17:02 | 2.2499 | 2.0682 | 0.18173 | 2.4137e-05 | 0
[13 empty] | 17:02 | 1.1006 | 0.91146 | 0 |  | 17:02 | 0 | 0 | 5507.423 | 17:02 | 2.2506 | 2.0688 | 0.18178 | 2.4144e-05 | 0
[13 empty] | 17:03 | 1.0859 | 0.91146 | 0 |  | 17:03 | 0 | 0 | 5507.423 | 17:03 | 2.2512 | 2.0693 | 0.18184 | 2.4152e-05 | 0
[13 empty] | 17:03 | 1.0714 | 0.91146 | 0 |  | 17:03 | 0 | 0 | 5507.423 | 17:03 | 2.2518 | 2.0699 | 0.18189 | 2.416e-05 | 0
[13 empty] | 17:03 | 1.0572 | 0.91146 | 0 |  | 17:03 | 0 | 0 | 5507.423 | 17:03 | 2.2524 | 2.0705 | 0.18194 | 2.4165e-05 | 0
[13 empty] | 17:03 | 1.0434 | 0.91146 | 0 |  | 17:03 | 0 | 0 | 5507.423 | 17:03 | 2.2531 | 2.0711 | 0.18199 | 2.4173e-05 | 0
[13 empty] | 17:04 | 1.0298 | 0.91146 | 0 |  | 17:04 | 0 | 0 | 5507.423 | 17:04 | 2.2537 | 2.0716 | 0.18204 | 2.4179e-05 | 0
[13 empty] | 17:04 | 1.0164 | 0.91146 | 0 |  | 17:04 | 0 | 0 | 5507.423 | 17:04 | 2.2543 | 2.0722 | 0.18209 | 2.4186e-05 | 0
[13 empty] | 17:04 | 1.0034 | 0.91146 | 0 |  | 17:04 | 0 | 0 | 5507.423 | 17:04 | 2.2549 | 2.0728 | 0.18214 | 2.4192e-05 | 0
[13 empty] | 17:04 | 0.99062 | 0.91146 | 0 |  | 17:04 | 0 | 0 | 5507.423 | 17:04 | 2.2556 | 2.0733 | 0.18219 | 2.4198e-05 | 0
[13 empty] | 17:04 | 0.97811 | 0.91146 | 0 |  | 17:04 | 0 | 0 | 5507.423 | 17:04 | 2.2562 | 2.0739 | 0.18224 | 2.4206e-05 | 0
[13 empty] | 17:05 | 0.96585 | 0.91146 | 0 |  | 17:05 | 0 | 0 | 5507.423 | 17:05 | 2.2568 | 2.0745 | 0.18228 | 2.4211e-05 | 0
[13 empty] | 17:05 | 0.95385 | 0.91146 | 0 |  | 17:05 | 0 | 0 | 5507.423 | 17:05 | 2.2574 | 2.0751 | 0.18233 | 2.4217e-05 | 0
[13 empty] | 17:05 | 0.94209 | 0.91146 | 0 |  | 17:05 | 0 | 0 | 5507.423 | 17:05 | 2.2578 | 2.0754 | 0.18238 | 2.4223e-05 | 0
[13 empty] | 17:06 | 0.93058 | 0.91146 | 0 |  | 17:06 | 0 | 0 | 5507.423 | 17:06 | 2.2585 | 2.076 | 0.18242 | 2.423e-05 | 0
[13 empty] | 17:06 | 0.9193 | 0.91146 | 0 |  | 17:06 | 0 | 0 | 5507.423 | 17:06 | 2.2591 | 2.0766 | 0.18247 | 2.4236e-05 | 0
[13 empty] | 17:06 | 0.90825 | 0.91146 | 0 |  | 17:06 | 0 | 0 | 5507.423 | 17:06 | 2.2595 | 2.077 | 0.18251 | 2.4242e-05 | 0
[13 empty] | 17:06 | 0.89743 | 0.91146 | 0 |  | 17:06 | 0 | 0 | 5507.423 | 17:06 | 2.2601 | 2.0775 | 0.18256 | 2.4248e-05 | 0
[13 empty] | 17:06 | 0.88683 | 0.91146 | 0 |  | 17:06 | 0 | 0 | 5507.423 | 17:06 | 2.2607 | 2.0781 | 0.1826 | 2.4253e-05 | 0
[13 empty] | 17:07 | 0.87645 | 0.91146 | 0 |  | 17:07 | 0 | 0 | 5507.423 | 17:07 | 2.2612 | 2.0785 | 0.18264 | 2.4259e-05 | 0
[13 empty] | 17:07 | 0.86628 | 0.91146 | 0 |  | 17:07 | 0 | 0 | 5507.423 | 17:07 | 2.2618 | 2.0791 | 0.18268 | 2.4265e-05 | 0
[13 empty] | 17:07 | 0.85633 | 0.91146 | 0 |  | 17:07 | 0 | 0 | 5507.423 | 17:07 | 2.2622 | 2.0795 | 0.18273 | 2.427e-05 | 0
[13 empty] | 17:08 | 0.84657 | 0.91146 | 0 |  | 17:08 | 0 | 0 | 5507.423 | 17:08 | 2.2628 | 2.08 | 0.18277 | 2.4276e-05 | 0
[13 empty] | 17:08 | 0.83702 | 0.91146 | 0 |  | 17:08 | 0 | 0 | 5507.423 | 17:08 | 2.2632 | 2.0804 | 0.18281 | 2.428e-05 | 0
[13 empty] | 17:08 | 0.82766 | 0.91146 | 0 |  | 17:08 | 0 | 0 | 5507.423 | 17:08 | 2.2637 | 2.0808 | 0.18285 | 2.4286e-05 | 0
[13 empty] | 17:08 | 0.8185 | 0.91146 | 0 |  | 17:08 | 0 | 0 | 5507.423 | 17:08 | 2.2643 | 2.0814 | 0.18289 | 2.4292e-05 | 0
[13 empty] | 17:08 | 0.80952 | 0.91146 | 0 |  | 17:08 | 0 | 0 | 5507.423 | 17:08 | 2.2647 | 2.0817 | 0.18293 | 2.4297e-05 | 0
[13 empty] | 17:09 | 0.80073 | 0.91146 | 0 |  | 17:09 | 0 | 0 | 5507.423 | 17:09 | 2.2653 | 2.0823 | 0.18297 | 2.4303e-05 | 0
[13 empty] | 17:09 | 0.79211 | 0.91146 | 0 |  | 17:09 | 0 | 0 | 5507.423 | 17:09 | 2.2657 | 2.0827 | 0.18301 | 2.4307e-05 | 0
[13 empty] | 17:09 | 0.78368 | 0.91146 | 0 |  | 17:09 | 0 | 0 | 5507.423 | 17:09 | 2.2662 | 2.0831 | 0.18304 | 2.4313e-05 | 0
[13 empty] | 17:10 | 0.77542 | 0.91146 | 0 |  | 17:10 | 0 | 0 | 5507.423 | 17:10 | 2.2666 | 2.0835 | 0.18308 | 2.4318e-05 | 0
[13 empty] | 17:10 | 0.76733 | 0.91146 | 0 |  | 17:10 | 0 | 0 | 5507.423 | 17:10 | 2.2672 | 2.084 | 0.18312 | 2.4322e-05 | 0
[13 empty] | 17:10 | 0.7594 | 0.91146 | 0 |  | 17:10 | 0 | 0 | 5507.423 | 17:10 | 2.2676 | 2.0844 | 0.18316 | 2.4328e-05 | 0
[13 empty] | 17:10 | 0.75164 | 0.91146 | 0 |  | 17:10 | 0 | 0 | 5507.423 | 17:10 | 2.268 | 2.0848 | 0.18319 | 2.4332e-05 | 0
[13 empty] | 17:10 | 0.74403 | 0.91146 | 0 |  | 17:10 | 0 | 0 | 5507.423 | 17:10 | 2.2684 | 2.0852 | 0.18323 | 2.4337e-05 | 0
[13 empty] | 17:11 | 0.73658 | 0.91146 | 0 |  | 17:11 | 0 | 0 | 5507.423 | 17:11 | 2.2689 | 2.0856 | 0.18327 | 2.4341e-05 | 0
[13 empty] | 17:11 | 0.72929 | 0.91146 | 0 |  | 17:11 | 0 | 0 | 5507.423 | 17:11 | 2.2695 | 2.0861 | 0.1833 | 2.4347e-05 | 0
[13 empty] | 17:11 | 1.1629 | 0.91146 | 0 |  | 17:11 | 0 | 0 | 5507.423 | 17:11 | 2.2701 | 2.0867 | 0.18336 | 2.4355e-05 | 0
[13 empty] | 17:12 | 1.1468 | 0.91146 | 0 |  | 17:12 | 0 | 0 | 5507.423 | 17:12 | 2.2707 | 2.0873 | 0.18342 | 2.4362e-05 | 0
[13 empty] | 17:12 | 1.1311 | 0.91146 | 0 |  | 17:12 | 0 | 0 | 5507.423 | 17:12 | 2.2715 | 2.088 | 0.18347 | 2.437e-05 | 0
[13 empty] | 17:12 | 1.1157 | 0.91146 | 0 |  | 17:12 | 0 | 0 | 5507.423 | 17:12 | 2.2722 | 2.0886 | 0.18352 | 2.4376e-05 | 0
[13 empty] | 17:12 | 1.1006 | 0.91146 | 0 |  | 17:12 | 0 | 0 | 5507.423 | 17:12 | 2.2728 | 2.0892 | 0.18358 | 2.4383e-05 | 0
[13 empty] | 17:12 | 1.0859 | 0.91146 | 0 |  | 17:12 | 0 | 0 | 5507.423 | 17:12 | 2.2734 | 2.0898 | 0.18363 | 2.4391e-05 | 0
[13 empty] | 17:13 | 1.0714 | 0.91146 | 0 |  | 17:13 | 0 | 0 | 5507.423 | 17:13 | 2.274 | 2.0903 | 0.18368 | 2.4397e-05 | 0
[13 empty] | 17:13 | 1.0572 | 0.91146 | 0 |  | 17:13 | 0 | 0 | 5507.423 | 17:13 | 2.2747 | 2.0909 | 0.18374 | 2.4404e-05 | 0
[13 empty] | 17:13 | 1.0434 | 0.91146 | 0 |  | 17:13 | 0 | 0 | 5507.423 | 17:13 | 2.2753 | 2.0915 | 0.18379 | 2.4412e-05 | 0
[13 empty] | 17:14 | 1.0298 | 0.91146 | 0 |  | 17:14 | 0 | 0 | 5507.423 | 17:14 | 2.2759 | 2.0921 | 0.18384 | 2.4418e-05 | 0
[13 empty] | 17:14 | 1.0164 | 0.91146 | 0 |  | 17:14 | 0 | 0 | 5507.423 | 17:14 | 2.2765 | 2.0926 | 0.18389 | 2.4425e-05 | 0
[13 empty] | 17:14 | 1.0034 | 0.91146 | 0 |  | 17:14 | 0 | 0 | 5507.423 | 17:14 | 2.2772 | 2.0932 | 0.18394 | 2.4431e-05 | 0
[13 empty] | 17:14 | 0.99062 | 0.91146 | 0 |  | 17:14 | 0 | 0 | 5507.423 | 17:14 | 2.2778 | 2.0938 | 0.18398 | 2.4437e-05 | 0
[13 empty] | 17:14 | 0.97811 | 0.91146 | 0 |  | 17:14 | 0 | 0 | 5507.423 | 17:14 | 2.2784 | 2.0944 | 0.18403 | 2.4444e-05 | 0
[13 empty] | 17:15 | 0.96585 | 0.91146 | 0 |  | 17:15 | 0 | 0 | 5507.423 | 17:15 | 2.279 | 2.0949 | 0.18408 | 2.445e-05 | 0
[13 empty] | 17:15 | 0.95385 | 0.91146 | 0 |  | 17:15 | 0 | 0 | 5507.423 | 17:15 | 2.2796 | 2.0955 | 0.18413 | 2.4456e-05 | 0
[13 empty] | 17:15 | 0.94209 | 0.91146 | 0 |  | 17:15 | 0 | 0 | 5507.423 | 17:15 | 2.2801 | 2.0959 | 0.18417 | 2.4461e-05 | 0
[13 empty] | 17:16 | 0.93058 | 0.91146 | 0 |  | 17:16 | 0 | 0 | 5507.423 | 17:16 | 2.2807 | 2.0965 | 0.18422 | 2.4469e-05 | 0
[13 empty] | 17:16 | 0.9193 | 0.91146 | 0 |  | 17:16 | 0 | 0 | 5507.423 | 17:16 | 2.2813 | 2.097 | 0.18426 | 2.4475e-05 | 0
[13 empty] | 17:16 | 0.90825 | 0.91146 | 0 |  | 17:16 | 0 | 0 | 5507.423 | 17:16 | 2.2817 | 2.0974 | 0.18431 | 2.4481e-05 | 0
[13 empty] | 17:16 | 0.89743 | 0.91146 | 0 |  | 17:16 | 0 | 0 | 5507.423 | 17:16 | 2.2824 | 2.098 | 0.18435 | 2.4486e-05 | 0
[13 empty] | 17:16 | 0.88683 | 0.91146 | 0 |  | 17:16 | 0 | 0 | 5507.423 | 17:16 | 2.283 | 2.0986 | 0.1844 | 2.4492e-05 | 0
[13 empty] | 17:17 | 0.87645 | 0.91146 | 0 |  | 17:17 | 0 | 0 | 5507.423 | 17:17 | 2.2834 | 2.0989 | 0.18444 | 2.4498e-05 | 0
[13 empty] | 17:17 | 0.86628 | 0.91146 | 0 |  | 17:17 | 0 | 0 | 5507.423 | 17:17 | 2.284 | 2.0995 | 0.18448 | 2.4503e-05 | 0
[13 empty] | 17:17 | 0.85633 | 0.91146 | 0 |  | 17:17 | 0 | 0 | 5507.423 | 17:17 | 2.2844 | 2.0999 | 0.18452 | 2.4509e-05 | 0
[13 empty] | 17:18 | 0.84657 | 0.91146 | 0 |  | 17:18 | 0 | 0 | 5507.423 | 17:18 | 2.2851 | 2.1005 | 0.18456 | 2.4515e-05 | 0
[13 empty] | 17:18 | 0.83702 | 0.91146 | 0 |  | 17:18 | 0 | 0 | 5507.423 | 17:18 | 2.2855 | 2.1008 | 0.1846 | 2.4519e-05 | 0
[13 empty] | 17:18 | 0.82766 | 0.91146 | 0 |  | 17:18 | 0 | 0 | 5507.423 | 17:18 | 2.2859 | 2.1012 | 0.18464 | 2.4525e-05 | 0
[13 empty] | 17:18 | 0.8185 | 0.91146 | 0 |  | 17:18 | 0 | 0 | 5507.423 | 17:18 | 2.2865 | 2.1018 | 0.18468 | 2.453e-05 | 0
[13 empty] | 17:18 | 0.80952 | 0.91146 | 0 |  | 17:18 | 0 | 0 | 5507.423 | 17:18 | 2.2869 | 2.1022 | 0.18472 | 2.4536e-05 | 0
[13 empty] | 17:19 | 0.80073 | 0.91146 | 0 |  | 17:19 | 0 | 0 | 5507.423 | 17:19 | 2.2875 | 2.1028 | 0.18476 | 2.454e-05 | 0
[13 empty] | 17:19 | 0.79211 | 0.91146 | 0 |  | 17:19 | 0 | 0 | 5507.423 | 17:19 | 2.288 | 2.1031 | 0.1848 | 2.4546e-05 | 0
[13 empty] | 17:19 | 0.78368 | 0.91146 | 0 |  | 17:19 | 0 | 0 | 5507.423 | 17:19 | 2.2884 | 2.1035 | 0.18484 | 2.4551e-05 | 0
[13 empty] | 17:20 | 0.77542 | 0.91146 | 0 |  | 17:20 | 0 | 0 | 5507.423 | 17:20 | 2.2888 | 2.1039 | 0.18488 | 2.4555e-05 | 0
[13 empty] | 17:20 | 0.76733 | 0.91146 | 0 |  | 17:20 | 0 | 0 | 5507.423 | 17:20 | 2.2894 | 2.1045 | 0.18492 | 2.4561e-05 | 0
[13 empty] | 17:20 | 0.7594 | 0.91146 | 0 |  | 17:20 | 0 | 0 | 5507.423 | 17:20 | 2.2898 | 2.1049 | 0.18495 | 2.4567e-05 | 0
[13 empty] | 17:20 | 0.75164 | 0.91146 | 0 |  | 17:20 | 0 | 0 | 5507.423 | 17:20 | 2.2903 | 2.1052 | 0.18499 | 2.457e-05 | 0
[13 empty] | 17:20 | 0.74403 | 0.91146 | 0 |  | 17:20 | 0 | 0 | 5507.423 | 17:20 | 2.2907 | 2.1056 | 0.18503 | 2.4576e-05 | 0
[13 empty] | 17:21 | 0.73658 | 0.91146 | 0 |  | 17:21 | 0 | 0 | 5507.423 | 17:21 | 2.2911 | 2.106 | 0.18506 | 2.458e-05 | 0
[13 empty] | 17:21 | 0.72929 | 0.91146 | 0 |  | 17:21 | 0 | 0 | 5507.423 | 17:21 | 2.2915 | 2.1064 | 0.1851 | 2.4586e-05 | 0
[13 empty] | 17:21 | 1.1629 | 0.91146 | 0 |  | 17:21 | 0 | 0 | 5507.423 | 17:21 | 2.2923 | 2.1071 | 0.18516 | 2.4593e-05 | 0
[13 empty] | 17:22 | 1.1468 | 0.91146 | 0 |  | 17:22 | 0 | 0 | 5507.423 | 17:22 | 2.293 | 2.1077 | 0.18521 | 2.4601e-05 | 0
[13 empty] | 17:22 | 1.1311 | 0.91146 | 0 |  | 17:22 | 0 | 0 | 5507.423 | 17:22 | 2.2938 | 2.1085 | 0.18527 | 2.4607e-05 | 0
[13 empty] | 17:22 | 1.1157 | 0.91146 | 0 |  | 17:22 | 0 | 0 | 5507.423 | 17:22 | 2.2944 | 2.1091 | 0.18532 | 2.4614e-05 | 0
[13 empty] | 17:22 | 1.1006 | 0.91146 | 0 |  | 17:22 | 0 | 0 | 5507.423 | 17:22 | 2.295 | 2.1096 | 0.18537 | 2.4622e-05 | 0
[13 empty] | 17:22 | 1.0859 | 0.91146 | 0 |  | 17:22 | 0 | 0 | 5507.423 | 17:22 | 2.2957 | 2.1102 | 0.18543 | 2.463e-05 | 0
[13 empty] | 17:23 | 1.0714 | 0.91146 | 0 |  | 17:23 | 0 | 0 | 5507.423 | 17:23 | 2.2963 | 2.1108 | 0.18548 | 2.4635e-05 | 0
[13 empty] | 17:23 | 1.0572 | 0.91146 | 0 |  | 17:23 | 0 | 0 | 5507.423 | 17:23 | 2.2969 | 2.1113 | 0.18553 | 2.4643e-05 | 0
[13 empty] | 17:23 | 1.0434 | 0.91146 | 0 |  | 17:23 | 0 | 0 | 5507.423 | 17:23 | 2.2975 | 2.1119 | 0.18558 | 2.4649e-05 | 0
[13 empty] | 17:24 | 1.0298 | 0.91146 | 0 |  | 17:24 | 0 | 0 | 5507.423 | 17:24 | 2.2982 | 2.1125 | 0.18563 | 2.4656e-05 | 0
[13 empty] | 17:24 | 1.0164 | 0.91146 | 0 |  | 17:24 | 0 | 0 | 5507.423 | 17:24 | 2.2988 | 2.1131 | 0.18568 | 2.4662e-05 | 0
[13 empty] | 17:24 | 1.0034 | 0.91146 | 0 |  | 17:24 | 0 | 0 | 5507.423 | 17:24 | 2.2994 | 2.1136 | 0.18573 | 2.467e-05 | 0
[13 empty] | 17:24 | 0.99062 | 0.91146 | 0 |  | 17:24 | 0 | 0 | 5507.423 | 17:24 | 2.3 | 2.1142 | 0.18578 | 2.4675e-05 | 0
[13 empty] | 17:24 | 0.97811 | 0.91146 | 0 |  | 17:24 | 0 | 0 | 5507.423 | 17:24 | 2.3006 | 2.1148 | 0.18583 | 2.4681e-05 | 0
[13 empty] | 17:25 | 0.96585 | 0.91146 | 0 |  | 17:25 | 0 | 0 | 5507.423 | 17:25 | 2.3013 | 2.1154 | 0.18588 | 2.4689e-05 | 0
[13 empty] | 17:25 | 0.95385 | 0.91146 | 0 |  | 17:25 | 0 | 0 | 5507.423 | 17:25 | 2.3019 | 2.1159 | 0.18592 | 2.4694e-05 | 0
[13 empty] | 17:25 | 0.94209 | 0.91146 | 0 |  | 17:25 | 0 | 0 | 5507.423 | 17:25 | 2.3023 | 2.1163 | 0.18597 | 2.47e-05 | 0
[13 empty] | 17:26 | 0.93058 | 0.91146 | 0 |  | 17:26 | 0 | 0 | 5507.423 | 17:26 | 2.3029 | 2.1169 | 0.18601 | 2.4706e-05 | 0
[13 empty] | 17:26 | 0.9193 | 0.91146 | 0 |  | 17:26 | 0 | 0 | 5507.423 | 17:26 | 2.3035 | 2.1175 | 0.18606 | 2.4712e-05 | 0
[13 empty] | 17:26 | 0.90825 | 0.91146 | 0 |  | 17:26 | 0 | 0 | 5507.423 | 17:26 | 2.304 | 2.1178 | 0.1861 | 2.4719e-05 | 0
[13 empty] | 17:26 | 0.89743 | 0.91146 | 0 |  | 17:26 | 0 | 0 | 5507.423 | 17:26 | 2.3046 | 2.1184 | 0.18615 | 2.4725e-05 | 0
[13 empty] | 17:26 | 0.88683 | 0.91146 | 0 |  | 17:26 | 0 | 0 | 5507.423 | 17:26 | 2.3052 | 2.119 | 0.18619 | 2.4731e-05 | 0
[13 empty] | 17:27 | 0.87645 | 0.91146 | 0 |  | 17:27 | 0 | 0 | 5507.423 | 17:27 | 2.3056 | 2.1194 | 0.18623 | 2.4736e-05 | 0
[13 empty] | 17:27 | 0.86628 | 0.91146 | 0 |  | 17:27 | 0 | 0 | 5507.423 | 17:27 | 2.3062 | 2.1199 | 0.18627 | 2.4742e-05 | 0
[13 empty] | 17:27 | 0.85633 | 0.91146 | 0 |  | 17:27 | 0 | 0 | 5507.423 | 17:27 | 2.3067 | 2.1203 | 0.18632 | 2.4746e-05 | 0
[13 empty] | 17:27 | 0.84657 | 0.91146 | 0 |  | 17:27 | 0 | 0 | 5507.423 | 17:27 | 2.3073 | 2.1209 | 0.18636 | 2.4752e-05 | 0
[13 empty] | 17:28 | 0.83702 | 0.91146 | 0 |  | 17:28 | 0 | 0 | 5507.423 | 17:28 | 2.3077 | 2.1213 | 0.1864 | 2.4758e-05 | 0
[13 empty] | 17:28 | 0.82766 | 0.91146 | 0 |  | 17:28 | 0 | 0 | 5507.423 | 17:28 | 2.3081 | 2.1217 | 0.18644 | 2.4763e-05 | 0
[13 empty] | 17:28 | 0.8185 | 0.91146 | 0 |  | 17:28 | 0 | 0 | 5507.423 | 17:28 | 2.3087 | 2.1222 | 0.18648 | 2.4769e-05 | 0
[13 empty] | 17:28 | 0.80952 | 0.91146 | 0 |  | 17:28 | 0 | 0 | 5507.423 | 17:28 | 2.3092 | 2.1226 | 0.18652 | 2.4775e-05 | 0
[13 empty] | 17:29 | 0.80073 | 0.91146 | 0 |  | 17:29 | 0 | 0 | 5507.423 | 17:29 | 2.3098 | 2.1232 | 0.18656 | 2.4779e-05 | 0
[13 empty] | 17:29 | 0.79211 | 0.91146 | 0 |  | 17:29 | 0 | 0 | 5507.423 | 17:29 | 2.3102 | 2.1236 | 0.1866 | 2.4784e-05 | 0
[13 empty] | 17:29 | 0.78368 | 0.91146 | 0 |  | 17:29 | 0 | 0 | 5507.423 | 17:29 | 2.3106 | 2.124 | 0.18664 | 2.479e-05 | 0
[13 empty] | 17:30 | 0.77542 | 0.91146 | 0 |  | 17:30 | 0 | 0 | 5507.423 | 17:30 | 2.311 | 2.1243 | 0.18667 | 2.4794e-05 | 0
[13 empty] | 17:30 | 0.76733 | 0.91146 | 0 |  | 17:30 | 0 | 0 | 5507.423 | 17:30 | 2.3116 | 2.1249 | 0.18671 | 2.48e-05 | 0
[13 empty] | 17:30 | 0.7594 | 0.91146 | 0 |  | 17:30 | 0 | 0 | 5507.423 | 17:30 | 2.3121 | 2.1253 | 0.18675 | 2.4803e-05 | 0
[13 empty] | 17:30 | 0.75164 | 0.91146 | 0 |  | 17:30 | 0 | 0 | 5507.423 | 17:30 | 2.3125 | 2.1257 | 0.18678 | 2.4809e-05 | 0
[13 empty] | 17:30 | 0.74403 | 0.91146 | 0 |  | 17:30 | 0 | 0 | 5507.423 | 17:30 | 2.3129 | 2.1261 | 0.18682 | 2.4815e-05 | 0
[13 empty] | 17:31 | 0.73658 | 0.91146 | 0 |  | 17:31 | 0 | 0 | 5507.423 | 17:31 | 2.3133 | 2.1264 | 0.18686 | 2.4819e-05 | 0
[13 empty] | 17:31 | 0.72929 | 0.91146 | 0 |  | 17:31 | 0 | 0 | 5507.423 | 17:31 | 2.3137 | 2.1268 | 0.18689 | 2.4824e-05 | 0
[13 empty] | 17:31 | 1.1629 | 0.91146 | 0 |  | 17:31 | 0 | 0 | 5507.423 | 17:31 | 2.3146 | 2.1276 | 0.18695 | 2.4832e-05 | 0
[13 empty] | 17:31 | 1.1468 | 0.91146 | 0 |  | 17:31 | 0 | 0 | 5507.423 | 17:31 | 2.3152 | 2.1282 | 0.18701 | 2.4838e-05 | 0
[13 empty] | 17:32 | 1.1311 | 0.91146 | 0 |  | 17:32 | 0 | 0 | 5507.423 | 17:32 | 2.3158 | 2.1287 | 0.18706 | 2.4845e-05 | 0
[13 empty] | 17:32 | 1.1157 | 0.91146 | 0 |  | 17:32 | 0 | 0 | 5507.423 | 17:32 | 2.3166 | 2.1295 | 0.18712 | 2.4853e-05 | 0
[13 empty] | 17:32 | 1.1006 | 0.91146 | 0 |  | 17:32 | 0 | 0 | 5507.423 | 17:32 | 2.3173 | 2.1301 | 0.18717 | 2.4861e-05 | 0
[13 empty] | 17:32 | 1.0859 | 0.91146 | 0 |  | 17:32 | 0 | 0 | 5507.423 | 17:32 | 2.3179 | 2.1306 | 0.18722 | 2.4866e-05 | 0
[13 empty] | 17:33 | 1.0714 | 0.91146 | 0 |  | 17:33 | 0 | 0 | 5507.423 | 17:33 | 2.3185 | 2.1312 | 0.18728 | 2.4874e-05 | 0
[13 empty] | 17:33 | 1.0572 | 0.91146 | 0 |  | 17:33 | 0 | 0 | 5507.423 | 17:33 | 2.3191 | 2.1318 | 0.18733 | 2.4882e-05 | 0
[13 empty] | 17:33 | 1.0434 | 0.91146 | 0 |  | 17:33 | 0 | 0 | 5507.423 | 17:33 | 2.3198 | 2.1324 | 0.18738 | 2.4887e-05 | 0
[13 empty] | 17:34 | 1.0298 | 0.91146 | 0 |  | 17:34 | 0 | 0 | 5507.423 | 17:34 | 2.3204 | 2.1329 | 0.18743 | 2.4895e-05 | 0
[13 empty] | 17:34 | 1.0164 | 0.91146 | 0 |  | 17:34 | 0 | 0 | 5507.423 | 17:34 | 2.321 | 2.1335 | 0.18748 | 2.4901e-05 | 0
[13 empty] | 17:34 | 1.0034 | 0.91146 | 0 |  | 17:34 | 0 | 0 | 5507.423 | 17:34 | 2.3216 | 2.1341 | 0.18753 | 2.4908e-05 | 0
[13 empty] | 17:34 | 0.99062 | 0.91146 | 0 |  | 17:34 | 0 | 0 | 5507.423 | 17:34 | 2.3222 | 2.1346 | 0.18757 | 2.4914e-05 | 0
[13 empty] | 17:34 | 0.97811 | 0.91146 | 0 |  | 17:34 | 0 | 0 | 5507.423 | 17:34 | 2.3229 | 2.1352 | 0.18762 | 2.492e-05 | 0
[13 empty] | 17:35 | 0.96585 | 0.91146 | 0 |  | 17:35 | 0 | 0 | 5507.423 | 17:35 | 2.3235 | 2.1358 | 0.18767 | 2.4927e-05 | 0
[13 empty] | 17:35 | 0.95385 | 0.91146 | 0 |  | 17:35 | 0 | 0 | 5507.423 | 17:35 | 2.3241 | 2.1364 | 0.18772 | 2.4933e-05 | 0
[13 empty] | 17:35 | 0.94209 | 0.91146 | 0 |  | 17:35 | 0 | 0 | 5507.423 | 17:35 | 2.3245 | 2.1368 | 0.18776 | 2.4939e-05 | 0
[13 empty] | 17:35 | 0.93058 | 0.91146 | 0 |  | 17:35 | 0 | 0 | 5507.423 | 17:35 | 2.3252 | 2.1373 | 0.18781 | 2.4945e-05 | 0
[13 empty] | 17:36 | 0.9193 | 0.91146 | 0 |  | 17:36 | 0 | 0 | 5507.423 | 17:36 | 2.3258 | 2.1379 | 0.18785 | 2.495e-05 | 0
[13 empty] | 17:36 | 0.90825 | 0.91146 | 0 |  | 17:36 | 0 | 0 | 5507.423 | 17:36 | 2.3262 | 2.1383 | 0.1879 | 2.4956e-05 | 0
[13 empty] | 17:36 | 0.89743 | 0.91146 | 0 |  | 17:36 | 0 | 0 | 5507.423 | 17:36 | 2.3268 | 2.1389 | 0.18794 | 2.4964e-05 | 0
[13 empty] | 17:36 | 0.88683 | 0.91146 | 0 |  | 17:36 | 0 | 0 | 5507.423 | 17:36 | 2.3274 | 2.1394 | 0.18799 | 2.497e-05 | 0
[13 empty] | 17:37 | 0.87645 | 0.91146 | 0 |  | 17:37 | 0 | 0 | 5507.423 | 17:37 | 2.3279 | 2.1398 | 0.18803 | 2.4973e-05 | 0
[13 empty] | 17:37 | 0.86628 | 0.91146 | 0 |  | 17:37 | 0 | 0 | 5507.423 | 17:37 | 2.3285 | 2.1404 | 0.18807 | 2.4979e-05 | 0
[13 empty] | 17:37 | 0.85633 | 0.91146 | 0 |  | 17:37 | 0 | 0 | 5507.423 | 17:37 | 2.3289 | 2.1408 | 0.18811 | 2.4985e-05 | 0
[13 empty] | 17:38 | 0.84657 | 0.91146 | 0 |  | 17:38 | 0 | 0 | 5507.423 | 17:38 | 2.3295 | 2.1413 | 0.18815 | 2.4991e-05 | 0
[13 empty] | 17:38 | 0.83702 | 0.91146 | 0 |  | 17:38 | 0 | 0 | 5507.423 | 17:38 | 2.3299 | 2.1417 | 0.18819 | 2.4996e-05 | 0
[13 empty] | 17:38 | 0.82766 | 0.91146 | 0 |  | 17:38 | 0 | 0 | 5507.423 | 17:38 | 2.3304 | 2.1421 | 0.18824 | 2.5002e-05 | 0
[13 empty] | 17:38 | 0.8185 | 0.91146 | 0 |  | 17:38 | 0 | 0 | 5507.423 | 17:38 | 2.331 | 2.1427 | 0.18828 | 2.5008e-05 | 0
[13 empty] | 17:38 | 0.80952 | 0.91146 | 0 |  | 17:38 | 0 | 0 | 5507.423 | 17:38 | 2.3314 | 2.1431 | 0.18831 | 2.5012e-05 | 0
[13 empty] | 17:39 | 0.80073 | 0.91146 | 0 |  | 17:39 | 0 | 0 | 5507.423 | 17:39 | 2.332 | 2.1436 | 0.18835 | 2.5017e-05 | 0
[13 empty] | 17:39 | 0.79211 | 0.91146 | 0 |  | 17:39 | 0 | 0 | 5507.423 | 17:39 | 2.3324 | 2.144 | 0.18839 | 2.5023e-05 | 0
[13 empty] | 17:39 | 0.78368 | 0.91146 | 0 |  | 17:39 | 0 | 0 | 5507.423 | 17:39 | 2.3328 | 2.1444 | 0.18843 | 2.5029e-05 | 0
[13 empty] | 17:40 | 0.77542 | 0.91146 | 0 |  | 17:40 | 0 | 0 | 5507.423 | 17:40 | 2.3333 | 2.1448 | 0.18847 | 2.5033e-05 | 0
[13 empty] | 17:40 | 0.76733 | 0.91146 | 0 |  | 17:40 | 0 | 0 | 5507.423 | 17:40 | 2.3339 | 2.1453 | 0.18851 | 2.5038e-05 | 0
[13 empty] | 17:40 | 0.7594 | 0.91146 | 0 |  | 17:40 | 0 | 0 | 5507.423 | 17:40 | 2.3343 | 2.1457 | 0.18854 | 2.5042e-05 | 0
[13 empty] | 17:40 | 0.75164 | 0.91146 | 0 |  | 17:40 | 0 | 0 | 5507.423 | 17:40 | 2.3347 | 2.1461 | 0.18858 | 2.5048e-05 | 0
[13 empty] | 17:40 | 0.74403 | 0.91146 | 0 |  | 17:40 | 0 | 0 | 5507.423 | 17:40 | 2.3351 | 2.1465 | 0.18862 | 2.5052e-05 | 0
[13 empty] | 17:41 | 0.73658 | 0.91146 | 0 |  | 17:41 | 0 | 0 | 5507.423 | 17:41 | 2.3355 | 2.1469 | 0.18865 | 2.5057e-05 | 0
[13 empty] | 17:41 | 0.72929 | 0.91146 | 0 |  | 17:41 | 0 | 0 | 5507.423 | 17:41 | 2.336 | 2.1473 | 0.18869 | 2.5061e-05 | 0
[13 empty] | 17:41 | 1.1629 | 0.91146 | 0 |  | 17:41 | 0 | 0 | 5507.423 | 17:41 | 2.3368 | 2.148 | 0.18875 | 2.5069e-05 | 0
[13 empty] | 17:42 | 1.1468 | 0.91146 | 0 |  | 17:42 | 0 | 0 | 5507.423 | 17:42 | 2.3374 | 2.1486 | 0.1888 | 2.5076e-05 | 0
[13 empty] | 17:42 | 1.1311 | 0.91146 | 0 |  | 17:42 | 0 | 0 | 5507.423 | 17:42 | 2.338 | 2.1492 | 0.18886 | 2.5084e-05 | 0
[13 empty] | 17:42 | 1.1157 | 0.91146 | 0 |  | 17:42 | 0 | 0 | 5507.423 | 17:42 | 2.3389 | 2.1499 | 0.18891 | 2.5092e-05 | 0
[13 empty] | 17:42 | 1.1006 | 0.91146 | 0 |  | 17:42 | 0 | 0 | 5507.423 | 17:42 | 2.3395 | 2.1505 | 0.18897 | 2.5099e-05 | 0
[13 empty] | 17:42 | 1.0859 | 0.91146 | 0 |  | 17:42 | 0 | 0 | 5507.423 | 17:42 | 2.3401 | 2.1511 | 0.18902 | 2.5105e-05 | 0
[13 empty] | 17:43 | 1.0714 | 0.91146 | 0 |  | 17:43 | 0 | 0 | 5507.423 | 17:43 | 2.3407 | 2.1516 | 0.18907 | 2.5113e-05 | 0
[13 empty] | 17:43 | 1.0572 | 0.91146 | 0 |  | 17:43 | 0 | 0 | 5507.423 | 17:43 | 2.3414 | 2.1522 | 0.18912 | 2.512e-05 | 0
[13 empty] | 17:43 | 1.0434 | 0.91146 | 0 |  | 17:43 | 0 | 0 | 5507.423 | 17:43 | 2.342 | 2.1528 | 0.18917 | 2.5126e-05 | 0
[13 empty] | 17:44 | 1.0298 | 0.91146 | 0 |  | 17:44 | 0 | 0 | 5507.423 | 17:44 | 2.3426 | 2.1534 | 0.18922 | 2.5134e-05 | 0
[13 empty] | 17:44 | 1.0164 | 0.91146 | 0 |  | 17:44 | 0 | 0 | 5507.423 | 17:44 | 2.3432 | 2.1539 | 0.18927 | 2.5139e-05 | 0
[13 empty] | 17:44 | 1.0034 | 0.91146 | 0 |  | 17:44 | 0 | 0 | 5507.423 | 17:44 | 2.3439 | 2.1545 | 0.18932 | 2.5147e-05 | 0
[13 empty] | 17:44 | 0.99062 | 0.91146 | 0 |  | 17:44 | 0 | 0 | 5507.423 | 17:44 | 2.3445 | 2.1551 | 0.18937 | 2.5153e-05 | 0
[13 empty] | 17:44 | 0.97811 | 0.91146 | 0 |  | 17:44 | 0 | 0 | 5507.423 | 17:44 | 2.3451 | 2.1557 | 0.18942 | 2.5159e-05 | 0
[13 empty] | 17:45 | 0.96585 | 0.91146 | 0 |  | 17:45 | 0 | 0 | 5507.423 | 17:45 | 2.3457 | 2.1562 | 0.18947 | 2.5164e-05 | 0
[13 empty] | 17:45 | 0.95385 | 0.91146 | 0 |  | 17:45 | 0 | 0 | 5507.423 | 17:45 | 2.3463 | 2.1568 | 0.18951 | 2.5172e-05 | 0
[13 empty] | 17:45 | 0.94209 | 0.91146 | 0 |  | 17:45 | 0 | 0 | 5507.423 | 17:45 | 2.3468 | 2.1572 | 0.18956 | 2.5178e-05 | 0
[13 empty] | 17:46 | 0.93058 | 0.91146 | 0 |  | 17:46 | 0 | 0 | 5507.423 | 17:46 | 2.3474 | 2.1578 | 0.1896 | 2.5183e-05 | 0
[13 empty] | 17:46 | 0.9193 | 0.91146 | 0 |  | 17:46 | 0 | 0 | 5507.423 | 17:46 | 2.348 | 2.1583 | 0.18965 | 2.5189e-05 | 0
[13 empty] | 17:46 | 0.90825 | 0.91146 | 0 |  | 17:46 | 0 | 0 | 5507.423 | 17:46 | 2.3484 | 2.1587 | 0.18969 | 2.5195e-05 | 0
[13 empty] | 17:46 | 0.89743 | 0.91146 | 0 |  | 17:46 | 0 | 0 | 5507.423 | 17:46 | 2.349 | 2.1593 | 0.18974 | 2.5201e-05 | 0
[13 empty] | 17:46 | 0.88683 | 0.91146 | 0 |  | 17:46 | 0 | 0 | 5507.423 | 17:46 | 2.3497 | 2.1599 | 0.18978 | 2.5206e-05 | 0
[13 empty] | 17:47 | 0.87645 | 0.91146 | 0 |  | 17:47 | 0 | 0 | 5507.423 | 17:47 | 2.3501 | 2.1602 | 0.18982 | 2.5212e-05 | 0
[13 empty] | 17:47 | 0.86628 | 0.91146 | 0 |  | 17:47 | 0 | 0 | 5507.423 | 17:47 | 2.3507 | 2.1608 | 0.18986 | 2.5218e-05 | 0
[13 empty] | 17:47 | 0.85633 | 0.91146 | 0 |  | 17:47 | 0 | 0 | 5507.423 | 17:47 | 2.3511 | 2.1612 | 0.18991 | 2.5224e-05 | 0
[13 empty] | 17:48 | 0.84657 | 0.91146 | 0 |  | 17:48 | 0 | 0 | 5507.423 | 17:48 | 2.3517 | 2.1618 | 0.18995 | 2.5229e-05 | 0
[13 empty] | 17:48 | 0.83702 | 0.91146 | 0 |  | 17:48 | 0 | 0 | 5507.423 | 17:48 | 2.3522 | 2.1622 | 0.18999 | 2.5235e-05 | 0
[13 empty] | 17:48 | 0.82766 | 0.91146 | 0 |  | 17:48 | 0 | 0 | 5507.423 | 17:48 | 2.3526 | 2.1625 | 0.19003 | 2.5241e-05 | 0
[13 empty] | 17:48 | 0.8185 | 0.91146 | 0 |  | 17:48 | 0 | 0 | 5507.423 | 17:48 | 2.3532 | 2.1631 | 0.19007 | 2.5246e-05 | 0
[13 empty] | 17:48 | 0.80952 | 0.91146 | 0 |  | 17:48 | 0 | 0 | 5507.423 | 17:48 | 2.3536 | 2.1635 | 0.19011 | 2.525e-05 | 0
[13 empty] | 17:49 | 0.80073 | 0.91146 | 0 |  | 17:49 | 0 | 0 | 5507.423 | 17:49 | 2.3542 | 2.1641 | 0.19015 | 2.5256e-05 | 0
[13 empty] | 17:49 | 0.79211 | 0.91146 | 0 |  | 17:49 | 0 | 0 | 5507.423 | 17:49 | 2.3547 | 2.1644 | 0.19019 | 2.5262e-05 | 0
[13 empty] | 17:49 | 0.78368 | 0.91146 | 0 |  | 17:49 | 0 | 0 | 5507.423 | 17:49 | 2.3551 | 2.1648 | 0.19023 | 2.5266e-05 | 0
[13 empty] | 17:50 | 0.77542 | 0.91146 | 0 |  | 17:50 | 0 | 0 | 5507.423 | 17:50 | 2.3555 | 2.1652 | 0.19026 | 2.5271e-05 | 0
[13 empty] | 17:50 | 0.76733 | 0.91146 | 0 |  | 17:50 | 0 | 0 | 5507.423 | 17:50 | 2.3561 | 2.1658 | 0.1903 | 2.5277e-05 | 0
[13 empty] | 17:50 | 0.7594 | 0.91146 | 0 |  | 17:50 | 0 | 0 | 5507.423 | 17:50 | 2.3565 | 2.1662 | 0.19034 | 2.5281e-05 | 0
[13 empty] | 17:50 | 0.75164 | 0.91146 | 0 |  | 17:50 | 0 | 0 | 5507.423 | 17:50 | 2.3569 | 2.1665 | 0.19037 | 2.5287e-05 | 0
[13 empty] | 17:50 | 0.74403 | 0.91146 | 0 |  | 17:50 | 0 | 0 | 5507.423 | 17:50 | 2.3574 | 2.1669 | 0.19041 | 2.529e-05 | 0
[13 empty] | 17:51 | 0.73658 | 0.91146 | 0 |  | 17:51 | 0 | 0 | 5507.423 | 17:51 | 2.3578 | 2.1673 | 0.19045 | 2.5296e-05 | 0
[13 empty] | 17:51 | 0.72929 | 0.91146 | 0 |  | 17:51 | 0 | 0 | 5507.423 | 17:51 | 2.3582 | 2.1677 | 0.19048 | 2.53e-05 | 0
[13 empty] | 17:51 | 1.1629 | 0.91146 | 0 |  | 17:51 | 0 | 0 | 5507.423 | 17:51 | 2.359 | 2.1685 | 0.19054 | 2.5308e-05 | 0
[13 empty] | 17:52 | 1.1468 | 0.91146 | 0 |  | 17:52 | 0 | 0 | 5507.423 | 17:52 | 2.3596 | 2.169 | 0.1906 | 2.5315e-05 | 0
[13 empty] | 17:52 | 1.1311 | 0.91146 | 0 |  | 17:52 | 0 | 0 | 5507.423 | 17:52 | 2.3603 | 2.1696 | 0.19065 | 2.5323e-05 | 0
[13 empty] | 17:52 | 1.1157 | 0.91146 | 0 |  | 17:52 | 0 | 0 | 5507.423 | 17:52 | 2.3611 | 2.1704 | 0.19071 | 2.533e-05 | 0
[13 empty] | 17:52 | 1.1006 | 0.91146 | 0 |  | 17:52 | 0 | 0 | 5507.423 | 17:52 | 2.3617 | 2.1709 | 0.19076 | 2.5338e-05 | 0
[13 empty] | 17:52 | 1.0859 | 0.91146 | 0 |  | 17:52 | 0 | 0 | 5507.423 | 17:52 | 2.3623 | 2.1715 | 0.19081 | 2.5344e-05 | 0
[13 empty] | 17:53 | 1.0714 | 0.91146 | 0 |  | 17:53 | 0 | 0 | 5507.423 | 17:53 | 2.363 | 2.1721 | 0.19087 | 2.5351e-05 | 0
[13 empty] | 17:53 | 1.0572 | 0.91146 | 0 |  | 17:53 | 0 | 0 | 5507.423 | 17:53 | 2.3636 | 2.1727 | 0.19092 | 2.5357e-05 | 0
[13 empty] | 17:53 | 1.0434 | 0.91146 | 0 |  | 17:53 | 0 | 0 | 5507.423 | 17:53 | 2.3642 | 2.1732 | 0.19097 | 2.5365e-05 | 0
[13 empty] | 17:54 | 1.0298 | 0.91146 | 0 |  | 17:54 | 0 | 0 | 5507.423 | 17:54 | 2.3649 | 2.1738 | 0.19102 | 2.5371e-05 | 0
[13 empty] | 17:54 | 1.0164 | 0.91146 | 0 |  | 17:54 | 0 | 0 | 5507.423 | 17:54 | 2.3655 | 2.1744 | 0.19106 | 2.5378e-05 | 0
[13 empty] | 17:54 | 1.0034 | 0.91146 | 0 |  | 17:54 | 0 | 0 | 5507.423 | 17:54 | 2.3661 | 2.1749 | 0.19112 | 2.5384e-05 | 0
[13 empty] | 17:54 | 0.99062 | 0.91146 | 0 |  | 17:54 | 0 | 0 | 5507.423 | 17:54 | 2.3667 | 2.1755 | 0.19116 | 2.5392e-05 | 0
[13 empty] | 17:54 | 0.97811 | 0.91146 | 0 |  | 17:54 | 0 | 0 | 5507.423 | 17:54 | 2.3673 | 2.1761 | 0.19122 | 2.5397e-05 | 0
[13 empty] | 17:55 | 0.96585 | 0.91146 | 0 |  | 17:55 | 0 | 0 | 5507.423 | 17:55 | 2.3679 | 2.1767 | 0.19125 | 2.5403e-05 | 0
[13 empty] | 17:55 | 0.95385 | 0.91146 | 0 |  | 17:55 | 0 | 0 | 5507.423 | 17:55 | 2.3686 | 2.1772 | 0.19131 | 2.5411e-05 | 0
[13 empty] | 17:55 | 0.94209 | 0.91146 | 0 |  | 17:55 | 0 | 0 | 5507.423 | 17:55 | 2.369 | 2.1776 | 0.19135 | 2.5416e-05 | 0
[13 empty] | 17:56 | 0.93058 | 0.91146 | 0 |  | 17:56 | 0 | 0 | 5507.423 | 17:56 | 2.3696 | 2.1782 | 0.19141 | 2.5422e-05 | 0
[13 empty] | 17:56 | 0.9193 | 0.91146 | 0 |  | 17:56 | 0 | 0 | 5507.423 | 17:56 | 2.3702 | 2.1788 | 0.19144 | 2.5428e-05 | 0
[13 empty] | 17:56 | 0.90825 | 0.91146 | 0 |  | 17:56 | 0 | 0 | 5507.423 | 17:56 | 2.3707 | 2.1791 | 0.19148 | 2.5434e-05 | 0
[13 empty] | 17:56 | 0.89743 | 0.91146 | 0 |  | 17:56 | 0 | 0 | 5507.423 | 17:56 | 2.3713 | 2.1797 | 0.19154 | 2.5439e-05 | 0
[13 empty] | 17:56 | 0.88683 | 0.91146 | 0 |  | 17:56 | 0 | 0 | 5507.423 | 17:56 | 2.3719 | 2.1803 | 0.19158 | 2.5445e-05 | 0
[13 empty] | 17:57 | 0.87645 | 0.91146 | 0 |  | 17:57 | 0 | 0 | 5507.423 | 17:57 | 2.3723 | 2.1807 | 0.19162 | 2.5451e-05 | 0
[13 empty] | 17:57 | 0.86628 | 0.91146 | 0 |  | 17:57 | 0 | 0 | 5507.423 | 17:57 | 2.3729 | 2.1813 | 0.19165 | 2.5457e-05 | 0
[13 empty] | 17:57 | 0.85633 | 0.91146 | 0 |  | 17:57 | 0 | 0 | 5507.423 | 17:57 | 2.3734 | 2.1816 | 0.19171 | 2.5462e-05 | 0
[13 empty] | 17:58 | 0.84657 | 0.91146 | 0 |  | 17:58 | 0 | 0 | 5507.423 | 17:58 | 2.374 | 2.1822 | 0.19175 | 2.5468e-05 | 0
[13 empty] | 17:58 | 0.83702 | 0.91146 | 0 |  | 17:58 | 0 | 0 | 5507.423 | 17:58 | 2.3744 | 2.1826 | 0.19179 | 2.5474e-05 | 0
[13 empty] | 17:58 | 0.82766 | 0.91146 | 0 |  | 17:58 | 0 | 0 | 5507.423 | 17:58 | 2.3748 | 2.183 | 0.19183 | 2.5479e-05 | 0
[13 empty] | 17:58 | 0.8185 | 0.91146 | 0 |  | 17:58 | 0 | 0 | 5507.423 | 17:58 | 2.3754 | 2.1835 | 0.19186 | 2.5483e-05 | 0
[13 empty] | 17:58 | 0.80952 | 0.91146 | 0 |  | 17:58 | 0 | 0 | 5507.423 | 17:58 | 2.3759 | 2.1839 | 0.1919 | 2.5489e-05 | 0
[13 empty] | 17:59 | 0.80073 | 0.91146 | 0 |  | 17:59 | 0 | 0 | 5507.423 | 17:59 | 2.3763 | 2.1843 | 0.19194 | 2.5495e-05 | 0
[13 empty] | 17:59 | 0.79211 | 0.91146 | 0 |  | 17:59 | 0 | 0 | 5507.423 | 17:59 | 2.3769 | 2.1849 | 0.19198 | 2.55e-05 | 0
[13 empty] | 17:59 | 0.78368 | 0.91146 | 0 |  | 17:59 | 0 | 0 | 5507.423 | 17:59 | 2.3773 | 2.1853 | 0.19202 | 2.5504e-05 | 0
[13 empty] | 18:00 | 0.77542 | 0.91146 | 0 |  | 18:00 | 0 | 0 | 5507.423 | 18:00 | 2.3777 | 2.1856 | 0.19206 | 2.551e-05 | 0
[13 empty] | 18:00 | 0.76733 | 0.91146 | 0 |  | 18:00 | 0 | 0 | 5507.423 | 18:00 | 2.3783 | 2.1862 | 0.19209 | 2.5514e-05 | 0
[13 empty] | 18:00 | 0.7594 | 0.91146 | 0 |  | 18:00 | 0 | 0 | 5507.423 | 18:00 | 2.3788 | 2.1866 | 0.19213 | 2.552e-05 | 0
[13 empty] | 18:00 | 0.75164 | 0.91146 | 0 |  | 18:00 | 0 | 0 | 5507.423 | 18:00 | 2.3792 | 2.187 | 0.19217 | 2.5525e-05 | 0
[13 empty] | 18:00 | 0.74403 | 0.91146 | 0 |  | 18:00 | 0 | 0 | 5507.423 | 18:00 | 2.3796 | 2.1874 | 0.19221 | 2.5529e-05 | 0
[13 empty] | 18:01 | 0.73658 | 0.91146 | 0 |  | 18:01 | 0 | 0 | 5507.423 | 18:01 | 2.38 | 2.1877 | 0.19225 | 2.5535e-05 | 0
[13 empty] | 18:01 | 0.72929 | 0.91146 | 0 |  | 18:01 | 0 | 0 | 5507.423 | 18:01 | 2.3804 | 2.1881 | 0.19228 | 2.5539e-05 | 0
[13 empty] | 18:01 | 1.1629 | 0.91146 | 0 |  | 18:01 | 0 | 0 | 5507.423 | 18:01 | 2.3813 | 2.1889 | 0.19234 | 2.5546e-05 | 0
[13 empty] | 18:02 | 1.1468 | 0.91146 | 0 |  | 18:02 | 0 | 0 | 5507.423 | 18:02 | 2.3819 | 2.1895 | 0.1924 | 2.5554e-05 | 0
[13 empty] | 18:02 | 1.1311 | 0.91146 | 0 |  | 18:02 | 0 | 0 | 5507.423 | 18:02 | 2.3825 | 2.19 | 0.19246 | 2.5562e-05 | 0
[13 empty] | 18:02 | 1.1157 | 0.91146 | 0 |  | 18:02 | 0 | 0 | 5507.423 | 18:02 | 2.3833 | 2.1908 | 0.19249 | 2.5569e-05 | 0
[13 empty] | 18:02 | 1.1006 | 0.91146 | 0 |  | 18:02 | 0 | 0 | 5507.423 | 18:02 | 2.384 | 2.1914 | 0.19255 | 2.5575e-05 | 0
[13 empty] | 18:02 | 1.0859 | 0.91146 | 0 |  | 18:02 | 0 | 0 | 5507.423 | 18:02 | 2.3846 | 2.1919 | 0.19261 | 2.5583e-05 | 0
[13 empty] | 18:03 | 1.0714 | 0.91146 | 0 |  | 18:03 | 0 | 0 | 5507.423 | 18:03 | 2.3852 | 2.1925 | 0.19267 | 2.559e-05 | 0
[13 empty] | 18:03 | 1.0572 | 0.91146 | 0 |  | 18:03 | 0 | 0 | 5507.423 | 18:03 | 2.3858 | 2.1931 | 0.1927 | 2.5596e-05 | 0
[13 empty] | 18:03 | 1.0434 | 0.91146 | 0 |  | 18:03 | 0 | 0 | 5507.423 | 18:03 | 2.3865 | 2.1937 | 0.19276 | 2.5604e-05 | 0
[13 empty] | 18:04 | 1.0298 | 0.91146 | 0 |  | 18:04 | 0 | 0 | 5507.423 | 18:04 | 2.3871 | 2.1942 | 0.19282 | 2.5609e-05 | 0
[13 empty] | 18:04 | 1.0164 | 0.91146 | 0 |  | 18:04 | 0 | 0 | 5507.423 | 18:04 | 2.3877 | 2.1948 | 0.19286 | 2.5617e-05 | 0
[13 empty] | 18:04 | 1.0034 | 0.91146 | 0 |  | 18:04 | 0 | 0 | 5507.423 | 18:04 | 2.3883 | 2.1954 | 0.19291 | 2.5623e-05 | 0
[13 empty] | 18:04 | 0.99062 | 0.91146 | 0 |  | 18:04 | 0 | 0 | 5507.423 | 18:04 | 2.3889 | 2.196 | 0.19295 | 2.563e-05 | 0
[13 empty] | 18:04 | 0.97811 | 0.91146 | 0 |  | 18:04 | 0 | 0 | 5507.423 | 18:04 | 2.3896 | 2.1965 | 0.19301 | 2.5636e-05 | 0
[13 empty] | 18:05 | 0.96585 | 0.91146 | 0 |  | 18:05 | 0 | 0 | 5507.423 | 18:05 | 2.3902 | 2.1971 | 0.19305 | 2.5642e-05 | 0
[13 empty] | 18:05 | 0.95385 | 0.91146 | 0 |  | 18:05 | 0 | 0 | 5507.423 | 18:05 | 2.3908 | 2.1977 | 0.19311 | 2.5648e-05 | 0
[13 empty] | 18:05 | 0.94209 | 0.91146 | 0 |  | 18:05 | 0 | 0 | 5507.423 | 18:05 | 2.3912 | 2.1981 | 0.19314 | 2.5655e-05 | 0
[13 empty] | 18:06 | 0.93058 | 0.91146 | 0 |  | 18:06 | 0 | 0 | 5507.423 | 18:06 | 2.3919 | 2.1986 | 0.1932 | 2.5661e-05 | 0
[13 empty] | 18:06 | 0.9193 | 0.91146 | 0 |  | 18:06 | 0 | 0 | 5507.423 | 18:06 | 2.3925 | 2.1992 | 0.19324 | 2.5667e-05 | 0
[13 empty] | 18:06 | 0.90825 | 0.91146 | 0 |  | 18:06 | 0 | 0 | 5507.423 | 18:06 | 2.3929 | 2.1996 | 0.19328 | 2.5672e-05 | 0
[13 empty] | 18:06 | 0.89743 | 0.91146 | 0 |  | 18:06 | 0 | 0 | 5507.423 | 18:06 | 2.3935 | 2.2002 | 0.19334 | 2.5678e-05 | 0
[13 empty] | 18:06 | 0.88683 | 0.91146 | 0 |  | 18:06 | 0 | 0 | 5507.423 | 18:06 | 2.3941 | 2.2007 | 0.19337 | 2.5684e-05 | 0
[13 empty] | 18:07 | 0.87645 | 0.91146 | 0 |  | 18:07 | 0 | 0 | 5507.423 | 18:07 | 2.3945 | 2.2011 | 0.19341 | 2.569e-05 | 0
[13 empty] | 18:07 | 0.86628 | 0.91146 | 0 |  | 18:07 | 0 | 0 | 5507.423 | 18:07 | 2.3952 | 2.2017 | 0.19345 | 2.5695e-05 | 0
[13 empty] | 18:07 | 0.85633 | 0.91146 | 0 |  | 18:07 | 0 | 0 | 5507.423 | 18:07 | 2.3956 | 2.2021 | 0.19351 | 2.5701e-05 | 0
[13 empty] | 18:08 | 0.84657 | 0.91146 | 0 |  | 18:08 | 0 | 0 | 5507.423 | 18:08 | 2.3962 | 2.2026 | 0.19355 | 2.5707e-05 | 0
[13 empty] | 18:08 | 0.83702 | 0.91146 | 0 |  | 18:08 | 0 | 0 | 5507.423 | 18:08 | 2.3966 | 2.203 | 0.19358 | 2.5712e-05 | 0
[13 empty] | 18:08 | 0.82766 | 0.91146 | 0 |  | 18:08 | 0 | 0 | 5507.423 | 18:08 | 2.3971 | 2.2034 | 0.19362 | 2.5716e-05 | 0
[13 empty] | 18:08 | 0.8185 | 0.91146 | 0 |  | 18:08 | 0 | 0 | 5507.423 | 18:08 | 2.3977 | 2.204 | 0.19366 | 2.5722e-05 | 0
[13 empty] | 18:08 | 0.80952 | 0.91146 | 0 |  | 18:08 | 0 | 0 | 5507.423 | 18:08 | 2.3981 | 2.2044 | 0.1937 | 2.5728e-05 | 0
[13 empty] | 18:09 | 0.80073 | 0.91146 | 0 |  | 18:09 | 0 | 0 | 5507.423 | 18:09 | 2.3985 | 2.2047 | 0.19374 | 2.5733e-05 | 0
[13 empty] | 18:09 | 0.79211 | 0.91146 | 0 |  | 18:09 | 0 | 0 | 5507.423 | 18:09 | 2.3991 | 2.2053 | 0.19377 | 2.5737e-05 | 0
[13 empty] | 18:09 | 0.78368 | 0.91146 | 0 |  | 18:09 | 0 | 0 | 5507.423 | 18:09 | 2.3995 | 2.2057 | 0.19381 | 2.5743e-05 | 0
[13 empty] | 18:10 | 0.77542 | 0.91146 | 0 |  | 18:10 | 0 | 0 | 5507.423 | 18:10 | 2.4 | 2.2061 | 0.19385 | 2.5749e-05 | 0
[13 empty] | 18:10 | 0.76733 | 0.91146 | 0 |  | 18:10 | 0 | 0 | 5507.423 | 18:10 | 2.4006 | 2.2067 | 0.19389 | 2.5753e-05 | 0
[13 empty] | 18:10 | 0.7594 | 0.91146 | 0 |  | 18:10 | 0 | 0 | 5507.423 | 18:10 | 2.401 | 2.207 | 0.19393 | 2.5758e-05 | 0
[13 empty] | 18:10 | 0.75164 | 0.91146 | 0 |  | 18:10 | 0 | 0 | 5507.423 | 18:10 | 2.4014 | 2.2074 | 0.19397 | 2.5762e-05 | 0
[13 empty] | 18:10 | 0.74403 | 0.91146 | 0 |  | 18:10 | 0 | 0 | 5507.423 | 18:10 | 2.4018 | 2.2078 | 0.194 | 2.5768e-05 | 0
[13 empty] | 18:11 | 0.73658 | 0.91146 | 0 |  | 18:11 | 0 | 0 | 5507.423 | 18:11 | 2.4022 | 2.2082 | 0.19404 | 2.5774e-05 | 0
[13 empty] | 18:11 | 0.72929 | 0.91146 | 0 |  | 18:11 | 0 | 0 | 5507.423 | 18:11 | 2.4027 | 2.2086 | 0.19408 | 2.5777e-05 | 0
[13 empty] | 18:11 | 1.1629 | 0.91146 | 0 |  | 18:11 | 0 | 0 | 5507.423 | 18:11 | 2.4035 | 2.2093 | 0.19414 | 2.5785e-05 | 0
[13 empty] | 18:12 | 1.1468 | 0.91146 | 0 |  | 18:12 | 0 | 0 | 5507.423 | 18:12 | 2.4041 | 2.2099 | 0.19419 | 2.5793e-05 | 0
[13 empty] | 18:12 | 1.1311 | 0.91146 | 0 |  | 18:12 | 0 | 0 | 5507.423 | 18:12 | 2.4047 | 2.2105 | 0.19425 | 2.58e-05 | 0
[13 empty] | 18:12 | 1.1157 | 0.91146 | 0 |  | 18:12 | 0 | 0 | 5507.423 | 18:12 | 2.4056 | 2.2112 | 0.19429 | 2.5806e-05 | 0
[13 empty] | 18:12 | 1.1006 | 0.91146 | 0 |  | 18:12 | 0 | 0 | 5507.423 | 18:12 | 2.4062 | 2.2118 | 0.19435 | 2.5814e-05 | 0
[13 empty] | 18:12 | 1.0859 | 0.91146 | 0 |  | 18:12 | 0 | 0 | 5507.423 | 18:12 | 2.4068 | 2.2124 | 0.1944 | 2.5821e-05 | 0
[13 empty] | 18:13 | 1.0714 | 0.91146 | 0 |  | 18:13 | 0 | 0 | 5507.423 | 18:13 | 2.4074 | 2.213 | 0.19446 | 2.5829e-05 | 0
[13 empty] | 18:13 | 1.0572 | 0.91146 | 0 |  | 18:13 | 0 | 0 | 5507.423 | 18:13 | 2.4081 | 2.2135 | 0.1945 | 2.5835e-05 | 0
[13 empty] | 18:13 | 1.0434 | 0.91146 | 0 |  | 18:13 | 0 | 0 | 5507.423 | 18:13 | 2.4087 | 2.2141 | 0.19456 | 2.5842e-05 | 0
[13 empty] | 18:14 | 1.0298 | 0.91146 | 0 |  | 18:14 | 0 | 0 | 5507.423 | 18:14 | 2.4093 | 2.2147 | 0.19461 | 2.5848e-05 | 0
[13 empty] | 18:14 | 1.0164 | 0.91146 | 0 |  | 18:14 | 0 | 0 | 5507.423 | 18:14 | 2.4099 | 2.2152 | 0.19465 | 2.5856e-05 | 0
[13 empty] | 18:14 | 1.0034 | 0.91146 | 0 |  | 18:14 | 0 | 0 | 5507.423 | 18:14 | 2.4106 | 2.2158 | 0.19471 | 2.5861e-05 | 0
[13 empty] | 18:14 | 0.99062 | 0.91146 | 0 |  | 18:14 | 0 | 0 | 5507.423 | 18:14 | 2.4112 | 2.2164 | 0.19475 | 2.5867e-05 | 0
[13 empty] | 18:14 | 0.97811 | 0.91146 | 0 |  | 18:14 | 0 | 0 | 5507.423 | 18:14 | 2.4118 | 2.217 | 0.19481 | 2.5875e-05 | 0
[13 empty] | 18:15 | 0.96585 | 0.91146 | 0 |  | 18:15 | 0 | 0 | 5507.423 | 18:15 | 2.4124 | 2.2175 | 0.19484 | 2.5881e-05 | 0
[13 empty] | 18:15 | 0.95385 | 0.91146 | 0 |  | 18:15 | 0 | 0 | 5507.423 | 18:15 | 2.413 | 2.2181 | 0.1949 | 2.5886e-05 | 0
[13 empty] | 18:15 | 0.94209 | 0.91146 | 0 |  | 18:15 | 0 | 0 | 5507.423 | 18:15 | 2.4135 | 2.2185 | 0.19494 | 2.5894e-05 | 0
[13 empty] | 18:16 | 0.93058 | 0.91146 | 0 |  | 18:16 | 0 | 0 | 5507.423 | 18:16 | 2.4141 | 2.2191 | 0.195 | 2.59e-05 | 0
[13 empty] | 18:16 | 0.9193 | 0.91146 | 0 |  | 18:16 | 0 | 0 | 5507.423 | 18:16 | 2.4147 | 2.2196 | 0.19503 | 2.5905e-05 | 0
[13 empty] | 18:16 | 0.90825 | 0.91146 | 0 |  | 18:16 | 0 | 0 | 5507.423 | 18:16 | 2.4151 | 2.22 | 0.19507 | 2.5911e-05 | 0
[13 empty] | 18:16 | 0.89743 | 0.91146 | 0 |  | 18:16 | 0 | 0 | 5507.423 | 18:16 | 2.4157 | 2.2206 | 0.19513 | 2.5917e-05 | 0
[13 empty] | 18:16 | 0.88683 | 0.91146 | 0 |  | 18:16 | 0 | 0 | 5507.423 | 18:16 | 2.4162 | 2.221 | 0.19517 | 2.5923e-05 | 0
[13 empty] | 18:17 | 0.87645 | 0.91146 | 0 |  | 18:17 | 0 | 0 | 5507.423 | 18:17 | 2.4168 | 2.2215 | 0.19521 | 2.5928e-05 | 0
[13 empty] | 18:17 | 0.86628 | 0.91146 | 0 |  | 18:17 | 0 | 0 | 5507.423 | 18:17 | 2.4174 | 2.2221 | 0.19524 | 2.5934e-05 | 0
[13 empty] | 18:17 | 0.85633 | 0.91146 | 0 |  | 18:17 | 0 | 0 | 5507.423 | 18:17 | 2.4178 | 2.2225 | 0.1953 | 2.594e-05 | 0
[13 empty] | 18:18 | 0.84657 | 0.91146 | 0 |  | 18:18 | 0 | 0 | 5507.423 | 18:18 | 2.4184 | 2.2231 | 0.19534 | 2.5945e-05 | 0
[13 empty] | 18:18 | 0.83702 | 0.91146 | 0 |  | 18:18 | 0 | 0 | 5507.423 | 18:18 | 2.4189 | 2.2235 | 0.19538 | 2.5951e-05 | 0
[13 empty] | 18:18 | 0.82766 | 0.91146 | 0 |  | 18:18 | 0 | 0 | 5507.423 | 18:18 | 2.4193 | 2.2238 | 0.19542 | 2.5955e-05 | 0
[13 empty] | 18:18 | 0.8185 | 0.91146 | 0 |  | 18:18 | 0 | 0 | 5507.423 | 18:18 | 2.4199 | 2.2244 | 0.19545 | 2.5961e-05 | 0
[13 empty] | 18:18 | 0.80952 | 0.91146 | 0 |  | 18:18 | 0 | 0 | 5507.423 | 18:18 | 2.4203 | 2.2248 | 0.19549 | 2.5966e-05 | 0
[13 empty] | 18:19 | 0.80073 | 0.91146 | 0 |  | 18:19 | 0 | 0 | 5507.423 | 18:19 | 2.4207 | 2.2252 | 0.19553 | 2.5972e-05 | 0
[13 empty] | 18:19 | 0.79211 | 0.91146 | 0 |  | 18:19 | 0 | 0 | 5507.423 | 18:19 | 2.4213 | 2.2258 | 0.19557 | 2.5976e-05 | 0
[13 empty] | 18:19 | 0.78368 | 0.91146 | 0 |  | 18:19 | 0 | 0 | 5507.423 | 18:19 | 2.4218 | 2.2261 | 0.19561 | 2.5982e-05 | 0
[13 empty] | 18:20 | 0.77542 | 0.91146 | 0 |  | 18:20 | 0 | 0 | 5507.423 | 18:20 | 2.4222 | 2.2265 | 0.19565 | 2.5987e-05 | 0
[13 empty] | 18:20 | 0.76733 | 0.91146 | 0 |  | 18:20 | 0 | 0 | 5507.423 | 18:20 | 2.4228 | 2.2271 | 0.19568 | 2.5991e-05 | 0
[13 empty] | 18:20 | 0.7594 | 0.91146 | 0 |  | 18:20 | 0 | 0 | 5507.423 | 18:20 | 2.4232 | 2.2275 | 0.19572 | 2.5997e-05 | 0
[13 empty] | 18:20 | 0.75164 | 0.91146 | 0 |  | 18:20 | 0 | 0 | 5507.423 | 18:20 | 2.4236 | 2.2279 | 0.19576 | 2.6001e-05 | 0
[13 empty] | 18:20 | 0.74403 | 0.91146 | 0 |  | 18:20 | 0 | 0 | 5507.423 | 18:20 | 2.4241 | 2.2282 | 0.1958 | 2.6007e-05 | 0
[13 empty] | 18:21 | 0.73658 | 0.91146 | 0 |  | 18:21 | 0 | 0 | 5507.423 | 18:21 | 2.4245 | 2.2286 | 0.19584 | 2.601e-05 | 0
[13 empty] | 18:21 | 0.72929 | 0.91146 | 0 |  | 18:21 | 0 | 0 | 5507.423 | 18:21 | 2.4249 | 2.229 | 0.19588 | 2.6016e-05 | 0
[13 empty] | 18:21 | 1.1629 | 0.91146 | 0 |  | 18:21 | 0 | 0 | 5507.423 | 18:21 | 2.4257 | 2.2298 | 0.19593 | 2.6024e-05 | 0
[13 empty] | 18:22 | 1.1468 | 0.91146 | 0 |  | 18:22 | 0 | 0 | 5507.423 | 18:22 | 2.4263 | 2.2303 | 0.19599 | 2.6031e-05 | 0
[13 empty] | 18:22 | 1.1311 | 0.91146 | 0 |  | 18:22 | 0 | 0 | 5507.423 | 18:22 | 2.427 | 2.2309 | 0.19605 | 2.6039e-05 | 0
[13 empty] | 18:22 | 1.1157 | 0.91146 | 0 |  | 18:22 | 0 | 0 | 5507.423 | 18:22 | 2.4278 | 2.2317 | 0.19609 | 2.6045e-05 | 0
[13 empty] | 18:22 | 1.1006 | 0.91146 | 0 |  | 18:22 | 0 | 0 | 5507.423 | 18:22 | 2.4284 | 2.2322 | 0.19614 | 2.6052e-05 | 0
[13 empty] | 18:22 | 1.0859 | 0.91146 | 0 |  | 18:22 | 0 | 0 | 5507.423 | 18:22 | 2.429 | 2.2328 | 0.1962 | 2.606e-05 | 0
[13 empty] | 18:23 | 1.0714 | 0.91146 | 0 |  | 18:23 | 0 | 0 | 5507.423 | 18:23 | 2.4297 | 2.2334 | 0.19626 | 2.6066e-05 | 0
[13 empty] | 18:23 | 1.0572 | 0.91146 | 0 |  | 18:23 | 0 | 0 | 5507.423 | 18:23 | 2.4303 | 2.234 | 0.1963 | 2.6073e-05 | 0
[13 empty] | 18:23 | 1.0434 | 0.91146 | 0 |  | 18:23 | 0 | 0 | 5507.423 | 18:23 | 2.4309 | 2.2345 | 0.19635 | 2.6081e-05 | 0
[13 empty] | 18:24 | 1.0298 | 0.91146 | 0 |  | 18:24 | 0 | 0 | 5507.423 | 18:24 | 2.4315 | 2.2351 | 0.19641 | 2.6087e-05 | 0
[13 empty] | 18:24 | 1.0164 | 0.91146 | 0 |  | 18:24 | 0 | 0 | 5507.423 | 18:24 | 2.4322 | 2.2357 | 0.19645 | 2.6094e-05 | 0
[13 empty] | 18:24 | 1.0034 | 0.91146 | 0 |  | 18:24 | 0 | 0 | 5507.423 | 18:24 | 2.4328 | 2.2363 | 0.19651 | 2.61e-05 | 0
[13 empty] | 18:24 | 0.99062 | 0.91146 | 0 |  | 18:24 | 0 | 0 | 5507.423 | 18:24 | 2.4334 | 2.2368 | 0.19654 | 2.6106e-05 | 0
[13 empty] | 18:25 | 0.97811 | 0.91146 | 0 |  | 18:25 | 0 | 0 | 5507.423 | 18:25 | 2.434 | 2.2374 | 0.1966 | 2.6114e-05 | 0
[13 empty] | 18:25 | 0.96585 | 0.91146 | 0 |  | 18:25 | 0 | 0 | 5507.423 | 18:25 | 2.4346 | 2.238 | 0.19664 | 2.6119e-05 | 0
[13 empty] | 18:25 | 0.95385 | 0.91146 | 0 |  | 18:25 | 0 | 0 | 5507.423 | 18:25 | 2.4351 | 2.2384 | 0.1967 | 2.6125e-05 | 0
[13 empty] | 18:25 | 0.94209 | 0.91146 | 0 |  | 18:25 | 0 | 0 | 5507.423 | 18:25 | 2.4357 | 2.2389 | 0.19673 | 2.6131e-05 | 0
[13 empty] | 18:26 | 0.93058 | 0.91146 | 0 |  | 18:26 | 0 | 0 | 5507.423 | 18:26 | 2.4363 | 2.2395 | 0.19679 | 2.6138e-05 | 0
[13 empty] | 18:26 | 0.9193 | 0.91146 | 0 |  | 18:26 | 0 | 0 | 5507.423 | 18:26 | 2.4369 | 2.2401 | 0.19683 | 2.6144e-05 | 0
[13 empty] | 18:26 | 0.90825 | 0.91146 | 0 |  | 18:26 | 0 | 0 | 5507.423 | 18:26 | 2.4374 | 2.2405 | 0.19687 | 2.615e-05 | 0
[13 empty] | 18:26 | 0.89743 | 0.91146 | 0 |  | 18:26 | 0 | 0 | 5507.423 | 18:26 | 2.438 | 2.241 | 0.19693 | 2.6156e-05 | 0
[13 empty] | 18:26 | 0.88683 | 0.91146 | 0 |  | 18:26 | 0 | 0 | 5507.423 | 18:26 | 2.4384 | 2.2414 | 0.19696 | 2.6161e-05 | 0
[13 empty] | 18:27 | 0.87645 | 0.91146 | 0 |  | 18:27 | 0 | 0 | 5507.423 | 18:27 | 2.439 | 2.242 | 0.197 | 2.6167e-05 | 0
[13 empty] | 18:27 | 0.86628 | 0.91146 | 0 |  | 18:27 | 0 | 0 | 5507.423 | 18:27 | 2.4396 | 2.2426 | 0.19704 | 2.6173e-05 | 0
[13 empty] | 18:27 | 0.85633 | 0.91146 | 0 |  | 18:27 | 0 | 0 | 5507.423 | 18:27 | 2.4401 | 2.2429 | 0.1971 | 2.6178e-05 | 0
[13 empty] | 18:28 | 0.84657 | 0.91146 | 0 |  | 18:28 | 0 | 0 | 5507.423 | 18:28 | 2.4407 | 2.2435 | 0.19714 | 2.6184e-05 | 0
[13 empty] | 18:28 | 0.83702 | 0.91146 | 0 |  | 18:28 | 0 | 0 | 5507.423 | 18:28 | 2.4411 | 2.2439 | 0.19717 | 2.6188e-05 | 0
[13 empty] | 18:28 | 0.82766 | 0.91146 | 0 |  | 18:28 | 0 | 0 | 5507.423 | 18:28 | 2.4415 | 2.2443 | 0.19721 | 2.6194e-05 | 0
[13 empty] | 18:28 | 0.8185 | 0.91146 | 0 |  | 18:28 | 0 | 0 | 5507.423 | 18:28 | 2.4421 | 2.2448 | 0.19725 | 2.6199e-05 | 0
[13 empty] | 18:29 | 0.80952 | 0.91146 | 0 |  | 18:29 | 0 | 0 | 5507.423 | 18:29 | 2.4425 | 2.2452 | 0.19729 | 2.6205e-05 | 0
[13 empty] | 18:29 | 0.80073 | 0.91146 | 0 |  | 18:29 | 0 | 0 | 5507.423 | 18:29 | 2.443 | 2.2456 | 0.19733 | 2.6209e-05 | 0
[13 empty] | 18:29 | 0.79211 | 0.91146 | 0 |  | 18:29 | 0 | 0 | 5507.423 | 18:29 | 2.4436 | 2.2462 | 0.19736 | 2.6215e-05 | 0
[13 empty] | 18:29 | 0.78368 | 0.91146 | 0 |  | 18:29 | 0 | 0 | 5507.423 | 18:29 | 2.444 | 2.2466 | 0.1974 | 2.622e-05 | 0
[13 empty] | 18:30 | 0.77542 | 0.91146 | 0 |  | 18:30 | 0 | 0 | 5507.423 | 18:30 | 2.4444 | 2.2469 | 0.19744 | 2.6224e-05 | 0
[13 empty] | 18:30 | 0.76733 | 0.91146 | 0 |  | 18:30 | 0 | 0 | 5507.423 | 18:30 | 2.445 | 2.2475 | 0.19748 | 2.623e-05 | 0
[13 empty] | 18:30 | 0.7594 | 0.91146 | 0 |  | 18:30 | 0 | 0 | 5507.423 | 18:30 | 2.4454 | 2.2479 | 0.19752 | 2.6236e-05 | 0
[13 empty] | 18:30 | 0.75164 | 0.91146 | 0 |  | 18:30 | 0 | 0 | 5507.423 | 18:30 | 2.4459 | 2.2483 | 0.19756 | 2.624e-05 | 0
[13 empty] | 18:30 | 0.74403 | 0.91146 | 0 |  | 18:30 | 0 | 0 | 5507.423 | 18:30 | 2.4463 | 2.2487 | 0.19759 | 2.6245e-05 | 0
[13 empty] | 18:31 | 0.73658 | 0.91146 | 0 |  | 18:31 | 0 | 0 | 5507.423 | 18:31 | 2.4467 | 2.2491 | 0.19763 | 2.6249e-05 | 0
[13 empty] | 18:31 | 0.72929 | 0.91146 | 0 |  | 18:31 | 0 | 0 | 5507.423 | 18:31 | 2.4471 | 2.2494 | 0.19767 | 2.6255e-05 | 0
[13 empty] | 18:31 | 1.1629 | 0.91146 | 0 |  | 18:31 | 0 | 0 | 5507.423 | 18:31 | 2.448 | 2.2502 | 0.19773 | 2.6262e-05 | 0
[13 empty] | 18:32 | 1.1468 | 0.91146 | 0 |  | 18:32 | 0 | 0 | 5507.423 | 18:32 | 2.4486 | 2.2508 | 0.19779 | 2.627e-05 | 0
[13 empty] | 18:32 | 1.1311 | 0.91146 | 0 |  | 18:32 | 0 | 0 | 5507.423 | 18:32 | 2.4492 | 2.2513 | 0.19784 | 2.6276e-05 | 0
[13 empty] | 18:32 | 1.1157 | 0.91146 | 0 |  | 18:32 | 0 | 0 | 5507.423 | 18:32 | 2.45 | 2.2521 | 0.19788 | 2.6283e-05 | 0
[13 empty] | 18:32 | 1.1006 | 0.91146 | 0 |  | 18:32 | 0 | 0 | 5507.423 | 18:32 | 2.4506 | 2.2527 | 0.19794 | 2.6291e-05 | 0
[13 empty] | 18:33 | 1.0859 | 0.91146 | 0 |  | 18:33 | 0 | 0 | 5507.423 | 18:33 | 2.4513 | 2.2533 | 0.198 | 2.6299e-05 | 0
[13 empty] | 18:33 | 1.0714 | 0.91146 | 0 |  | 18:33 | 0 | 0 | 5507.423 | 18:33 | 2.4519 | 2.2538 | 0.19805 | 2.6304e-05 | 0
[13 empty] | 18:33 | 1.0572 | 0.91146 | 0 |  | 18:33 | 0 | 0 | 5507.423 | 18:33 | 2.4525 | 2.2544 | 0.19809 | 2.6312e-05 | 0
[13 empty] | 18:33 | 1.0434 | 0.91146 | 0 |  | 18:33 | 0 | 0 | 5507.423 | 18:33 | 2.4531 | 2.255 | 0.19815 | 2.6318e-05 | 0
[13 empty] | 18:34 | 1.0298 | 0.91146 | 0 |  | 18:34 | 0 | 0 | 5507.423 | 18:34 | 2.4538 | 2.2555 | 0.19821 | 2.6326e-05 | 0
[13 empty] | 18:34 | 1.0164 | 0.91146 | 0 |  | 18:34 | 0 | 0 | 5507.423 | 18:34 | 2.4544 | 2.2561 | 0.19824 | 2.6331e-05 | 0
[13 empty] | 18:34 | 1.0034 | 0.91146 | 0 |  | 18:34 | 0 | 0 | 5507.423 | 18:34 | 2.455 | 2.2567 | 0.1983 | 2.6339e-05 | 0
[13 empty] | 18:34 | 0.99062 | 0.91146 | 0 |  | 18:34 | 0 | 0 | 5507.423 | 18:34 | 2.4556 | 2.2573 | 0.19834 | 2.6345e-05 | 0
[13 empty] | 18:34 | 0.97811 | 0.91146 | 0 |  | 18:34 | 0 | 0 | 5507.423 | 18:34 | 2.4563 | 2.2578 | 0.1984 | 2.6352e-05 | 0
[13 empty] | 18:35 | 0.96585 | 0.91146 | 0 |  | 18:35 | 0 | 0 | 5507.423 | 18:35 | 2.4569 | 2.2584 | 0.19843 | 2.6358e-05 | 0
[13 empty] | 18:35 | 0.95385 | 0.91146 | 0 |  | 18:35 | 0 | 0 | 5507.423 | 18:35 | 2.4573 | 2.2588 | 0.19849 | 2.6364e-05 | 0
[13 empty] | 18:35 | 0.94209 | 0.91146 | 0 |  | 18:35 | 0 | 0 | 5507.423 | 18:35 | 2.4579 | 2.2594 | 0.19853 | 2.6369e-05 | 0
[13 empty] | 18:36 | 0.93058 | 0.91146 | 0 |  | 18:36 | 0 | 0 | 5507.423 | 18:36 | 2.4586 | 2.2599 | 0.19859 | 2.6375e-05 | 0
[13 empty] | 18:36 | 0.9193 | 0.91146 | 0 |  | 18:36 | 0 | 0 | 5507.423 | 18:36 | 2.4592 | 2.2605 | 0.19863 | 2.6383e-05 | 0
[13 empty] | 18:36 | 0.90825 | 0.91146 | 0 |  | 18:36 | 0 | 0 | 5507.423 | 18:36 | 2.4596 | 2.2609 | 0.19866 | 2.6389e-05 | 0
[13 empty] | 18:36 | 0.89743 | 0.91146 | 0 |  | 18:36 | 0 | 0 | 5507.423 | 18:36 | 2.4602 | 2.2615 | 0.19872 | 2.6394e-05 | 0
[13 empty] | 18:36 | 0.88683 | 0.91146 | 0 |  | 18:36 | 0 | 0 | 5507.423 | 18:36 | 2.4606 | 2.2618 | 0.19876 | 2.64e-05 | 0
[13 empty] | 18:37 | 0.87645 | 0.91146 | 0 |  | 18:37 | 0 | 0 | 5507.423 | 18:37 | 2.4612 | 2.2624 | 0.1988 | 2.6406e-05 | 0
[13 empty] | 18:37 | 0.86628 | 0.91146 | 0 |  | 18:37 | 0 | 0 | 5507.423 | 18:37 | 2.4619 | 2.263 | 0.19884 | 2.6411e-05 | 0
[13 empty] | 18:37 | 0.85633 | 0.91146 | 0 |  | 18:37 | 0 | 0 | 5507.423 | 18:37 | 2.4623 | 2.2634 | 0.19889 | 2.6417e-05 | 0
[13 empty] | 18:38 | 0.84657 | 0.91146 | 0 |  | 18:38 | 0 | 0 | 5507.423 | 18:38 | 2.4629 | 2.2639 | 0.19893 | 2.6421e-05 | 0
[13 empty] | 18:38 | 0.83702 | 0.91146 | 0 |  | 18:38 | 0 | 0 | 5507.423 | 18:38 | 2.4633 | 2.2643 | 0.19897 | 2.6427e-05 | 0
[13 empty] | 18:38 | 0.82766 | 0.91146 | 0 |  | 18:38 | 0 | 0 | 5507.423 | 18:38 | 2.4637 | 2.2647 | 0.19901 | 2.6432e-05 | 0
[13 empty] | 18:38 | 0.8185 | 0.91146 | 0 |  | 18:38 | 0 | 0 | 5507.423 | 18:38 | 2.4644 | 2.2653 | 0.19905 | 2.6438e-05 | 0
[13 empty] | 18:38 | 0.80952 | 0.91146 | 0 |  | 18:38 | 0 | 0 | 5507.423 | 18:38 | 2.4648 | 2.2657 | 0.19908 | 2.6444e-05 | 0
[13 empty] | 18:39 | 0.80073 | 0.91146 | 0 |  | 18:39 | 0 | 0 | 5507.423 | 18:39 | 2.4652 | 2.266 | 0.19912 | 2.6448e-05 | 0
[13 empty] | 18:39 | 0.79211 | 0.91146 | 0 |  | 18:39 | 0 | 0 | 5507.423 | 18:39 | 2.4658 | 2.2666 | 0.19916 | 2.6453e-05 | 0
[13 empty] | 18:39 | 0.78368 | 0.91146 | 0 |  | 18:39 | 0 | 0 | 5507.423 | 18:39 | 2.4662 | 2.267 | 0.1992 | 2.6459e-05 | 0
[13 empty] | 18:40 | 0.77542 | 0.91146 | 0 |  | 18:40 | 0 | 0 | 5507.423 | 18:40 | 2.4666 | 2.2674 | 0.19924 | 2.6463e-05 | 0
[13 empty] | 18:40 | 0.76733 | 0.91146 | 0 |  | 18:40 | 0 | 0 | 5507.423 | 18:40 | 2.4673 | 2.268 | 0.19927 | 2.6469e-05 | 0
[13 empty] | 18:40 | 0.7594 | 0.91146 | 0 |  | 18:40 | 0 | 0 | 5507.423 | 18:40 | 2.4677 | 2.2683 | 0.19931 | 2.6474e-05 | 0
[13 empty] | 18:40 | 0.75164 | 0.91146 | 0 |  | 18:40 | 0 | 0 | 5507.423 | 18:40 | 2.4681 | 2.2687 | 0.19935 | 2.6478e-05 | 0
[13 empty] | 18:40 | 0.74403 | 0.91146 | 0 |  | 18:40 | 0 | 0 | 5507.423 | 18:40 | 2.4685 | 2.2691 | 0.19939 | 2.6484e-05 | 0
[13 empty] | 18:41 | 0.73658 | 0.91146 | 0 |  | 18:41 | 0 | 0 | 5507.423 | 18:41 | 2.4689 | 2.2695 | 0.19943 | 2.6488e-05 | 0
[13 empty] | 18:41 | 0.72929 | 0.91146 | 0 |  | 18:41 | 0 | 0 | 5507.423 | 18:41 | 2.4694 | 2.2699 | 0.19947 | 2.6494e-05 | 0
[13 empty] | 18:41 | 1.1629 | 0.91146 | 0 |  | 18:41 | 0 | 0 | 5507.423 | 18:41 | 2.4702 | 2.2706 | 0.19952 | 2.6501e-05 | 0
[13 empty] | 18:42 | 1.1468 | 0.91146 | 0 |  | 18:42 | 0 | 0 | 5507.423 | 18:42 | 2.4708 | 2.2712 | 0.19958 | 2.6507e-05 | 0
[13 empty] | 18:42 | 1.1311 | 0.91146 | 0 |  | 18:42 | 0 | 0 | 5507.423 | 18:42 | 2.4714 | 2.2718 | 0.19964 | 2.6515e-05 | 0
[13 empty] | 18:42 | 1.1157 | 0.91146 | 0 |  | 18:42 | 0 | 0 | 5507.423 | 18:42 | 2.4722 | 2.2725 | 0.19968 | 2.6522e-05 | 0
[13 empty] | 18:42 | 1.1006 | 0.91146 | 0 |  | 18:42 | 0 | 0 | 5507.423 | 18:42 | 2.4729 | 2.2731 | 0.19973 | 2.653e-05 | 0
[13 empty] | 18:42 | 1.0859 | 0.91146 | 0 |  | 18:42 | 0 | 0 | 5507.423 | 18:42 | 2.4735 | 2.2737 | 0.19979 | 2.6537e-05 | 0
[13 empty] | 18:43 | 1.0714 | 0.91146 | 0 |  | 18:43 | 0 | 0 | 5507.423 | 18:43 | 2.4741 | 2.2743 | 0.19985 | 2.6543e-05 | 0
[13 empty] | 18:43 | 1.0572 | 0.91146 | 0 |  | 18:43 | 0 | 0 | 5507.423 | 18:43 | 2.4747 | 2.2748 | 0.19989 | 2.6551e-05 | 0
[13 empty] | 18:43 | 1.0434 | 0.91146 | 0 |  | 18:43 | 0 | 0 | 5507.423 | 18:43 | 2.4754 | 2.2754 | 0.19994 | 2.6557e-05 | 0
[13 empty] | 18:44 | 1.0298 | 0.91146 | 0 |  | 18:44 | 0 | 0 | 5507.423 | 18:44 | 2.476 | 2.276 | 0.2 | 2.6564e-05 | 0
[13 empty] | 18:44 | 1.0164 | 0.91146 | 0 |  | 18:44 | 0 | 0 | 5507.423 | 18:44 | 2.4766 | 2.2766 | 0.20004 | 2.657e-05 | 0
[13 empty] | 18:44 | 1.0034 | 0.91146 | 0 |  | 18:44 | 0 | 0 | 5507.423 | 18:44 | 2.4772 | 2.2771 | 0.2001 | 2.6578e-05 | 0
[13 empty] | 18:44 | 0.99062 | 0.91146 | 0 |  | 18:44 | 0 | 0 | 5507.423 | 18:44 | 2.4779 | 2.2777 | 0.20013 | 2.6583e-05 | 0
[13 empty] | 18:44 | 0.97811 | 0.91146 | 0 |  | 18:44 | 0 | 0 | 5507.423 | 18:44 | 2.4785 | 2.2783 | 0.20019 | 2.6589e-05 | 0
[13 empty] | 18:45 | 0.96585 | 0.91146 | 0 |  | 18:45 | 0 | 0 | 5507.423 | 18:45 | 2.4791 | 2.2788 | 0.20023 | 2.6597e-05 | 0
[13 empty] | 18:45 | 0.95385 | 0.91146 | 0 |  | 18:45 | 0 | 0 | 5507.423 | 18:45 | 2.4795 | 2.2792 | 0.20029 | 2.6602e-05 | 0
[13 empty] | 18:45 | 0.94209 | 0.91146 | 0 |  | 18:45 | 0 | 0 | 5507.423 | 18:45 | 2.4802 | 2.2798 | 0.20033 | 2.6608e-05 | 0
[13 empty] | 18:46 | 0.93058 | 0.91146 | 0 |  | 18:46 | 0 | 0 | 5507.423 | 18:46 | 2.4808 | 2.2804 | 0.20038 | 2.6614e-05 | 0
[13 empty] | 18:46 | 0.9193 | 0.91146 | 0 |  | 18:46 | 0 | 0 | 5507.423 | 18:46 | 2.4814 | 2.2809 | 0.20042 | 2.662e-05 | 0
[13 empty] | 18:46 | 0.90825 | 0.91146 | 0 |  | 18:46 | 0 | 0 | 5507.423 | 18:46 | 2.4818 | 2.2813 | 0.20046 | 2.6625e-05 | 0
[13 empty] | 18:46 | 0.89743 | 0.91146 | 0 |  | 18:46 | 0 | 0 | 5507.423 | 18:46 | 2.4824 | 2.2819 | 0.20052 | 2.6633e-05 | 0
[13 empty] | 18:46 | 0.88683 | 0.91146 | 0 |  | 18:46 | 0 | 0 | 5507.423 | 18:46 | 2.4829 | 2.2823 | 0.20055 | 2.6639e-05 | 0
[13 empty] | 18:47 | 0.87645 | 0.91146 | 0 |  | 18:47 | 0 | 0 | 5507.423 | 18:47 | 2.4835 | 2.2829 | 0.20059 | 2.6644e-05 | 0
[13 empty] | 18:47 | 0.86628 | 0.91146 | 0 |  | 18:47 | 0 | 0 | 5507.423 | 18:47 | 2.4841 | 2.2834 | 0.20063 | 2.6648e-05 | 0
[13 empty] | 18:47 | 0.85633 | 0.91146 | 0 |  | 18:47 | 0 | 0 | 5507.423 | 18:47 | 2.4845 | 2.2838 | 0.20069 | 2.6654e-05 | 0
[13 empty] | 18:48 | 0.84657 | 0.91146 | 0 |  | 18:48 | 0 | 0 | 5507.423 | 18:48 | 2.4849 | 2.2842 | 0.20073 | 2.666e-05 | 0
[13 empty] | 18:48 | 0.83702 | 0.91146 | 0 |  | 18:48 | 0 | 0 | 5507.423 | 18:48 | 2.4856 | 2.2848 | 0.20076 | 2.6665e-05 | 0
[13 empty] | 18:48 | 0.82766 | 0.91146 | 0 |  | 18:48 | 0 | 0 | 5507.423 | 18:48 | 2.486 | 2.2851 | 0.2008 | 2.6671e-05 | 0
[13 empty] | 18:48 | 0.8185 | 0.91146 | 0 |  | 18:48 | 0 | 0 | 5507.423 | 18:48 | 2.4866 | 2.2857 | 0.20084 | 2.6677e-05 | 0
[13 empty] | 18:48 | 0.80952 | 0.91146 | 0 |  | 18:48 | 0 | 0 | 5507.423 | 18:48 | 2.487 | 2.2861 | 0.20088 | 2.6681e-05 | 0
[13 empty] | 18:49 | 0.80073 | 0.91146 | 0 |  | 18:49 | 0 | 0 | 5507.423 | 18:49 | 2.4874 | 2.2865 | 0.20092 | 2.6686e-05 | 0
[13 empty] | 18:49 | 0.79211 | 0.91146 | 0 |  | 18:49 | 0 | 0 | 5507.423 | 18:49 | 2.488 | 2.2871 | 0.20096 | 2.6692e-05 | 0
[13 empty] | 18:49 | 0.78368 | 0.91146 | 0 |  | 18:49 | 0 | 0 | 5507.423 | 18:49 | 2.4885 | 2.2874 | 0.20099 | 2.6698e-05 | 0
[13 empty] | 18:50 | 0.77542 | 0.91146 | 0 |  | 18:50 | 0 | 0 | 5507.423 | 18:50 | 2.4889 | 2.2878 | 0.20103 | 2.6702e-05 | 0
[13 empty] | 18:50 | 0.76733 | 0.91146 | 0 |  | 18:50 | 0 | 0 | 5507.423 | 18:50 | 2.4895 | 2.2884 | 0.20107 | 2.6707e-05 | 0
[13 empty] | 18:50 | 0.7594 | 0.91146 | 0 |  | 18:50 | 0 | 0 | 5507.423 | 18:50 | 2.4899 | 2.2888 | 0.20111 | 2.6711e-05 | 0
[13 empty] | 18:50 | 0.75164 | 0.91146 | 0 |  | 18:50 | 0 | 0 | 5507.423 | 18:50 | 2.4903 | 2.2892 | 0.20115 | 2.6717e-05 | 0
[13 empty] | 18:50 | 0.74403 | 0.91146 | 0 |  | 18:50 | 0 | 0 | 5507.423 | 18:50 | 2.4908 | 2.2895 | 0.20118 | 2.6721e-05 | 0
[13 empty] | 18:51 | 0.73658 | 0.91146 | 0 |  | 18:51 | 0 | 0 | 5507.423 | 18:51 | 2.4912 | 2.2899 | 0.20122 | 2.6727e-05 | 0
[13 empty] | 18:51 | 0.72929 | 0.91146 | 0 |  | 18:51 | 0 | 0 | 5507.423 | 18:51 | 2.4916 | 2.2903 | 0.20126 | 2.673e-05 | 0
[13 empty] | 18:51 | 1.1629 | 0.91146 | 0 |  | 18:51 | 0 | 0 | 5507.423 | 18:51 | 2.4924 | 2.2911 | 0.20132 | 2.6738e-05 | 0
[13 empty] | 18:52 | 1.1468 | 0.91146 | 0 |  | 18:52 | 0 | 0 | 5507.423 | 18:52 | 2.493 | 2.2916 | 0.20138 | 2.6746e-05 | 0
[13 empty] | 18:52 | 1.1311 | 0.91146 | 0 |  | 18:52 | 0 | 0 | 5507.423 | 18:52 | 2.4937 | 2.2922 | 0.20143 | 2.6753e-05 | 0
[13 empty] | 18:52 | 1.1157 | 0.91146 | 0 |  | 18:52 | 0 | 0 | 5507.423 | 18:52 | 2.4945 | 2.293 | 0.20147 | 2.6761e-05 | 0
[13 empty] | 18:52 | 1.1006 | 0.91146 | 0 |  | 18:52 | 0 | 0 | 5507.423 | 18:52 | 2.4951 | 2.2936 | 0.20153 | 2.6769e-05 | 0
[13 empty] | 18:52 | 1.0859 | 0.91146 | 0 |  | 18:52 | 0 | 0 | 5507.423 | 18:52 | 2.4957 | 2.2941 | 0.20159 | 2.6774e-05 | 0
[13 empty] | 18:53 | 1.0714 | 0.91146 | 0 |  | 18:53 | 0 | 0 | 5507.423 | 18:53 | 2.4964 | 2.2947 | 0.20164 | 2.6782e-05 | 0
[13 empty] | 18:53 | 1.0572 | 0.91146 | 0 |  | 18:53 | 0 | 0 | 5507.423 | 18:53 | 2.497 | 2.2953 | 0.20168 | 2.679e-05 | 0
[13 empty] | 18:53 | 1.0434 | 0.91146 | 0 |  | 18:53 | 0 | 0 | 5507.423 | 18:53 | 2.4976 | 2.2958 | 0.20174 | 2.6795e-05 | 0
[13 empty] | 18:54 | 1.0298 | 0.91146 | 0 |  | 18:54 | 0 | 0 | 5507.423 | 18:54 | 2.4982 | 2.2964 | 0.2018 | 2.6803e-05 | 0
[13 empty] | 18:54 | 1.0164 | 0.91146 | 0 |  | 18:54 | 0 | 0 | 5507.423 | 18:54 | 2.4988 | 2.297 | 0.20183 | 2.6809e-05 | 0
[13 empty] | 18:54 | 1.0034 | 0.91146 | 0 |  | 18:54 | 0 | 0 | 5507.423 | 18:54 | 2.4995 | 2.2976 | 0.20189 | 2.6816e-05 | 0
[13 empty] | 18:54 | 0.99062 | 0.91146 | 0 |  | 18:54 | 0 | 0 | 5507.423 | 18:54 | 2.5001 | 2.2981 | 0.20193 | 2.6822e-05 | 0
[13 empty] | 18:54 | 0.97811 | 0.91146 | 0 |  | 18:54 | 0 | 0 | 5507.423 | 18:54 | 2.5007 | 2.2987 | 0.20199 | 2.6828e-05 | 0
[13 empty] | 18:55 | 0.96585 | 0.91146 | 0 |  | 18:55 | 0 | 0 | 5507.423 | 18:55 | 2.5013 | 2.2993 | 0.20202 | 2.6835e-05 | 0
[13 empty] | 18:55 | 0.95385 | 0.91146 | 0 |  | 18:55 | 0 | 0 | 5507.423 | 18:55 | 2.5018 | 2.2997 | 0.20208 | 2.6841e-05 | 0
[13 empty] | 18:55 | 0.94209 | 0.91146 | 0 |  | 18:55 | 0 | 0 | 5507.423 | 18:55 | 2.5024 | 2.3002 | 0.20212 | 2.6847e-05 | 0
[13 empty] | 18:56 | 0.93058 | 0.91146 | 0 |  | 18:56 | 0 | 0 | 5507.423 | 18:56 | 2.503 | 2.3008 | 0.20218 | 2.6853e-05 | 0
[13 empty] | 18:56 | 0.9193 | 0.91146 | 0 |  | 18:56 | 0 | 0 | 5507.423 | 18:56 | 2.5036 | 2.3014 | 0.20222 | 2.6858e-05 | 0
[13 empty] | 18:56 | 0.90825 | 0.91146 | 0 |  | 18:56 | 0 | 0 | 5507.423 | 18:56 | 2.504 | 2.3018 | 0.20225 | 2.6864e-05 | 0
[13 empty] | 18:56 | 0.89743 | 0.91146 | 0 |  | 18:56 | 0 | 0 | 5507.423 | 18:56 | 2.5047 | 2.3023 | 0.20231 | 2.687e-05 | 0
[13 empty] | 18:56 | 0.88683 | 0.91146 | 0 |  | 18:56 | 0 | 0 | 5507.423 | 18:56 | 2.5051 | 2.3027 | 0.20235 | 2.6876e-05 | 0
[13 empty] | 18:57 | 0.87645 | 0.91146 | 0 |  | 18:57 | 0 | 0 | 5507.423 | 18:57 | 2.5057 | 2.3033 | 0.20239 | 2.6881e-05 | 0
[13 empty] | 18:57 | 0.86628 | 0.91146 | 0 |  | 18:57 | 0 | 0 | 5507.423 | 18:57 | 2.5063 | 2.3039 | 0.20243 | 2.6887e-05 | 0
[13 empty] | 18:57 | 0.85633 | 0.91146 | 0 |  | 18:57 | 0 | 0 | 5507.423 | 18:57 | 2.5068 | 2.3042 | 0.20248 | 2.6893e-05 | 0
[13 empty] | 18:57 | 0.84657 | 0.91146 | 0 |  | 18:57 | 0 | 0 | 5507.423 | 18:57 | 2.5072 | 2.3046 | 0.20252 | 2.6898e-05 | 0
[13 empty] | 18:58 | 0.83702 | 0.91146 | 0 |  | 18:58 | 0 | 0 | 5507.423 | 18:58 | 2.5078 | 2.3052 | 0.20256 | 2.6904e-05 | 0
[13 empty] | 18:58 | 0.82766 | 0.91146 | 0 |  | 18:58 | 0 | 0 | 5507.423 | 18:58 | 2.5082 | 2.3056 | 0.2026 | 2.691e-05 | 0
[13 empty] | 18:58 | 0.8185 | 0.91146 | 0 |  | 18:58 | 0 | 0 | 5507.423 | 18:58 | 2.5088 | 2.3062 | 0.20264 | 2.6916e-05 | 0
[13 empty] | 18:58 | 0.80952 | 0.91146 | 0 |  | 18:58 | 0 | 0 | 5507.423 | 18:58 | 2.5092 | 2.3065 | 0.20267 | 2.6919e-05 | 0
[13 empty] | 18:59 | 0.80073 | 0.91146 | 0 |  | 18:59 | 0 | 0 | 5507.423 | 18:59 | 2.5097 | 2.3069 | 0.20271 | 2.6925e-05 | 0
[13 empty] | 18:59 | 0.79211 | 0.91146 | 0 |  | 18:59 | 0 | 0 | 5507.423 | 18:59 | 2.5103 | 2.3075 | 0.20275 | 2.6931e-05 | 0
[13 empty] | 18:59 | 0.78368 | 0.91146 | 0 |  | 18:59 | 0 | 0 | 5507.423 | 18:59 | 2.5107 | 2.3079 | 0.20279 | 2.6935e-05 | 0
[13 empty] | 19:00 | 0.77542 | 0.91146 | 0 |  | 19:00 | 0 | 0 | 5507.423 | 19:00 | 2.5111 | 2.3083 | 0.20283 | 2.694e-05 | 0
[13 empty] | 19:00 | 0.76733 | 0.91146 | 0 |  | 19:00 | 0 | 0 | 5507.423 | 19:00 | 2.5115 | 2.3086 | 0.20287 | 2.6946e-05 | 0
[13 empty] | 19:00 | 0.7594 | 0.91146 | 0 |  | 19:00 | 0 | 0 | 5507.423 | 19:00 | 2.5121 | 2.3092 | 0.2029 | 2.695e-05 | 0
[13 empty] | 19:00 | 0.75164 | 0.91146 | 0 |  | 19:00 | 0 | 0 | 5507.423 | 19:00 | 2.5126 | 2.3096 | 0.20294 | 2.6956e-05 | 0
[13 empty] | 19:00 | 0.74403 | 0.91146 | 0 |  | 19:00 | 0 | 0 | 5507.423 | 19:00 | 2.513 | 2.31 | 0.20298 | 2.696e-05 | 0
[13 empty] | 19:01 | 0.73658 | 0.91146 | 0 |  | 19:01 | 0 | 0 | 5507.423 | 19:01 | 2.5134 | 2.3104 | 0.20302 | 2.6965e-05 | 0
[13 empty] | 19:01 | 0.72929 | 0.91146 | 0 |  | 19:01 | 0 | 0 | 5507.423 | 19:01 | 2.5138 | 2.3107 | 0.20306 | 2.6969e-05 | 0
[13 empty] | 19:01 | 1.1629 | 0.91146 | 0 |  | 19:01 | 0 | 0 | 5507.423 | 19:01 | 2.5146 | 2.3115 | 0.20311 | 2.6977e-05 | 0
[13 empty] | 19:01 | 1.1468 | 0.91146 | 0 |  | 19:01 | 0 | 0 | 5507.423 | 19:01 | 2.5153 | 2.3121 | 0.20317 | 2.6984e-05 | 0
[13 empty] | 19:02 | 1.1311 | 0.91146 | 0 |  | 19:02 | 0 | 0 | 5507.423 | 19:02 | 2.5159 | 2.3126 | 0.20323 | 2.6992e-05 | 0
[13 empty] | 19:02 | 1.1157 | 0.91146 | 0 |  | 19:02 | 0 | 0 | 5507.423 | 19:02 | 2.5167 | 2.3134 | 0.20327 | 2.7e-05 | 0
[13 empty] | 19:02 | 1.1006 | 0.91146 | 0 |  | 19:02 | 0 | 0 | 5507.423 | 19:02 | 2.5173 | 2.314 | 0.20332 | 2.7007e-05 | 0
[13 empty] | 19:02 | 1.0859 | 0.91146 | 0 |  | 19:02 | 0 | 0 | 5507.423 | 19:02 | 2.518 | 2.3146 | 0.20338 | 2.7013e-05 | 0
[13 empty] | 19:03 | 1.0714 | 0.91146 | 0 |  | 19:03 | 0 | 0 | 5507.423 | 19:03 | 2.5186 | 2.3151 | 0.20344 | 2.7021e-05 | 0
[13 empty] | 19:03 | 1.0572 | 0.91146 | 0 |  | 19:03 | 0 | 0 | 5507.423 | 19:03 | 2.5192 | 2.3157 | 0.20348 | 2.7026e-05 | 0
[13 empty] | 19:03 | 1.0434 | 0.91146 | 0 |  | 19:03 | 0 | 0 | 5507.423 | 19:03 | 2.5198 | 2.3163 | 0.20353 | 2.7034e-05 | 0
[13 empty] | 19:04 | 1.0298 | 0.91146 | 0 |  | 19:04 | 0 | 0 | 5507.423 | 19:04 | 2.5205 | 2.3169 | 0.20359 | 2.7042e-05 | 0
[13 empty] | 19:04 | 1.0164 | 0.91146 | 0 |  | 19:04 | 0 | 0 | 5507.423 | 19:04 | 2.5211 | 2.3174 | 0.20363 | 2.7047e-05 | 0
[13 empty] | 19:04 | 1.0034 | 0.91146 | 0 |  | 19:04 | 0 | 0 | 5507.423 | 19:04 | 2.5217 | 2.318 | 0.20369 | 2.7053e-05 | 0
[13 empty] | 19:04 | 0.99062 | 0.91146 | 0 |  | 19:04 | 0 | 0 | 5507.423 | 19:04 | 2.5223 | 2.3186 | 0.20372 | 2.7061e-05 | 0
[13 empty] | 19:04 | 0.97811 | 0.91146 | 0 |  | 19:04 | 0 | 0 | 5507.423 | 19:04 | 2.523 | 2.3191 | 0.20378 | 2.7067e-05 | 0
[13 empty] | 19:05 | 0.96585 | 0.91146 | 0 |  | 19:05 | 0 | 0 | 5507.423 | 19:05 | 2.5236 | 2.3197 | 0.20382 | 2.7072e-05 | 0
[13 empty] | 19:05 | 0.95385 | 0.91146 | 0 |  | 19:05 | 0 | 0 | 5507.423 | 19:05 | 2.524 | 2.3201 | 0.20388 | 2.708e-05 | 0
[13 empty] | 19:05 | 0.94209 | 0.91146 | 0 |  | 19:05 | 0 | 0 | 5507.423 | 19:05 | 2.5246 | 2.3207 | 0.20392 | 2.7086e-05 | 0
[13 empty] | 19:05 | 0.93058 | 0.91146 | 0 |  | 19:05 | 0 | 0 | 5507.423 | 19:05 | 2.5252 | 2.3212 | 0.20397 | 2.7091e-05 | 0
[13 empty] | 19:06 | 0.9193 | 0.91146 | 0 |  | 19:06 | 0 | 0 | 5507.423 | 19:06 | 2.5259 | 2.3218 | 0.20401 | 2.7097e-05 | 0
[13 empty] | 19:06 | 0.90825 | 0.91146 | 0 |  | 19:06 | 0 | 0 | 5507.423 | 19:06 | 2.5263 | 2.3222 | 0.20405 | 2.7103e-05 | 0
[13 empty] | 19:06 | 0.89743 | 0.91146 | 0 |  | 19:06 | 0 | 0 | 5507.423 | 19:06 | 2.5269 | 2.3228 | 0.20411 | 2.7109e-05 | 0
[13 empty] | 19:06 | 0.88683 | 0.91146 | 0 |  | 19:06 | 0 | 0 | 5507.423 | 19:06 | 2.5273 | 2.3232 | 0.20414 | 2.7114e-05 | 0
[13 empty] | 19:07 | 0.87645 | 0.91146 | 0 |  | 19:07 | 0 | 0 | 5507.423 | 19:07 | 2.5279 | 2.3237 | 0.20418 | 2.712e-05 | 0
[13 empty] | 19:07 | 0.86628 | 0.91146 | 0 |  | 19:07 | 0 | 0 | 5507.423 | 19:07 | 2.5284 | 2.3241 | 0.20422 | 2.7126e-05 | 0
[13 empty] | 19:07 | 0.85633 | 0.91146 | 0 |  | 19:07 | 0 | 0 | 5507.423 | 19:07 | 2.529 | 2.3247 | 0.20428 | 2.7131e-05 | 0
[13 empty] | 19:08 | 0.84657 | 0.91146 | 0 |  | 19:08 | 0 | 0 | 5507.423 | 19:08 | 2.5294 | 2.3251 | 0.20432 | 2.7137e-05 | 0
[13 empty] | 19:08 | 0.83702 | 0.91146 | 0 |  | 19:08 | 0 | 0 | 5507.423 | 19:08 | 2.53 | 2.3256 | 0.20435 | 2.7143e-05 | 0
[13 empty] | 19:08 | 0.82766 | 0.91146 | 0 |  | 19:08 | 0 | 0 | 5507.423 | 19:08 | 2.5304 | 2.326 | 0.20439 | 2.7149e-05 | 0
[13 empty] | 19:08 | 0.8185 | 0.91146 | 0 |  | 19:08 | 0 | 0 | 5507.423 | 19:08 | 2.531 | 2.3266 | 0.20443 | 2.7152e-05 | 0
[13 empty] | 19:08 | 0.80952 | 0.91146 | 0 |  | 19:08 | 0 | 0 | 5507.423 | 19:08 | 2.5315 | 2.327 | 0.20447 | 2.7158e-05 | 0
[13 empty] | 19:09 | 0.80073 | 0.91146 | 0 |  | 19:09 | 0 | 0 | 5507.423 | 19:09 | 2.5319 | 2.3274 | 0.20451 | 2.7164e-05 | 0
[13 empty] | 19:09 | 0.79211 | 0.91146 | 0 |  | 19:09 | 0 | 0 | 5507.423 | 19:09 | 2.5325 | 2.3279 | 0.20455 | 2.717e-05 | 0
[13 empty] | 19:09 | 0.78368 | 0.91146 | 0 |  | 19:09 | 0 | 0 | 5507.423 | 19:09 | 2.5329 | 2.3283 | 0.20458 | 2.7173e-05 | 0
[13 empty] | 19:10 | 0.77542 | 0.91146 | 0 |  | 19:10 | 0 | 0 | 5507.423 | 19:10 | 2.5333 | 2.3287 | 0.20462 | 2.7179e-05 | 0
[13 empty] | 19:10 | 0.76733 | 0.91146 | 0 |  | 19:10 | 0 | 0 | 5507.423 | 19:10 | 2.5338 | 2.3291 | 0.20466 | 2.7185e-05 | 0
[13 empty] | 19:10 | 0.7594 | 0.91146 | 0 |  | 19:10 | 0 | 0 | 5507.423 | 19:10 | 2.5344 | 2.3296 | 0.2047 | 2.7189e-05 | 0
[13 empty] | 19:10 | 0.75164 | 0.91146 | 0 |  | 19:10 | 0 | 0 | 5507.423 | 19:10 | 2.5348 | 2.33 | 0.20474 | 2.7194e-05 | 0
[13 empty] | 19:10 | 0.74403 | 0.91146 | 0 |  | 19:10 | 0 | 0 | 5507.423 | 19:10 | 2.5352 | 2.3304 | 0.20478 | 2.7198e-05 | 0
[13 empty] | 19:11 | 0.73658 | 0.91146 | 0 |  | 19:11 | 0 | 0 | 5507.423 | 19:11 | 2.5356 | 2.3308 | 0.20481 | 2.7204e-05 | 0
[13 empty] | 19:11 | 0.72929 | 0.91146 | 0 |  | 19:11 | 0 | 0 | 5507.423 | 19:11 | 2.5361 | 2.3312 | 0.20485 | 2.7208e-05 | 0
[13 empty] | 19:11 | 1.1629 | 0.91146 | 0 |  | 19:11 | 0 | 0 | 5507.423 | 19:11 | 2.5369 | 2.3319 | 0.20491 | 2.7215e-05 | 0
[13 empty] | 19:12 | 1.1468 | 0.91146 | 0 |  | 19:12 | 0 | 0 | 5507.423 | 19:12 | 2.5375 | 2.3325 | 0.20497 | 2.7223e-05 | 0
[13 empty] | 19:12 | 1.1311 | 0.91146 | 0 |  | 19:12 | 0 | 0 | 5507.423 | 19:12 | 2.5381 | 2.3331 | 0.20502 | 2.7231e-05 | 0
[13 empty] | 19:12 | 1.1157 | 0.91146 | 0 |  | 19:12 | 0 | 0 | 5507.423 | 19:12 | 2.5389 | 2.3338 | 0.20506 | 2.7238e-05 | 0
[13 empty] | 19:12 | 1.1006 | 0.91146 | 0 |  | 19:12 | 0 | 0 | 5507.423 | 19:12 | 2.5396 | 2.3344 | 0.20512 | 2.7244e-05 | 0
[13 empty] | 19:12 | 1.0859 | 0.91146 | 0 |  | 19:12 | 0 | 0 | 5507.423 | 19:12 | 2.5402 | 2.335 | 0.20518 | 2.7252e-05 | 0
[13 empty] | 19:13 | 1.0714 | 0.91146 | 0 |  | 19:13 | 0 | 0 | 5507.423 | 19:13 | 2.5408 | 2.3356 | 0.20523 | 2.7259e-05 | 0
[13 empty] | 19:13 | 1.0572 | 0.91146 | 0 |  | 19:13 | 0 | 0 | 5507.423 | 19:13 | 2.5414 | 2.3361 | 0.20527 | 2.7265e-05 | 0
[13 empty] | 19:13 | 1.0434 | 0.91146 | 0 |  | 19:13 | 0 | 0 | 5507.423 | 19:13 | 2.5421 | 2.3367 | 0.20533 | 2.7273e-05 | 0
[13 empty] | 19:14 | 1.0298 | 0.91146 | 0 |  | 19:14 | 0 | 0 | 5507.423 | 19:14 | 2.5427 | 2.3373 | 0.20539 | 2.7279e-05 | 0
[13 empty] | 19:14 | 1.0164 | 0.91146 | 0 |  | 19:14 | 0 | 0 | 5507.423 | 19:14 | 2.5433 | 2.3379 | 0.20542 | 2.7286e-05 | 0
[13 empty] | 19:14 | 1.0034 | 0.91146 | 0 |  | 19:14 | 0 | 0 | 5507.423 | 19:14 | 2.5439 | 2.3384 | 0.20548 | 2.7292e-05 | 0
[13 empty] | 19:14 | 0.99062 | 0.91146 | 0 |  | 19:14 | 0 | 0 | 5507.423 | 19:14 | 2.5446 | 2.339 | 0.20552 | 2.73e-05 | 0
[13 empty] | 19:14 | 0.97811 | 0.91146 | 0 |  | 19:14 | 0 | 0 | 5507.423 | 19:14 | 2.5452 | 2.3396 | 0.20558 | 2.7305e-05 | 0
[13 empty] | 19:15 | 0.96585 | 0.91146 | 0 |  | 19:15 | 0 | 0 | 5507.423 | 19:15 | 2.5458 | 2.3402 | 0.20562 | 2.7311e-05 | 0
[13 empty] | 19:15 | 0.95385 | 0.91146 | 0 |  | 19:15 | 0 | 0 | 5507.423 | 19:15 | 2.5462 | 2.3405 | 0.20567 | 2.7317e-05 | 0
[13 empty] | 19:15 | 0.94209 | 0.91146 | 0 |  | 19:15 | 0 | 0 | 5507.423 | 19:15 | 2.5468 | 2.3411 | 0.20571 | 2.7324e-05 | 0
[13 empty] | 19:16 | 0.93058 | 0.91146 | 0 |  | 19:16 | 0 | 0 | 5507.423 | 19:16 | 2.5475 | 2.3417 | 0.20577 | 2.733e-05 | 0
[13 empty] | 19:16 | 0.9193 | 0.91146 | 0 |  | 19:16 | 0 | 0 | 5507.423 | 19:16 | 2.5481 | 2.3423 | 0.20581 | 2.7336e-05 | 0
[13 empty] | 19:16 | 0.90825 | 0.91146 | 0 |  | 19:16 | 0 | 0 | 5507.423 | 19:16 | 2.5485 | 2.3426 | 0.20584 | 2.7342e-05 | 0
[13 empty] | 19:16 | 0.89743 | 0.91146 | 0 |  | 19:16 | 0 | 0 | 5507.423 | 19:16 | 2.5491 | 2.3432 | 0.2059 | 2.7347e-05 | 0
[13 empty] | 19:16 | 0.88683 | 0.91146 | 0 |  | 19:16 | 0 | 0 | 5507.423 | 19:16 | 2.5496 | 2.3436 | 0.20594 | 2.7353e-05 | 0
[13 empty] | 19:17 | 0.87645 | 0.91146 | 0 |  | 19:17 | 0 | 0 | 5507.423 | 19:17 | 2.5502 | 2.3442 | 0.20598 | 2.7359e-05 | 0
[13 empty] | 19:17 | 0.86628 | 0.91146 | 0 |  | 19:17 | 0 | 0 | 5507.423 | 19:17 | 2.5506 | 2.3445 | 0.20602 | 2.7364e-05 | 0
[13 empty] | 19:17 | 0.85633 | 0.91146 | 0 |  | 19:17 | 0 | 0 | 5507.423 | 19:17 | 2.5512 | 2.3451 | 0.20607 | 2.737e-05 | 0
[13 empty] | 19:18 | 0.84657 | 0.91146 | 0 |  | 19:18 | 0 | 0 | 5507.423 | 19:18 | 2.5516 | 2.3455 | 0.20611 | 2.7376e-05 | 0
[13 empty] | 19:18 | 0.83702 | 0.91146 | 0 |  | 19:18 | 0 | 0 | 5507.423 | 19:18 | 2.5522 | 2.3461 | 0.20615 | 2.7382e-05 | 0
[13 empty] | 19:18 | 0.82766 | 0.91146 | 0 |  | 19:18 | 0 | 0 | 5507.423 | 19:18 | 2.5527 | 2.3465 | 0.20619 | 2.7387e-05 | 0
[13 empty] | 19:18 | 0.8185 | 0.91146 | 0 |  | 19:18 | 0 | 0 | 5507.423 | 19:18 | 2.5533 | 2.347 | 0.20623 | 2.7391e-05 | 0
[13 empty] | 19:18 | 0.80952 | 0.91146 | 0 |  | 19:18 | 0 | 0 | 5507.423 | 19:18 | 2.5537 | 2.3474 | 0.20626 | 2.7397e-05 | 0
[13 empty] | 19:19 | 0.80073 | 0.91146 | 0 |  | 19:19 | 0 | 0 | 5507.423 | 19:19 | 2.5541 | 2.3478 | 0.2063 | 2.7403e-05 | 0
[13 empty] | 19:19 | 0.79211 | 0.91146 | 0 |  | 19:19 | 0 | 0 | 5507.423 | 19:19 | 2.5547 | 2.3484 | 0.20634 | 2.7406e-05 | 0
[13 empty] | 19:19 | 0.78368 | 0.91146 | 0 |  | 19:19 | 0 | 0 | 5507.423 | 19:19 | 2.5552 | 2.3487 | 0.20638 | 2.7412e-05 | 0
[13 empty] | 19:20 | 0.77542 | 0.91146 | 0 |  | 19:20 | 0 | 0 | 5507.423 | 19:20 | 2.5556 | 2.3491 | 0.20642 | 2.7418e-05 | 0
[13 empty] | 19:20 | 0.76733 | 0.91146 | 0 |  | 19:20 | 0 | 0 | 5507.423 | 19:20 | 2.556 | 2.3495 | 0.20646 | 2.7422e-05 | 0
[13 empty] | 19:20 | 0.7594 | 0.91146 | 0 |  | 19:20 | 0 | 0 | 5507.423 | 19:20 | 2.5566 | 2.3501 | 0.20649 | 2.7427e-05 | 0
[13 empty] | 19:20 | 0.75164 | 0.91146 | 0 |  | 19:20 | 0 | 0 | 5507.423 | 19:20 | 2.557 | 2.3505 | 0.20653 | 2.7433e-05 | 0
[13 empty] | 19:20 | 0.74403 | 0.91146 | 0 |  | 19:20 | 0 | 0 | 5507.423 | 19:20 | 2.5574 | 2.3508 | 0.20657 | 2.7437e-05 | 0
[13 empty] | 19:21 | 0.73658 | 0.91146 | 0 |  | 19:21 | 0 | 0 | 5507.423 | 19:21 | 2.5579 | 2.3512 | 0.20661 | 2.7443e-05 | 0
[13 empty] | 19:21 | 0.72929 | 0.91146 | 0 |  | 19:21 | 0 | 0 | 5507.423 | 19:21 | 2.5583 | 2.3516 | 0.20665 | 2.7447e-05 | 0
[13 empty] | 19:21 | 1.1629 | 0.91146 | 0 |  | 19:21 | 0 | 0 | 5507.423 | 19:21 | 2.5591 | 2.3524 | 0.2067 | 2.7454e-05 | 0
[13 empty] | 19:22 | 1.1468 | 0.91146 | 0 |  | 19:22 | 0 | 0 | 5507.423 | 19:22 | 2.5597 | 2.3529 | 0.20676 | 2.7462e-05 | 0
[13 empty] | 19:22 | 1.1311 | 0.91146 | 0 |  | 19:22 | 0 | 0 | 5507.423 | 19:22 | 2.5604 | 2.3535 | 0.20682 | 2.747e-05 | 0
[13 empty] | 19:22 | 1.1157 | 0.91146 | 0 |  | 19:22 | 0 | 0 | 5507.423 | 19:22 | 2.5612 | 2.3543 | 0.20686 | 2.7477e-05 | 0
[13 empty] | 19:22 | 1.1006 | 0.91146 | 0 |  | 19:22 | 0 | 0 | 5507.423 | 19:22 | 2.5618 | 2.3549 | 0.20691 | 2.7483e-05 | 0
[13 empty] | 19:22 | 1.0859 | 0.91146 | 0 |  | 19:22 | 0 | 0 | 5507.423 | 19:22 | 2.5624 | 2.3554 | 0.20697 | 2.7491e-05 | 0
[13 empty] | 19:23 | 1.0714 | 0.91146 | 0 |  | 19:23 | 0 | 0 | 5507.423 | 19:23 | 2.5631 | 2.356 | 0.20703 | 2.7498e-05 | 0
[13 empty] | 19:23 | 1.0572 | 0.91146 | 0 |  | 19:23 | 0 | 0 | 5507.423 | 19:23 | 2.5637 | 2.3566 | 0.20707 | 2.7504e-05 | 0
[13 empty] | 19:23 | 1.0434 | 0.91146 | 0 |  | 19:23 | 0 | 0 | 5507.423 | 19:23 | 2.5643 | 2.3571 | 0.20712 | 2.7512e-05 | 0
[13 empty] | 19:24 | 1.0298 | 0.91146 | 0 |  | 19:24 | 0 | 0 | 5507.423 | 19:24 | 2.5649 | 2.3577 | 0.20718 | 2.7517e-05 | 0
[13 empty] | 19:24 | 1.0164 | 0.91146 | 0 |  | 19:24 | 0 | 0 | 5507.423 | 19:24 | 2.5655 | 2.3583 | 0.20722 | 2.7525e-05 | 0
[13 empty] | 19:24 | 1.0034 | 0.91146 | 0 |  | 19:24 | 0 | 0 | 5507.423 | 19:24 | 2.5662 | 2.3589 | 0.20728 | 2.7531e-05 | 0
[13 empty] | 19:24 | 0.99062 | 0.91146 | 0 |  | 19:24 | 0 | 0 | 5507.423 | 19:24 | 2.5668 | 2.3594 | 0.20733 | 2.7538e-05 | 0
[13 empty] | 19:24 | 0.97811 | 0.91146 | 0 |  | 19:24 | 0 | 0 | 5507.423 | 19:24 | 2.5674 | 2.36 | 0.20737 | 2.7544e-05 | 0
[13 empty] | 19:25 | 0.96585 | 0.91146 | 0 |  | 19:25 | 0 | 0 | 5507.423 | 19:25 | 2.568 | 2.3606 | 0.20741 | 2.755e-05 | 0
[13 empty] | 19:25 | 0.95385 | 0.91146 | 0 |  | 19:25 | 0 | 0 | 5507.423 | 19:25 | 2.5685 | 2.361 | 0.20747 | 2.7555e-05 | 0
[13 empty] | 19:25 | 0.94209 | 0.91146 | 0 |  | 19:25 | 0 | 0 | 5507.423 | 19:25 | 2.5691 | 2.3615 | 0.20751 | 2.7563e-05 | 0
[13 empty] | 19:26 | 0.93058 | 0.91146 | 0 |  | 19:26 | 0 | 0 | 5507.423 | 19:26 | 2.5697 | 2.3621 | 0.20756 | 2.7569e-05 | 0
[13 empty] | 19:26 | 0.9193 | 0.91146 | 0 |  | 19:26 | 0 | 0 | 5507.423 | 19:26 | 2.5703 | 2.3627 | 0.2076 | 2.7575e-05 | 0
[13 empty] | 19:26 | 0.90825 | 0.91146 | 0 |  | 19:26 | 0 | 0 | 5507.423 | 19:26 | 2.5707 | 2.3631 | 0.20764 | 2.758e-05 | 0
[13 empty] | 19:26 | 0.89743 | 0.91146 | 0 |  | 19:26 | 0 | 0 | 5507.423 | 19:26 | 2.5714 | 2.3636 | 0.2077 | 2.7586e-05 | 0
[13 empty] | 19:26 | 0.88683 | 0.91146 | 0 |  | 19:26 | 0 | 0 | 5507.423 | 19:26 | 2.5718 | 2.364 | 0.20774 | 2.7592e-05 | 0
[13 empty] | 19:27 | 0.87645 | 0.91146 | 0 |  | 19:27 | 0 | 0 | 5507.423 | 19:27 | 2.5724 | 2.3646 | 0.20777 | 2.7597e-05 | 0
[13 empty] | 19:27 | 0.86628 | 0.91146 | 0 |  | 19:27 | 0 | 0 | 5507.423 | 19:27 | 2.5728 | 2.365 | 0.20781 | 2.7603e-05 | 0
[13 empty] | 19:27 | 0.85633 | 0.91146 | 0 |  | 19:27 | 0 | 0 | 5507.423 | 19:27 | 2.5734 | 2.3656 | 0.20787 | 2.7609e-05 | 0
[13 empty] | 19:28 | 0.84657 | 0.91146 | 0 |  | 19:28 | 0 | 0 | 5507.423 | 19:28 | 2.5739 | 2.3659 | 0.20791 | 2.7615e-05 | 0
[13 empty] | 19:28 | 0.83702 | 0.91146 | 0 |  | 19:28 | 0 | 0 | 5507.423 | 19:28 | 2.5745 | 2.3665 | 0.20795 | 2.762e-05 | 0
[13 empty] | 19:28 | 0.82766 | 0.91146 | 0 |  | 19:28 | 0 | 0 | 5507.423 | 19:28 | 2.5749 | 2.3669 | 0.20798 | 2.7624e-05 | 0
[13 empty] | 19:28 | 0.8185 | 0.91146 | 0 |  | 19:28 | 0 | 0 | 5507.423 | 19:28 | 2.5755 | 2.3675 | 0.20802 | 2.763e-05 | 0
[13 empty] | 19:28 | 0.80952 | 0.91146 | 0 |  | 19:28 | 0 | 0 | 5507.423 | 19:28 | 2.5759 | 2.3678 | 0.20806 | 2.7636e-05 | 0
[13 empty] | 19:29 | 0.80073 | 0.91146 | 0 |  | 19:29 | 0 | 0 | 5507.423 | 19:29 | 2.5764 | 2.3682 | 0.2081 | 2.7641e-05 | 0
[13 empty] | 19:29 | 0.79211 | 0.91146 | 0 |  | 19:29 | 0 | 0 | 5507.423 | 19:29 | 2.577 | 2.3688 | 0.20814 | 2.7645e-05 | 0
[13 empty] | 19:29 | 0.78368 | 0.91146 | 0 |  | 19:29 | 0 | 0 | 5507.423 | 19:29 | 2.5774 | 2.3692 | 0.20817 | 2.7651e-05 | 0
[13 empty] | 19:30 | 0.77542 | 0.91146 | 0 |  | 19:30 | 0 | 0 | 5507.423 | 19:30 | 2.5778 | 2.3696 | 0.20821 | 2.7657e-05 | 0
[13 empty] | 19:30 | 0.76733 | 0.91146 | 0 |  | 19:30 | 0 | 0 | 5507.423 | 19:30 | 2.5782 | 2.3699 | 0.20825 | 2.766e-05 | 0
[13 empty] | 19:30 | 0.7594 | 0.91146 | 0 |  | 19:30 | 0 | 0 | 5507.423 | 19:30 | 2.5788 | 2.3705 | 0.20829 | 2.7666e-05 | 0
[13 empty] | 19:30 | 0.75164 | 0.91146 | 0 |  | 19:30 | 0 | 0 | 5507.423 | 19:30 | 2.5793 | 2.3709 | 0.20833 | 2.767e-05 | 0
[13 empty] | 19:30 | 0.74403 | 0.91146 | 0 |  | 19:30 | 0 | 0 | 5507.423 | 19:30 | 2.5797 | 2.3713 | 0.20837 | 2.7676e-05 | 0
[13 empty] | 19:31 | 0.73658 | 0.91146 | 0 |  | 19:31 | 0 | 0 | 5507.423 | 19:31 | 2.5801 | 2.3717 | 0.2084 | 2.768e-05 | 0
[13 empty] | 19:31 | 0.72929 | 0.91146 | 0 |  | 19:31 | 0 | 0 | 5507.423 | 19:31 | 2.5805 | 2.372 | 0.20844 | 2.7685e-05 | 0
[13 empty] | 19:31 | 1.1629 | 0.91146 | 0 |  | 19:31 | 0 | 0 | 5507.423 | 19:31 | 2.5813 | 2.3728 | 0.2085 | 2.7693e-05 | 0
[13 empty] | 19:32 | 1.1468 | 0.91146 | 0 |  | 19:32 | 0 | 0 | 5507.423 | 19:32 | 2.582 | 2.3734 | 0.20856 | 2.7701e-05 | 0
[13 empty] | 19:32 | 1.1311 | 0.91146 | 0 |  | 19:32 | 0 | 0 | 5507.423 | 19:32 | 2.5826 | 2.374 | 0.20861 | 2.7708e-05 | 0
[13 empty] | 19:32 | 1.1157 | 0.91146 | 0 |  | 19:32 | 0 | 0 | 5507.423 | 19:32 | 2.5834 | 2.3747 | 0.20865 | 2.7714e-05 | 0
[13 empty] | 19:32 | 1.1006 | 0.91146 | 0 |  | 19:32 | 0 | 0 | 5507.423 | 19:32 | 2.584 | 2.3753 | 0.20871 | 2.7722e-05 | 0
[13 empty] | 19:32 | 1.0859 | 0.91146 | 0 |  | 19:32 | 0 | 0 | 5507.423 | 19:32 | 2.5847 | 2.3759 | 0.20877 | 2.7729e-05 | 0
[13 empty] | 19:33 | 1.0714 | 0.91146 | 0 |  | 19:33 | 0 | 0 | 5507.423 | 19:33 | 2.5853 | 2.3764 | 0.20882 | 2.7735e-05 | 0
[13 empty] | 19:33 | 1.0572 | 0.91146 | 0 |  | 19:33 | 0 | 0 | 5507.423 | 19:33 | 2.5859 | 2.377 | 0.20886 | 2.7743e-05 | 0
[13 empty] | 19:33 | 1.0434 | 0.91146 | 0 |  | 19:33 | 0 | 0 | 5507.423 | 19:33 | 2.5865 | 2.3776 | 0.20892 | 2.775e-05 | 0
[13 empty] | 19:34 | 1.0298 | 0.91146 | 0 |  | 19:34 | 0 | 0 | 5507.423 | 19:34 | 2.5872 | 2.3782 | 0.20898 | 2.7756e-05 | 0
[13 empty] | 19:34 | 1.0164 | 0.91146 | 0 |  | 19:34 | 0 | 0 | 5507.423 | 19:34 | 2.5878 | 2.3787 | 0.20901 | 2.7764e-05 | 0
[13 empty] | 19:34 | 1.0034 | 0.91146 | 0 |  | 19:34 | 0 | 0 | 5507.423 | 19:34 | 2.5884 | 2.3793 | 0.20907 | 2.7769e-05 | 0
[13 empty] | 19:34 | 0.99062 | 0.91146 | 0 |  | 19:34 | 0 | 0 | 5507.423 | 19:34 | 2.589 | 2.3799 | 0.20913 | 2.7775e-05 | 0
[13 empty] | 19:34 | 0.97811 | 0.91146 | 0 |  | 19:34 | 0 | 0 | 5507.423 | 19:34 | 2.5896 | 2.3804 | 0.20917 | 2.7783e-05 | 0
[13 empty] | 19:35 | 0.96585 | 0.91146 | 0 |  | 19:35 | 0 | 0 | 5507.423 | 19:35 | 2.5903 | 2.381 | 0.20921 | 2.7788e-05 | 0
[13 empty] | 19:35 | 0.95385 | 0.91146 | 0 |  | 19:35 | 0 | 0 | 5507.423 | 19:35 | 2.5907 | 2.3814 | 0.20926 | 2.7794e-05 | 0
[13 empty] | 19:35 | 0.94209 | 0.91146 | 0 |  | 19:35 | 0 | 0 | 5507.423 | 19:35 | 2.5913 | 2.382 | 0.2093 | 2.78e-05 | 0
[13 empty] | 19:36 | 0.93058 | 0.91146 | 0 |  | 19:36 | 0 | 0 | 5507.423 | 19:36 | 2.5919 | 2.3825 | 0.20936 | 2.7808e-05 | 0
[13 empty] | 19:36 | 0.9193 | 0.91146 | 0 |  | 19:36 | 0 | 0 | 5507.423 | 19:36 | 2.5925 | 2.3831 | 0.2094 | 2.7813e-05 | 0
[13 empty] | 19:36 | 0.90825 | 0.91146 | 0 |  | 19:36 | 0 | 0 | 5507.423 | 19:36 | 2.593 | 2.3835 | 0.20944 | 2.7819e-05 | 0
[13 empty] | 19:36 | 0.89743 | 0.91146 | 0 |  | 19:36 | 0 | 0 | 5507.423 | 19:36 | 2.5936 | 2.3841 | 0.20949 | 2.7825e-05 | 0
[13 empty] | 19:36 | 0.88683 | 0.91146 | 0 |  | 19:36 | 0 | 0 | 5507.423 | 19:36 | 2.594 | 2.3845 | 0.20953 | 2.783e-05 | 0
[13 empty] | 19:37 | 0.87645 | 0.91146 | 0 |  | 19:37 | 0 | 0 | 5507.423 | 19:37 | 2.5946 | 2.385 | 0.20957 | 2.7836e-05 | 0
[13 empty] | 19:37 | 0.86628 | 0.91146 | 0 |  | 19:37 | 0 | 0 | 5507.423 | 19:37 | 2.595 | 2.3854 | 0.20961 | 2.7842e-05 | 0
[13 empty] | 19:37 | 0.85633 | 0.91146 | 0 |  | 19:37 | 0 | 0 | 5507.423 | 19:37 | 2.5957 | 2.386 | 0.20966 | 2.7848e-05 | 0
[13 empty] | 19:38 | 0.84657 | 0.91146 | 0 |  | 19:38 | 0 | 0 | 5507.423 | 19:38 | 2.5961 | 2.3864 | 0.2097 | 2.7853e-05 | 0
[13 empty] | 19:38 | 0.83702 | 0.91146 | 0 |  | 19:38 | 0 | 0 | 5507.423 | 19:38 | 2.5967 | 2.3869 | 0.20974 | 2.7857e-05 | 0
[13 empty] | 19:38 | 0.82766 | 0.91146 | 0 |  | 19:38 | 0 | 0 | 5507.423 | 19:38 | 2.5971 | 2.3873 | 0.20978 | 2.7863e-05 | 0
[13 empty] | 19:38 | 0.8185 | 0.91146 | 0 |  | 19:38 | 0 | 0 | 5507.423 | 19:38 | 2.5977 | 2.3879 | 0.20982 | 2.7869e-05 | 0
[13 empty] | 19:38 | 0.80952 | 0.91146 | 0 |  | 19:38 | 0 | 0 | 5507.423 | 19:38 | 2.5982 | 2.3883 | 0.20986 | 2.7874e-05 | 0
[13 empty] | 19:39 | 0.80073 | 0.91146 | 0 |  | 19:39 | 0 | 0 | 5507.423 | 19:39 | 2.5986 | 2.3887 | 0.20989 | 2.788e-05 | 0
[13 empty] | 19:39 | 0.79211 | 0.91146 | 0 |  | 19:39 | 0 | 0 | 5507.423 | 19:39 | 2.5992 | 2.3892 | 0.20993 | 2.7884e-05 | 0
[13 empty] | 19:39 | 0.78368 | 0.91146 | 0 |  | 19:39 | 0 | 0 | 5507.423 | 19:39 | 2.5996 | 2.3896 | 0.20997 | 2.789e-05 | 0
[13 empty] | 19:40 | 0.77542 | 0.91146 | 0 |  | 19:40 | 0 | 0 | 5507.423 | 19:40 | 2.6 | 2.39 | 0.21001 | 2.7895e-05 | 0
[13 empty] | 19:40 | 0.76733 | 0.91146 | 0 |  | 19:40 | 0 | 0 | 5507.423 | 19:40 | 2.6005 | 2.3904 | 0.21005 | 2.7899e-05 | 0
[13 empty] | 19:40 | 0.7594 | 0.91146 | 0 |  | 19:40 | 0 | 0 | 5507.423 | 19:40 | 2.6011 | 2.391 | 0.21008 | 2.7905e-05 | 0
[13 empty] | 19:40 | 0.75164 | 0.91146 | 0 |  | 19:40 | 0 | 0 | 5507.423 | 19:40 | 2.6015 | 2.3913 | 0.21012 | 2.7909e-05 | 0
[13 empty] | 19:40 | 0.74403 | 0.91146 | 0 |  | 19:40 | 0 | 0 | 5507.423 | 19:40 | 2.6019 | 2.3917 | 0.21016 | 2.7915e-05 | 0
[13 empty] | 19:41 | 0.73658 | 0.91146 | 0 |  | 19:41 | 0 | 0 | 5507.423 | 19:41 | 2.6023 | 2.3921 | 0.2102 | 2.7918e-05 | 0
[13 empty] | 19:41 | 0.72929 | 0.91146 | 0 |  | 19:41 | 0 | 0 | 5507.423 | 19:41 | 2.6027 | 2.3925 | 0.21024 | 2.7924e-05 | 0
[13 empty] | 19:41 | 1.1629 | 0.91146 | 0 |  | 19:41 | 0 | 0 | 5507.423 | 19:41 | 2.6036 | 2.3932 | 0.21029 | 2.7932e-05 | 0
[13 empty] | 19:42 | 1.1468 | 0.91146 | 0 |  | 19:42 | 0 | 0 | 5507.423 | 19:42 | 2.6042 | 2.3938 | 0.21035 | 2.7939e-05 | 0
[13 empty] | 19:42 | 1.1311 | 0.91146 | 0 |  | 19:42 | 0 | 0 | 5507.423 | 19:42 | 2.6048 | 2.3944 | 0.21041 | 2.7945e-05 | 0
[13 empty] | 19:42 | 1.1157 | 0.91146 | 0 |  | 19:42 | 0 | 0 | 5507.423 | 19:42 | 2.6056 | 2.3952 | 0.21045 | 2.7953e-05 | 0
[13 empty] | 19:42 | 1.1006 | 0.91146 | 0 |  | 19:42 | 0 | 0 | 5507.423 | 19:42 | 2.6063 | 2.3957 | 0.2105 | 2.796e-05 | 0
[13 empty] | 19:42 | 1.0859 | 0.91146 | 0 |  | 19:42 | 0 | 0 | 5507.423 | 19:42 | 2.6069 | 2.3963 | 0.21056 | 2.7968e-05 | 0
[13 empty] | 19:43 | 1.0714 | 0.91146 | 0 |  | 19:43 | 0 | 0 | 5507.423 | 19:43 | 2.6075 | 2.3969 | 0.21062 | 2.7974e-05 | 0
[13 empty] | 19:43 | 1.0572 | 0.91146 | 0 |  | 19:43 | 0 | 0 | 5507.423 | 19:43 | 2.6082 | 2.3974 | 0.21068 | 2.7981e-05 | 0
[13 empty] | 19:43 | 1.0434 | 0.91146 | 0 |  | 19:43 | 0 | 0 | 5507.423 | 19:43 | 2.6088 | 2.398 | 0.21071 | 2.7987e-05 | 0
[13 empty] | 19:44 | 1.0298 | 0.91146 | 0 |  | 19:44 | 0 | 0 | 5507.423 | 19:44 | 2.6094 | 2.3986 | 0.21077 | 2.7995e-05 | 0
[13 empty] | 19:44 | 1.0164 | 0.91146 | 0 |  | 19:44 | 0 | 0 | 5507.423 | 19:44 | 2.61 | 2.3992 | 0.21081 | 2.8e-05 | 0
[13 empty] | 19:44 | 1.0034 | 0.91146 | 0 |  | 19:44 | 0 | 0 | 5507.423 | 19:44 | 2.6106 | 2.3997 | 0.21087 | 2.8008e-05 | 0
[13 empty] | 19:44 | 0.99062 | 0.91146 | 0 |  | 19:44 | 0 | 0 | 5507.423 | 19:44 | 2.6113 | 2.4003 | 0.21092 | 2.8014e-05 | 0
[13 empty] | 19:44 | 0.97811 | 0.91146 | 0 |  | 19:44 | 0 | 0 | 5507.423 | 19:44 | 2.6119 | 2.4009 | 0.21096 | 2.8021e-05 | 0
[13 empty] | 19:45 | 0.96585 | 0.91146 | 0 |  | 19:45 | 0 | 0 | 5507.423 | 19:45 | 2.6125 | 2.4015 | 0.211 | 2.8027e-05 | 0
[13 empty] | 19:45 | 0.95385 | 0.91146 | 0 |  | 19:45 | 0 | 0 | 5507.423 | 19:45 | 2.6129 | 2.4018 | 0.21106 | 2.8033e-05 | 0
[13 empty] | 19:45 | 0.94209 | 0.91146 | 0 |  | 19:45 | 0 | 0 | 5507.423 | 19:45 | 2.6135 | 2.4024 | 0.2111 | 2.8039e-05 | 0
[13 empty] | 19:46 | 0.93058 | 0.91146 | 0 |  | 19:46 | 0 | 0 | 5507.423 | 19:46 | 2.6142 | 2.403 | 0.21115 | 2.8044e-05 | 0
[13 empty] | 19:46 | 0.9193 | 0.91146 | 0 |  | 19:46 | 0 | 0 | 5507.423 | 19:46 | 2.6148 | 2.4036 | 0.21119 | 2.8052e-05 | 0
[13 empty] | 19:46 | 0.90825 | 0.91146 | 0 |  | 19:46 | 0 | 0 | 5507.423 | 19:46 | 2.6152 | 2.4039 | 0.21123 | 2.8058e-05 | 0
[13 empty] | 19:46 | 0.89743 | 0.91146 | 0 |  | 19:46 | 0 | 0 | 5507.423 | 19:46 | 2.6158 | 2.4045 | 0.21129 | 2.8063e-05 | 0
[13 empty] | 19:46 | 0.88683 | 0.91146 | 0 |  | 19:46 | 0 | 0 | 5507.423 | 19:46 | 2.6162 | 2.4049 | 0.21133 | 2.8069e-05 | 0
[13 empty] | 19:47 | 0.87645 | 0.91146 | 0 |  | 19:47 | 0 | 0 | 5507.423 | 19:47 | 2.6169 | 2.4055 | 0.21136 | 2.8075e-05 | 0
[13 empty] | 19:47 | 0.86628 | 0.91146 | 0 |  | 19:47 | 0 | 0 | 5507.423 | 19:47 | 2.6173 | 2.4058 | 0.2114 | 2.8081e-05 | 0
[13 empty] | 19:47 | 0.85633 | 0.91146 | 0 |  | 19:47 | 0 | 0 | 5507.423 | 19:47 | 2.6179 | 2.4064 | 0.21146 | 2.8086e-05 | 0
[13 empty] | 19:48 | 0.84657 | 0.91146 | 0 |  | 19:48 | 0 | 0 | 5507.423 | 19:48 | 2.6183 | 2.4068 | 0.2115 | 2.809e-05 | 0
[13 empty] | 19:48 | 0.83702 | 0.91146 | 0 |  | 19:48 | 0 | 0 | 5507.423 | 19:48 | 2.6189 | 2.4074 | 0.21154 | 2.8096e-05 | 0
[13 empty] | 19:48 | 0.82766 | 0.91146 | 0 |  | 19:48 | 0 | 0 | 5507.423 | 19:48 | 2.6194 | 2.4078 | 0.21157 | 2.8102e-05 | 0
[13 empty] | 19:48 | 0.8185 | 0.91146 | 0 |  | 19:48 | 0 | 0 | 5507.423 | 19:48 | 2.62 | 2.4083 | 0.21161 | 2.8107e-05 | 0
[13 empty] | 19:48 | 0.80952 | 0.91146 | 0 |  | 19:48 | 0 | 0 | 5507.423 | 19:48 | 2.6204 | 2.4087 | 0.21165 | 2.8113e-05 | 0
[13 empty] | 19:49 | 0.80073 | 0.91146 | 0 |  | 19:49 | 0 | 0 | 5507.423 | 19:49 | 2.6208 | 2.4091 | 0.21169 | 2.8117e-05 | 0
[13 empty] | 19:49 | 0.79211 | 0.91146 | 0 |  | 19:49 | 0 | 0 | 5507.423 | 19:49 | 2.6214 | 2.4097 | 0.21173 | 2.8123e-05 | 0
[13 empty] | 19:49 | 0.78368 | 0.91146 | 0 |  | 19:49 | 0 | 0 | 5507.423 | 19:49 | 2.6218 | 2.4101 | 0.21177 | 2.8128e-05 | 0
[13 empty] | 19:50 | 0.77542 | 0.91146 | 0 |  | 19:50 | 0 | 0 | 5507.423 | 19:50 | 2.6223 | 2.4104 | 0.2118 | 2.8132e-05 | 0
[13 empty] | 19:50 | 0.76733 | 0.91146 | 0 |  | 19:50 | 0 | 0 | 5507.423 | 19:50 | 2.6227 | 2.4108 | 0.21184 | 2.8138e-05 | 0
[13 empty] | 19:50 | 0.7594 | 0.91146 | 0 |  | 19:50 | 0 | 0 | 5507.423 | 19:50 | 2.6233 | 2.4114 | 0.21188 | 2.8144e-05 | 0
[13 empty] | 19:50 | 0.75164 | 0.91146 | 0 |  | 19:50 | 0 | 0 | 5507.423 | 19:50 | 2.6237 | 2.4118 | 0.21192 | 2.8148e-05 | 0
[13 empty] | 19:50 | 0.74403 | 0.91146 | 0 |  | 19:50 | 0 | 0 | 5507.423 | 19:50 | 2.6241 | 2.4122 | 0.21196 | 2.8153e-05 | 0
[13 empty] | 19:51 | 0.73658 | 0.91146 | 0 |  | 19:51 | 0 | 0 | 5507.423 | 19:51 | 2.6246 | 2.4125 | 0.21199 | 2.8157e-05 | 0
[13 empty] | 19:51 | 0.72929 | 0.91146 | 0 |  | 19:51 | 0 | 0 | 5507.423 | 19:51 | 2.625 | 2.4129 | 0.21203 | 2.8163e-05 | 0
[13 empty] | 19:51 | 1.1629 | 0.91146 | 0 |  | 19:51 | 0 | 0 | 5507.423 | 19:51 | 2.6258 | 2.4137 | 0.21209 | 2.817e-05 | 0
[13 empty] | 19:52 | 1.1468 | 0.91146 | 0 |  | 19:52 | 0 | 0 | 5507.423 | 19:52 | 2.6264 | 2.4143 | 0.21215 | 2.8176e-05 | 0
[13 empty] | 19:52 | 1.1311 | 0.91146 | 0 |  | 19:52 | 0 | 0 | 5507.423 | 19:52 | 2.6271 | 2.4148 | 0.2122 | 2.8184e-05 | 0
[13 empty] | 19:52 | 1.1157 | 0.91146 | 0 |  | 19:52 | 0 | 0 | 5507.423 | 19:52 | 2.6279 | 2.4156 | 0.21224 | 2.8191e-05 | 0
[13 empty] | 19:52 | 1.1006 | 0.91146 | 0 |  | 19:52 | 0 | 0 | 5507.423 | 19:52 | 2.6285 | 2.4162 | 0.2123 | 2.8199e-05 | 0
[13 empty] | 19:52 | 1.0859 | 0.91146 | 0 |  | 19:52 | 0 | 0 | 5507.423 | 19:52 | 2.6291 | 2.4167 | 0.21236 | 2.8207e-05 | 0
[13 empty] | 19:53 | 1.0714 | 0.91146 | 0 |  | 19:53 | 0 | 0 | 5507.423 | 19:53 | 2.6298 | 2.4173 | 0.21241 | 2.8212e-05 | 0
[13 empty] | 19:53 | 1.0572 | 0.91146 | 0 |  | 19:53 | 0 | 0 | 5507.423 | 19:53 | 2.6304 | 2.4179 | 0.21247 | 2.822e-05 | 0
[13 empty] | 19:53 | 1.0434 | 0.91146 | 0 |  | 19:53 | 0 | 0 | 5507.423 | 19:53 | 2.631 | 2.4185 | 0.21251 | 2.8226e-05 | 0
[13 empty] | 19:54 | 1.0298 | 0.91146 | 0 |  | 19:54 | 0 | 0 | 5507.423 | 19:54 | 2.6316 | 2.419 | 0.21257 | 2.8233e-05 | 0
[13 empty] | 19:54 | 1.0164 | 0.91146 | 0 |  | 19:54 | 0 | 0 | 5507.423 | 19:54 | 2.6322 | 2.4196 | 0.21261 | 2.8239e-05 | 0
[13 empty] | 19:54 | 1.0034 | 0.91146 | 0 |  | 19:54 | 0 | 0 | 5507.423 | 19:54 | 2.6329 | 2.4202 | 0.21266 | 2.8247e-05 | 0
[13 empty] | 19:54 | 0.99062 | 0.91146 | 0 |  | 19:54 | 0 | 0 | 5507.423 | 19:54 | 2.6335 | 2.4207 | 0.21272 | 2.8253e-05 | 0
[13 empty] | 19:55 | 0.97811 | 0.91146 | 0 |  | 19:55 | 0 | 0 | 5507.423 | 19:55 | 2.6341 | 2.4213 | 0.21276 | 2.8258e-05 | 0
[13 empty] | 19:55 | 0.96585 | 0.91146 | 0 |  | 19:55 | 0 | 0 | 5507.423 | 19:55 | 2.6347 | 2.4219 | 0.21282 | 2.8266e-05 | 0
[13 empty] | 19:55 | 0.95385 | 0.91146 | 0 |  | 19:55 | 0 | 0 | 5507.423 | 19:55 | 2.6352 | 2.4223 | 0.21285 | 2.8272e-05 | 0
[13 empty] | 19:55 | 0.94209 | 0.91146 | 0 |  | 19:55 | 0 | 0 | 5507.423 | 19:55 | 2.6358 | 2.4228 | 0.21289 | 2.8277e-05 | 0
[13 empty] | 19:56 | 0.93058 | 0.91146 | 0 |  | 19:56 | 0 | 0 | 5507.423 | 19:56 | 2.6364 | 2.4234 | 0.21295 | 2.8283e-05 | 0
[13 empty] | 19:56 | 0.9193 | 0.91146 | 0 |  | 19:56 | 0 | 0 | 5507.423 | 19:56 | 2.6368 | 2.4238 | 0.21299 | 2.8289e-05 | 0
[13 empty] | 19:56 | 0.90825 | 0.91146 | 0 |  | 19:56 | 0 | 0 | 5507.423 | 19:56 | 2.6374 | 2.4244 | 0.21303 | 2.8296e-05 | 0
[13 empty] | 19:56 | 0.89743 | 0.91146 | 0 |  | 19:56 | 0 | 0 | 5507.423 | 19:56 | 2.6381 | 2.4249 | 0.21308 | 2.8302e-05 | 0
[13 empty] | 19:56 | 0.88683 | 0.91146 | 0 |  | 19:56 | 0 | 0 | 5507.423 | 19:56 | 2.6385 | 2.4253 | 0.21312 | 2.8308e-05 | 0
[13 empty] | 19:57 | 0.87645 | 0.91146 | 0 |  | 19:57 | 0 | 0 | 5507.423 | 19:57 | 2.6391 | 2.4259 | 0.21316 | 2.8314e-05 | 0
[13 empty] | 19:57 | 0.86628 | 0.91146 | 0 |  | 19:57 | 0 | 0 | 5507.423 | 19:57 | 2.6395 | 2.4263 | 0.2132 | 2.8319e-05 | 0
[13 empty] | 19:57 | 0.85633 | 0.91146 | 0 |  | 19:57 | 0 | 0 | 5507.423 | 19:57 | 2.6401 | 2.4269 | 0.21325 | 2.8323e-05 | 0
[13 empty] | 19:58 | 0.84657 | 0.91146 | 0 |  | 19:58 | 0 | 0 | 5507.423 | 19:58 | 2.6406 | 2.4272 | 0.21329 | 2.8329e-05 | 0
[13 empty] | 19:58 | 0.83702 | 0.91146 | 0 |  | 19:58 | 0 | 0 | 5507.423 | 19:58 | 2.6412 | 2.4278 | 0.21333 | 2.8335e-05 | 0
[13 empty] | 19:58 | 0.82766 | 0.91146 | 0 |  | 19:58 | 0 | 0 | 5507.423 | 19:58 | 2.6416 | 2.4282 | 0.21337 | 2.834e-05 | 0
[13 empty] | 19:58 | 0.8185 | 0.91146 | 0 |  | 19:58 | 0 | 0 | 5507.423 | 19:58 | 2.6422 | 2.4288 | 0.21341 | 2.8346e-05 | 0
[13 empty] | 19:59 | 0.80952 | 0.91146 | 0 |  | 19:59 | 0 | 0 | 5507.423 | 19:59 | 2.6426 | 2.4292 | 0.21345 | 2.8352e-05 | 0
[13 empty] | 19:59 | 0.80073 | 0.91146 | 0 |  | 19:59 | 0 | 0 | 5507.423 | 19:59 | 2.643 | 2.4295 | 0.21348 | 2.8356e-05 | 0
[13 empty] | 19:59 | 0.79211 | 0.91146 | 0 |  | 19:59 | 0 | 0 | 5507.423 | 19:59 | 2.6437 | 2.4301 | 0.21352 | 2.8361e-05 | 0
[13 empty] | 19:59 | 0.78368 | 0.91146 | 0 |  | 19:59 | 0 | 0 | 5507.423 | 19:59 | 2.6441 | 2.4305 | 0.21356 | 2.8367e-05 | 0
[13 empty] | 20:00 | 0.77542 | 0.91146 | 0 |  | 20:00 | 0 | 0 | 5507.423 | 20:00 | 2.6445 | 2.4309 | 0.2136 | 2.8371e-05 | 0
[13 empty] | 20:00 | 0.76733 | 0.91146 | 0 |  | 20:00 | 0 | 0 | 5507.423 | 20:00 | 2.6449 | 2.4313 | 0.21364 | 2.8377e-05 | 0
[13 empty] | 20:00 | 0.7594 | 0.91146 | 0 |  | 20:00 | 0 | 0 | 5507.423 | 20:00 | 2.6455 | 2.4318 | 0.21368 | 2.8381e-05 | 0
[13 empty] | 20:00 | 0.75164 | 0.91146 | 0 |  | 20:00 | 0 | 0 | 5507.423 | 20:00 | 2.6459 | 2.4322 | 0.21371 | 2.8386e-05 | 0
[13 empty] | 20:00 | 0.74403 | 0.91146 | 0 |  | 20:00 | 0 | 0 | 5507.423 | 20:00 | 2.6464 | 2.4326 | 0.21375 | 2.8392e-05 | 0
[13 empty] | 20:01 | 0.73658 | 0.91146 | 0 |  | 20:01 | 0 | 0 | 5507.423 | 20:01 | 2.6468 | 2.433 | 0.21379 | 2.8396e-05 | 0
[13 empty] | 20:01 | 0.72929 | 0.91146 | 0 |  | 20:01 | 0 | 0 | 5507.423 | 20:01 | 2.6472 | 2.4334 | 0.21383 | 2.84e-05 | 0
[13 empty] | 20:01 | 1.1629 | 0.91146 | 0 |  | 20:01 | 0 | 0 | 5507.423 | 20:01 | 2.648 | 2.4341 | 0.21389 | 2.8407e-05 | 0
[13 empty] | 20:02 | 1.1468 | 0.91146 | 0 |  | 20:02 | 0 | 0 | 5507.423 | 20:02 | 2.6487 | 2.4347 | 0.21394 | 2.8415e-05 | 0
[13 empty] | 20:02 | 1.1311 | 0.91146 | 0 |  | 20:02 | 0 | 0 | 5507.423 | 20:02 | 2.6493 | 2.4353 | 0.214 | 2.8423e-05 | 0
[13 empty] | 20:02 | 1.1157 | 0.91146 | 0 |  | 20:02 | 0 | 0 | 5507.423 | 20:02 | 2.6501 | 2.436 | 0.21404 | 2.843e-05 | 0
[13 empty] | 20:02 | 1.1006 | 0.91146 | 0 |  | 20:02 | 0 | 0 | 5507.423 | 20:02 | 2.6507 | 2.4366 | 0.2141 | 2.8438e-05 | 0
[13 empty] | 20:03 | 1.0859 | 0.91146 | 0 |  | 20:03 | 0 | 0 | 5507.423 | 20:03 | 2.6514 | 2.4372 | 0.21415 | 2.8444e-05 | 0
[13 empty] | 20:03 | 1.0714 | 0.91146 | 0 |  | 20:03 | 0 | 0 | 5507.423 | 20:03 | 2.652 | 2.4377 | 0.21421 | 2.8451e-05 | 0
[13 empty] | 20:03 | 1.0572 | 0.91146 | 0 |  | 20:03 | 0 | 0 | 5507.423 | 20:03 | 2.6526 | 2.4383 | 0.21427 | 2.8459e-05 | 0
[13 empty] | 20:03 | 1.0434 | 0.91146 | 0 |  | 20:03 | 0 | 0 | 5507.423 | 20:03 | 2.6532 | 2.4389 | 0.21431 | 2.8465e-05 | 0
[13 empty] | 20:04 | 1.0298 | 0.91146 | 0 |  | 20:04 | 0 | 0 | 5507.423 | 20:04 | 2.6539 | 2.4395 | 0.21436 | 2.8472e-05 | 0
[13 empty] | 20:04 | 1.0164 | 0.91146 | 0 |  | 20:04 | 0 | 0 | 5507.423 | 20:04 | 2.6545 | 2.44 | 0.2144 | 2.8478e-05 | 0
[13 empty] | 20:04 | 1.0034 | 0.91146 | 0 |  | 20:04 | 0 | 0 | 5507.423 | 20:04 | 2.6551 | 2.4406 | 0.21446 | 2.8486e-05 | 0
[13 empty] | 20:04 | 0.99062 | 0.91146 | 0 |  | 20:04 | 0 | 0 | 5507.423 | 20:04 | 2.6557 | 2.4412 | 0.21452 | 2.8491e-05 | 0
[13 empty] | 20:04 | 0.97811 | 0.91146 | 0 |  | 20:04 | 0 | 0 | 5507.423 | 20:04 | 2.6563 | 2.4418 | 0.21455 | 2.8497e-05 | 0
[13 empty] | 20:05 | 0.96585 | 0.91146 | 0 |  | 20:05 | 0 | 0 | 5507.423 | 20:05 | 2.657 | 2.4423 | 0.21461 | 2.8505e-05 | 0
[13 empty] | 20:05 | 0.95385 | 0.91146 | 0 |  | 20:05 | 0 | 0 | 5507.423 | 20:05 | 2.6574 | 2.4427 | 0.21465 | 2.851e-05 | 0
[13 empty] | 20:05 | 0.94209 | 0.91146 | 0 |  | 20:05 | 0 | 0 | 5507.423 | 20:05 | 2.658 | 2.4433 | 0.21469 | 2.8516e-05 | 0
[13 empty] | 20:06 | 0.93058 | 0.91146 | 0 |  | 20:06 | 0 | 0 | 5507.423 | 20:06 | 2.6586 | 2.4439 | 0.21474 | 2.8522e-05 | 0
[13 empty] | 20:06 | 0.9193 | 0.91146 | 0 |  | 20:06 | 0 | 0 | 5507.423 | 20:06 | 2.659 | 2.4442 | 0.21478 | 2.8528e-05 | 0
[13 empty] | 20:06 | 0.90825 | 0.91146 | 0 |  | 20:06 | 0 | 0 | 5507.423 | 20:06 | 2.6597 | 2.4448 | 0.21482 | 2.8533e-05 | 0
[13 empty] | 20:06 | 0.89743 | 0.91146 | 0 |  | 20:06 | 0 | 0 | 5507.423 | 20:06 | 2.6603 | 2.4454 | 0.21488 | 2.8539e-05 | 0
[13 empty] | 20:06 | 0.88683 | 0.91146 | 0 |  | 20:06 | 0 | 0 | 5507.423 | 20:06 | 2.6607 | 2.4458 | 0.21492 | 2.8545e-05 | 0
[13 empty] | 20:07 | 0.87645 | 0.91146 | 0 |  | 20:07 | 0 | 0 | 5507.423 | 20:07 | 2.6613 | 2.4463 | 0.21495 | 2.855e-05 | 0
[13 empty] | 20:07 | 0.86628 | 0.91146 | 0 |  | 20:07 | 0 | 0 | 5507.423 | 20:07 | 2.6617 | 2.4467 | 0.21499 | 2.8556e-05 | 0
[13 empty] | 20:07 | 0.85633 | 0.91146 | 0 |  | 20:07 | 0 | 0 | 5507.423 | 20:07 | 2.6624 | 2.4473 | 0.21505 | 2.8562e-05 | 0
[13 empty] | 20:08 | 0.84657 | 0.91146 | 0 |  | 20:08 | 0 | 0 | 5507.423 | 20:08 | 2.6628 | 2.4477 | 0.21509 | 2.8568e-05 | 0
[13 empty] | 20:08 | 0.83702 | 0.91146 | 0 |  | 20:08 | 0 | 0 | 5507.423 | 20:08 | 2.6634 | 2.4482 | 0.21513 | 2.8573e-05 | 0
[13 empty] | 20:08 | 0.82766 | 0.91146 | 0 |  | 20:08 | 0 | 0 | 5507.423 | 20:08 | 2.6638 | 2.4486 | 0.21516 | 2.8579e-05 | 0
[13 empty] | 20:08 | 0.8185 | 0.91146 | 0 |  | 20:08 | 0 | 0 | 5507.423 | 20:08 | 2.6644 | 2.4492 | 0.2152 | 2.8585e-05 | 0
[13 empty] | 20:08 | 0.80952 | 0.91146 | 0 |  | 20:08 | 0 | 0 | 5507.423 | 20:08 | 2.6649 | 2.4496 | 0.21524 | 2.8589e-05 | 0
[13 empty] | 20:09 | 0.80073 | 0.91146 | 0 |  | 20:09 | 0 | 0 | 5507.423 | 20:09 | 2.6653 | 2.45 | 0.21528 | 2.8594e-05 | 0
[13 empty] | 20:09 | 0.79211 | 0.91146 | 0 |  | 20:09 | 0 | 0 | 5507.423 | 20:09 | 2.6659 | 2.4505 | 0.21532 | 2.86e-05 | 0
[13 empty] | 20:09 | 0.78368 | 0.91146 | 0 |  | 20:09 | 0 | 0 | 5507.423 | 20:09 | 2.6663 | 2.4509 | 0.21536 | 2.8604e-05 | 0
[13 empty] | 20:10 | 0.77542 | 0.91146 | 0 |  | 20:10 | 0 | 0 | 5507.423 | 20:10 | 2.6667 | 2.4513 | 0.21539 | 2.861e-05 | 0
[13 empty] | 20:10 | 0.76733 | 0.91146 | 0 |  | 20:10 | 0 | 0 | 5507.423 | 20:10 | 2.6671 | 2.4517 | 0.21543 | 2.8615e-05 | 0
[13 empty] | 20:10 | 0.7594 | 0.91146 | 0 |  | 20:10 | 0 | 0 | 5507.423 | 20:10 | 2.6678 | 2.4523 | 0.21547 | 2.8619e-05 | 0
[13 empty] | 20:10 | 0.75164 | 0.91146 | 0 |  | 20:10 | 0 | 0 | 5507.423 | 20:10 | 2.6682 | 2.4526 | 0.21551 | 2.8625e-05 | 0
[13 empty] | 20:10 | 0.74403 | 0.91146 | 0 |  | 20:10 | 0 | 0 | 5507.423 | 20:10 | 2.6686 | 2.453 | 0.21555 | 2.8629e-05 | 0
[13 empty] | 20:11 | 0.73658 | 0.91146 | 0 |  | 20:11 | 0 | 0 | 5507.423 | 20:11 | 2.669 | 2.4534 | 0.21558 | 2.8635e-05 | 0
[13 empty] | 20:11 | 0.72929 | 0.91146 | 0 |  | 20:11 | 0 | 0 | 5507.423 | 20:11 | 2.6694 | 2.4538 | 0.21562 | 2.8638e-05 | 0
[13 empty] | 20:11 | 1.1629 | 0.91146 | 0 |  | 20:11 | 0 | 0 | 5507.423 | 20:11 | 2.6703 | 2.4546 | 0.21568 | 2.8646e-05 | 0
[13 empty] | 20:12 | 1.1468 | 0.91146 | 0 |  | 20:12 | 0 | 0 | 5507.423 | 20:12 | 2.6709 | 2.4551 | 0.21574 | 2.8654e-05 | 0
[13 empty] | 20:12 | 1.1311 | 0.91146 | 0 |  | 20:12 | 0 | 0 | 5507.423 | 20:12 | 2.6715 | 2.4557 | 0.21579 | 2.8661e-05 | 0
[13 empty] | 20:12 | 1.1157 | 0.91146 | 0 |  | 20:12 | 0 | 0 | 5507.423 | 20:12 | 2.6721 | 2.4563 | 0.21583 | 2.8669e-05 | 0
[13 empty] | 20:12 | 1.1006 | 0.91146 | 0 |  | 20:12 | 0 | 0 | 5507.423 | 20:12 | 2.673 | 2.457 | 0.21589 | 2.8677e-05 | 0
[13 empty] | 20:12 | 1.0859 | 0.91146 | 0 |  | 20:12 | 0 | 0 | 5507.423 | 20:12 | 2.6736 | 2.4576 | 0.21595 | 2.8682e-05 | 0
[13 empty] | 20:13 | 1.0714 | 0.91146 | 0 |  | 20:13 | 0 | 0 | 5507.423 | 20:13 | 2.6742 | 2.4582 | 0.21601 | 2.869e-05 | 0
[13 empty] | 20:13 | 1.0572 | 0.91146 | 0 |  | 20:13 | 0 | 0 | 5507.423 | 20:13 | 2.6748 | 2.4588 | 0.21606 | 2.8698e-05 | 0
[13 empty] | 20:13 | 1.0434 | 0.91146 | 0 |  | 20:13 | 0 | 0 | 5507.423 | 20:13 | 2.6755 | 2.4593 | 0.2161 | 2.8703e-05 | 0
[13 empty] | 20:14 | 1.0298 | 0.91146 | 0 |  | 20:14 | 0 | 0 | 5507.423 | 20:14 | 2.6761 | 2.4599 | 0.21616 | 2.8711e-05 | 0
[13 empty] | 20:14 | 1.0164 | 0.91146 | 0 |  | 20:14 | 0 | 0 | 5507.423 | 20:14 | 2.6767 | 2.4605 | 0.2162 | 2.8717e-05 | 0
[13 empty] | 20:14 | 1.0034 | 0.91146 | 0 |  | 20:14 | 0 | 0 | 5507.423 | 20:14 | 2.6773 | 2.461 | 0.21625 | 2.8722e-05 | 0
[13 empty] | 20:14 | 0.99062 | 0.91146 | 0 |  | 20:14 | 0 | 0 | 5507.423 | 20:14 | 2.678 | 2.4616 | 0.21631 | 2.873e-05 | 0
[13 empty] | 20:14 | 0.97811 | 0.91146 | 0 |  | 20:14 | 0 | 0 | 5507.423 | 20:14 | 2.6786 | 2.4622 | 0.21635 | 2.8736e-05 | 0
[13 empty] | 20:15 | 0.96585 | 0.91146 | 0 |  | 20:15 | 0 | 0 | 5507.423 | 20:15 | 2.6792 | 2.4628 | 0.21641 | 2.8741e-05 | 0
[13 empty] | 20:15 | 0.95385 | 0.91146 | 0 |  | 20:15 | 0 | 0 | 5507.423 | 20:15 | 2.6796 | 2.4631 | 0.21644 | 2.8749e-05 | 0
[13 empty] | 20:15 | 0.94209 | 0.91146 | 0 |  | 20:15 | 0 | 0 | 5507.423 | 20:15 | 2.6802 | 2.4637 | 0.21648 | 2.8755e-05 | 0
[13 empty] | 20:16 | 0.93058 | 0.91146 | 0 |  | 20:16 | 0 | 0 | 5507.423 | 20:16 | 2.6809 | 2.4643 | 0.21654 | 2.8761e-05 | 0
[13 empty] | 20:16 | 0.9193 | 0.91146 | 0 |  | 20:16 | 0 | 0 | 5507.423 | 20:16 | 2.6813 | 2.4647 | 0.21658 | 2.8766e-05 | 0
[13 empty] | 20:16 | 0.90825 | 0.91146 | 0 |  | 20:16 | 0 | 0 | 5507.423 | 20:16 | 2.6819 | 2.4652 | 0.21662 | 2.8772e-05 | 0
[13 empty] | 20:16 | 0.89743 | 0.91146 | 0 |  | 20:16 | 0 | 0 | 5507.423 | 20:16 | 2.6825 | 2.4658 | 0.21667 | 2.8778e-05 | 0
[13 empty] | 20:16 | 0.88683 | 0.91146 | 0 |  | 20:16 | 0 | 0 | 5507.423 | 20:16 | 2.6829 | 2.4662 | 0.21671 | 2.8783e-05 | 0
[13 empty] | 20:17 | 0.87645 | 0.91146 | 0 |  | 20:17 | 0 | 0 | 5507.423 | 20:17 | 2.6836 | 2.4668 | 0.21675 | 2.8789e-05 | 0
[13 empty] | 20:17 | 0.86628 | 0.91146 | 0 |  | 20:17 | 0 | 0 | 5507.423 | 20:17 | 2.684 | 2.4672 | 0.21679 | 2.8795e-05 | 0
[13 empty] | 20:17 | 0.85633 | 0.91146 | 0 |  | 20:17 | 0 | 0 | 5507.423 | 20:17 | 2.6846 | 2.4677 | 0.21685 | 2.8801e-05 | 0
[13 empty] | 20:18 | 0.84657 | 0.91146 | 0 |  | 20:18 | 0 | 0 | 5507.423 | 20:18 | 2.685 | 2.4681 | 0.21688 | 2.8806e-05 | 0
[13 empty] | 20:18 | 0.83702 | 0.91146 | 0 |  | 20:18 | 0 | 0 | 5507.423 | 20:18 | 2.6856 | 2.4687 | 0.21692 | 2.8812e-05 | 0
[13 empty] | 20:18 | 0.82766 | 0.91146 | 0 |  | 20:18 | 0 | 0 | 5507.423 | 20:18 | 2.6861 | 2.4691 | 0.21696 | 2.8818e-05 | 0
[13 empty] | 20:18 | 0.8185 | 0.91146 | 0 |  | 20:18 | 0 | 0 | 5507.423 | 20:18 | 2.6867 | 2.4696 | 0.217 | 2.8822e-05 | 0
[13 empty] | 20:18 | 0.80952 | 0.91146 | 0 |  | 20:18 | 0 | 0 | 5507.423 | 20:18 | 2.6871 | 2.47 | 0.21704 | 2.8827e-05 | 0
[13 empty] | 20:19 | 0.80073 | 0.91146 | 0 |  | 20:19 | 0 | 0 | 5507.423 | 20:19 | 2.6875 | 2.4704 | 0.21707 | 2.8833e-05 | 0
[13 empty] | 20:19 | 0.79211 | 0.91146 | 0 |  | 20:19 | 0 | 0 | 5507.423 | 20:19 | 2.6881 | 2.471 | 0.21711 | 2.8839e-05 | 0
[13 empty] | 20:19 | 0.78368 | 0.91146 | 0 |  | 20:19 | 0 | 0 | 5507.423 | 20:19 | 2.6885 | 2.4714 | 0.21715 | 2.8843e-05 | 0
[13 empty] | 20:20 | 0.77542 | 0.91146 | 0 |  | 20:20 | 0 | 0 | 5507.423 | 20:20 | 2.689 | 2.4717 | 0.21719 | 2.8848e-05 | 0
[13 empty] | 20:20 | 0.76733 | 0.91146 | 0 |  | 20:20 | 0 | 0 | 5507.423 | 20:20 | 2.6894 | 2.4721 | 0.21723 | 2.8854e-05 | 0
[13 empty] | 20:20 | 0.7594 | 0.91146 | 0 |  | 20:20 | 0 | 0 | 5507.423 | 20:20 | 2.69 | 2.4727 | 0.21727 | 2.8858e-05 | 0
[13 empty] | 20:20 | 0.75164 | 0.91146 | 0 |  | 20:20 | 0 | 0 | 5507.423 | 20:20 | 2.6904 | 2.4731 | 0.2173 | 2.8864e-05 | 0
[13 empty] | 20:20 | 0.74403 | 0.91146 | 0 |  | 20:20 | 0 | 0 | 5507.423 | 20:20 | 2.6908 | 2.4735 | 0.21734 | 2.8868e-05 | 0
[13 empty] | 20:21 | 0.73658 | 0.91146 | 0 |  | 20:21 | 0 | 0 | 5507.423 | 20:21 | 2.6912 | 2.4738 | 0.21738 | 2.8873e-05 | 0
[13 empty] | 20:21 | 0.72929 | 0.91146 | 0 |  | 20:21 | 0 | 0 | 5507.423 | 20:21 | 2.6917 | 2.4742 | 0.21742 | 2.8877e-05 | 0
[13 empty] | 20:21 | 1.1629 | 0.91146 | 0 |  | 20:21 | 0 | 0 | 5507.423 | 20:21 | 2.6925 | 2.475 | 0.21748 | 2.8885e-05 | 0
[13 empty] | 20:22 | 1.1468 | 0.91146 | 0 |  | 20:22 | 0 | 0 | 5507.423 | 20:22 | 2.6931 | 2.4756 | 0.21753 | 2.8892e-05 | 0
[13 empty] | 20:22 | 1.1311 | 0.91146 | 0 |  | 20:22 | 0 | 0 | 5507.423 | 20:22 | 2.6938 | 2.4761 | 0.21759 | 2.89e-05 | 0
[13 empty] | 20:22 | 1.1157 | 0.91146 | 0 |  | 20:22 | 0 | 0 | 5507.423 | 20:22 | 2.6944 | 2.4767 | 0.21763 | 2.8908e-05 | 0
[13 empty] | 20:22 | 1.1006 | 0.91146 | 0 |  | 20:22 | 0 | 0 | 5507.423 | 20:22 | 2.6952 | 2.4775 | 0.21769 | 2.8913e-05 | 0
[13 empty] | 20:22 | 1.0859 | 0.91146 | 0 |  | 20:22 | 0 | 0 | 5507.423 | 20:22 | 2.6958 | 2.478 | 0.21774 | 2.8921e-05 | 0
[13 empty] | 20:23 | 1.0714 | 0.91146 | 0 |  | 20:23 | 0 | 0 | 5507.423 | 20:23 | 2.6964 | 2.4786 | 0.2178 | 2.8929e-05 | 0
[13 empty] | 20:23 | 1.0572 | 0.91146 | 0 |  | 20:23 | 0 | 0 | 5507.423 | 20:23 | 2.6971 | 2.4792 | 0.21786 | 2.8934e-05 | 0
[13 empty] | 20:23 | 1.0434 | 0.91146 | 0 |  | 20:23 | 0 | 0 | 5507.423 | 20:23 | 2.6977 | 2.4798 | 0.2179 | 2.8942e-05 | 0
[13 empty] | 20:24 | 1.0298 | 0.91146 | 0 |  | 20:24 | 0 | 0 | 5507.423 | 20:24 | 2.6983 | 2.4803 | 0.21795 | 2.8948e-05 | 0
[13 empty] | 20:24 | 1.0164 | 0.91146 | 0 |  | 20:24 | 0 | 0 | 5507.423 | 20:24 | 2.6989 | 2.4809 | 0.21799 | 2.8955e-05 | 0
[13 empty] | 20:24 | 1.0034 | 0.91146 | 0 |  | 20:24 | 0 | 0 | 5507.423 | 20:24 | 2.6996 | 2.4815 | 0.21805 | 2.8961e-05 | 0
[13 empty] | 20:24 | 0.99062 | 0.91146 | 0 |  | 20:24 | 0 | 0 | 5507.423 | 20:24 | 2.7002 | 2.4821 | 0.21811 | 2.8969e-05 | 0
[13 empty] | 20:24 | 0.97811 | 0.91146 | 0 |  | 20:24 | 0 | 0 | 5507.423 | 20:24 | 2.7008 | 2.4826 | 0.21814 | 2.8974e-05 | 0
[13 empty] | 20:25 | 0.96585 | 0.91146 | 0 |  | 20:25 | 0 | 0 | 5507.423 | 20:25 | 2.7014 | 2.4832 | 0.2182 | 2.898e-05 | 0
[13 empty] | 20:25 | 0.95385 | 0.91146 | 0 |  | 20:25 | 0 | 0 | 5507.423 | 20:25 | 2.7018 | 2.4836 | 0.21824 | 2.8988e-05 | 0
[13 empty] | 20:25 | 0.94209 | 0.91146 | 0 |  | 20:25 | 0 | 0 | 5507.423 | 20:25 | 2.7025 | 2.4842 | 0.21828 | 2.8994e-05 | 0
[13 empty] | 20:26 | 0.93058 | 0.91146 | 0 |  | 20:26 | 0 | 0 | 5507.423 | 20:26 | 2.7031 | 2.4847 | 0.21834 | 2.8999e-05 | 0
[13 empty] | 20:26 | 0.9193 | 0.91146 | 0 |  | 20:26 | 0 | 0 | 5507.423 | 20:26 | 2.7035 | 2.4851 | 0.21837 | 2.9005e-05 | 0
[13 empty] | 20:26 | 0.90825 | 0.91146 | 0 |  | 20:26 | 0 | 0 | 5507.423 | 20:26 | 2.7041 | 2.4857 | 0.21841 | 2.9011e-05 | 0
[13 empty] | 20:26 | 0.89743 | 0.91146 | 0 |  | 20:26 | 0 | 0 | 5507.423 | 20:26 | 2.7048 | 2.4863 | 0.21847 | 2.9016e-05 | 0
[13 empty] | 20:26 | 0.88683 | 0.91146 | 0 |  | 20:26 | 0 | 0 | 5507.423 | 20:26 | 2.7052 | 2.4866 | 0.21851 | 2.9022e-05 | 0
[13 empty] | 20:27 | 0.87645 | 0.91146 | 0 |  | 20:27 | 0 | 0 | 5507.423 | 20:27 | 2.7058 | 2.4872 | 0.21855 | 2.9028e-05 | 0
[13 empty] | 20:27 | 0.86628 | 0.91146 | 0 |  | 20:27 | 0 | 0 | 5507.423 | 20:27 | 2.7062 | 2.4876 | 0.21858 | 2.9034e-05 | 0
[13 empty] | 20:27 | 0.85633 | 0.91146 | 0 |  | 20:27 | 0 | 0 | 5507.423 | 20:27 | 2.7068 | 2.4882 | 0.21864 | 2.9039e-05 | 0
[13 empty] | 20:27 | 0.84657 | 0.91146 | 0 |  | 20:27 | 0 | 0 | 5507.423 | 20:27 | 2.7073 | 2.4885 | 0.21868 | 2.9045e-05 | 0
[13 empty] | 20:28 | 0.83702 | 0.91146 | 0 |  | 20:28 | 0 | 0 | 5507.423 | 20:28 | 2.7079 | 2.4891 | 0.21872 | 2.9051e-05 | 0
[13 empty] | 20:28 | 0.82766 | 0.91146 | 0 |  | 20:28 | 0 | 0 | 5507.423 | 20:28 | 2.7083 | 2.4895 | 0.21876 | 2.9057e-05 | 0
[13 empty] | 20:28 | 0.8185 | 0.91146 | 0 |  | 20:28 | 0 | 0 | 5507.423 | 20:28 | 2.7089 | 2.4901 | 0.21879 | 2.906e-05 | 0
[13 empty] | 20:28 | 0.80952 | 0.91146 | 0 |  | 20:28 | 0 | 0 | 5507.423 | 20:28 | 2.7093 | 2.4905 | 0.21883 | 2.9066e-05 | 0
[13 empty] | 20:29 | 0.80073 | 0.91146 | 0 |  | 20:29 | 0 | 0 | 5507.423 | 20:29 | 2.7097 | 2.4908 | 0.21887 | 2.9072e-05 | 0
[13 empty] | 20:29 | 0.79211 | 0.91146 | 0 |  | 20:29 | 0 | 0 | 5507.423 | 20:29 | 2.7103 | 2.4914 | 0.21891 | 2.9078e-05 | 0
[13 empty] | 20:29 | 0.78368 | 0.91146 | 0 |  | 20:29 | 0 | 0 | 5507.423 | 20:29 | 2.7108 | 2.4918 | 0.21895 | 2.9081e-05 | 0
[13 empty] | 20:30 | 0.77542 | 0.91146 | 0 |  | 20:30 | 0 | 0 | 5507.423 | 20:30 | 2.7112 | 2.4922 | 0.21898 | 2.9087e-05 | 0
[13 empty] | 20:30 | 0.76733 | 0.91146 | 0 |  | 20:30 | 0 | 0 | 5507.423 | 20:30 | 2.7116 | 2.4926 | 0.21902 | 2.9091e-05 | 0
[13 empty] | 20:30 | 0.7594 | 0.91146 | 0 |  | 20:30 | 0 | 0 | 5507.423 | 20:30 | 2.7122 | 2.4931 | 0.21906 | 2.9097e-05 | 0
[13 empty] | 20:30 | 0.75164 | 0.91146 | 0 |  | 20:30 | 0 | 0 | 5507.423 | 20:30 | 2.7126 | 2.4935 | 0.2191 | 2.9102e-05 | 0
[13 empty] | 20:30 | 0.74403 | 0.91146 | 0 |  | 20:30 | 0 | 0 | 5507.423 | 20:30 | 2.7131 | 2.4939 | 0.21914 | 2.9106e-05 | 0
[13 empty] | 20:31 | 0.73658 | 0.91146 | 0 |  | 20:31 | 0 | 0 | 5507.423 | 20:31 | 2.7135 | 2.4943 | 0.21918 | 2.9112e-05 | 0
[13 empty] | 20:31 | 0.72929 | 0.91146 | 0 |  | 20:31 | 0 | 0 | 5507.423 | 20:31 | 2.7139 | 2.4947 | 0.21921 | 2.9116e-05 | 0
[13 empty] | 20:31 | 1.1629 | 0.91146 | 0 |  | 20:31 | 0 | 0 | 5507.423 | 20:31 | 2.7147 | 2.4954 | 0.21927 | 2.9123e-05 | 0
[13 empty] | 20:31 | 1.1468 | 0.91146 | 0 |  | 20:31 | 0 | 0 | 5507.423 | 20:31 | 2.7154 | 2.496 | 0.21933 | 2.9131e-05 | 0
[13 empty] | 20:32 | 1.1311 | 0.91146 | 0 |  | 20:32 | 0 | 0 | 5507.423 | 20:32 | 2.716 | 2.4966 | 0.21939 | 2.9139e-05 | 0
[13 empty] | 20:32 | 1.1157 | 0.91146 | 0 |  | 20:32 | 0 | 0 | 5507.423 | 20:32 | 2.7166 | 2.4971 | 0.21942 | 2.9146e-05 | 0
[13 empty] | 20:32 | 1.1006 | 0.91146 | 0 |  | 20:32 | 0 | 0 | 5507.423 | 20:32 | 2.7174 | 2.4979 | 0.21948 | 2.9152e-05 | 0
[13 empty] | 20:32 | 1.0859 | 0.91146 | 0 |  | 20:32 | 0 | 0 | 5507.423 | 20:32 | 2.718 | 2.4985 | 0.21954 | 2.916e-05 | 0
[13 empty] | 20:33 | 1.0714 | 0.91146 | 0 |  | 20:33 | 0 | 0 | 5507.423 | 20:33 | 2.7187 | 2.4991 | 0.2196 | 2.9167e-05 | 0
[13 empty] | 20:33 | 1.0572 | 0.91146 | 0 |  | 20:33 | 0 | 0 | 5507.423 | 20:33 | 2.7193 | 2.4996 | 0.21965 | 2.9173e-05 | 0
[13 empty] | 20:33 | 1.0434 | 0.91146 | 0 |  | 20:33 | 0 | 0 | 5507.423 | 20:33 | 2.7199 | 2.5002 | 0.21969 | 2.9181e-05 | 0
[13 empty] | 20:34 | 1.0298 | 0.91146 | 0 |  | 20:34 | 0 | 0 | 5507.423 | 20:34 | 2.7205 | 2.5008 | 0.21975 | 2.9186e-05 | 0
[13 empty] | 20:34 | 1.0164 | 0.91146 | 0 |  | 20:34 | 0 | 0 | 5507.423 | 20:34 | 2.7212 | 2.5013 | 0.21979 | 2.9194e-05 | 0
[13 empty] | 20:34 | 1.0034 | 0.91146 | 0 |  | 20:34 | 0 | 0 | 5507.423 | 20:34 | 2.7218 | 2.5019 | 0.21984 | 2.92e-05 | 0
[13 empty] | 20:34 | 0.99062 | 0.91146 | 0 |  | 20:34 | 0 | 0 | 5507.423 | 20:34 | 2.7224 | 2.5025 | 0.2199 | 2.9207e-05 | 0
[13 empty] | 20:34 | 0.97811 | 0.91146 | 0 |  | 20:34 | 0 | 0 | 5507.423 | 20:34 | 2.723 | 2.5031 | 0.21994 | 2.9213e-05 | 0
[13 empty] | 20:35 | 0.96585 | 0.91146 | 0 |  | 20:35 | 0 | 0 | 5507.423 | 20:35 | 2.7237 | 2.5036 | 0.22 | 2.9219e-05 | 0
[13 empty] | 20:35 | 0.95385 | 0.91146 | 0 |  | 20:35 | 0 | 0 | 5507.423 | 20:35 | 2.7241 | 2.504 | 0.22003 | 2.9225e-05 | 0
[13 empty] | 20:35 | 0.94209 | 0.91146 | 0 |  | 20:35 | 0 | 0 | 5507.423 | 20:35 | 2.7247 | 2.5046 | 0.22007 | 2.9232e-05 | 0
[13 empty] | 20:35 | 0.93058 | 0.91146 | 0 |  | 20:35 | 0 | 0 | 5507.423 | 20:35 | 2.7253 | 2.5052 | 0.22013 | 2.9238e-05 | 0
[13 empty] | 20:36 | 0.9193 | 0.91146 | 0 |  | 20:36 | 0 | 0 | 5507.423 | 20:36 | 2.7257 | 2.5055 | 0.22017 | 2.9244e-05 | 0
[13 empty] | 20:36 | 0.90825 | 0.91146 | 0 |  | 20:36 | 0 | 0 | 5507.423 | 20:36 | 2.7264 | 2.5061 | 0.22021 | 2.9249e-05 | 0
[13 empty] | 20:36 | 0.89743 | 0.91146 | 0 |  | 20:36 | 0 | 0 | 5507.423 | 20:36 | 2.727 | 2.5067 | 0.22026 | 2.9255e-05 | 0
[13 empty] | 20:36 | 0.88683 | 0.91146 | 0 |  | 20:36 | 0 | 0 | 5507.423 | 20:36 | 2.7274 | 2.5071 | 0.2203 | 2.9261e-05 | 0
[13 empty] | 20:37 | 0.87645 | 0.91146 | 0 |  | 20:37 | 0 | 0 | 5507.423 | 20:37 | 2.728 | 2.5076 | 0.22034 | 2.9267e-05 | 0
[13 empty] | 20:37 | 0.86628 | 0.91146 | 0 |  | 20:37 | 0 | 0 | 5507.423 | 20:37 | 2.7284 | 2.508 | 0.22038 | 2.9272e-05 | 0
[13 empty] | 20:37 | 0.85633 | 0.91146 | 0 |  | 20:37 | 0 | 0 | 5507.423 | 20:37 | 2.7291 | 2.5086 | 0.22044 | 2.9278e-05 | 0
[13 empty] | 20:38 | 0.84657 | 0.91146 | 0 |  | 20:38 | 0 | 0 | 5507.423 | 20:38 | 2.7295 | 2.509 | 0.22047 | 2.9284e-05 | 0
[13 empty] | 20:38 | 0.83702 | 0.91146 | 0 |  | 20:38 | 0 | 0 | 5507.423 | 20:38 | 2.7301 | 2.5096 | 0.22051 | 2.929e-05 | 0
[13 empty] | 20:38 | 0.82766 | 0.91146 | 0 |  | 20:38 | 0 | 0 | 5507.423 | 20:38 | 2.7305 | 2.5099 | 0.22055 | 2.9293e-05 | 0
[13 empty] | 20:38 | 0.8185 | 0.91146 | 0 |  | 20:38 | 0 | 0 | 5507.423 | 20:38 | 2.7311 | 2.5105 | 0.22059 | 2.9299e-05 | 0
[13 empty] | 20:38 | 0.80952 | 0.91146 | 0 |  | 20:38 | 0 | 0 | 5507.423 | 20:38 | 2.7315 | 2.5109 | 0.22063 | 2.9305e-05 | 0
[13 empty] | 20:39 | 0.80073 | 0.91146 | 0 |  | 20:39 | 0 | 0 | 5507.423 | 20:39 | 2.732 | 2.5113 | 0.22067 | 2.9311e-05 | 0
[13 empty] | 20:39 | 0.79211 | 0.91146 | 0 |  | 20:39 | 0 | 0 | 5507.423 | 20:39 | 2.7326 | 2.5118 | 0.2207 | 2.9314e-05 | 0
[13 empty] | 20:39 | 0.78368 | 0.91146 | 0 |  | 20:39 | 0 | 0 | 5507.423 | 20:39 | 2.733 | 2.5122 | 0.22074 | 2.932e-05 | 0
[13 empty] | 20:40 | 0.77542 | 0.91146 | 0 |  | 20:40 | 0 | 0 | 5507.423 | 20:40 | 2.7334 | 2.5126 | 0.22078 | 2.9326e-05 | 0
[13 empty] | 20:40 | 0.76733 | 0.91146 | 0 |  | 20:40 | 0 | 0 | 5507.423 | 20:40 | 2.7338 | 2.513 | 0.22082 | 2.933e-05 | 0
[13 empty] | 20:40 | 0.7594 | 0.91146 | 0 |  | 20:40 | 0 | 0 | 5507.423 | 20:40 | 2.7345 | 2.5136 | 0.22086 | 2.9335e-05 | 0
[13 empty] | 20:40 | 0.75164 | 0.91146 | 0 |  | 20:40 | 0 | 0 | 5507.423 | 20:40 | 2.7349 | 2.5139 | 0.22089 | 2.9339e-05 | 0
[13 empty] | 20:40 | 0.74403 | 0.91146 | 0 |  | 20:40 | 0 | 0 | 5507.423 | 20:40 | 2.7353 | 2.5143 | 0.22093 | 2.9345e-05 | 0
[13 empty] | 20:41 | 0.73658 | 0.91146 | 0 |  | 20:41 | 0 | 0 | 5507.423 | 20:41 | 2.7357 | 2.5147 | 0.22097 | 2.9349e-05 | 0
[13 empty] | 20:41 | 0.72929 | 0.91146 | 0 |  | 20:41 | 0 | 0 | 5507.423 | 20:41 | 2.7361 | 2.5151 | 0.22101 | 2.9355e-05 | 0
[13 empty] | 20:41 | 1.1629 | 0.91146 | 0 |  | 20:41 | 0 | 0 | 5507.423 | 20:41 | 2.737 | 2.5159 | 0.22107 | 2.9362e-05 | 0
[13 empty] | 20:42 | 1.1468 | 0.91146 | 0 |  | 20:42 | 0 | 0 | 5507.423 | 20:42 | 2.7376 | 2.5164 | 0.22112 | 2.937e-05 | 0
[13 empty] | 20:42 | 1.1311 | 0.91146 | 0 |  | 20:42 | 0 | 0 | 5507.423 | 20:42 | 2.7382 | 2.517 | 0.22118 | 2.9377e-05 | 0
[13 empty] | 20:42 | 1.1157 | 0.91146 | 0 |  | 20:42 | 0 | 0 | 5507.423 | 20:42 | 2.7388 | 2.5176 | 0.22124 | 2.9383e-05 | 0
[13 empty] | 20:42 | 1.1006 | 0.91146 | 0 |  | 20:42 | 0 | 0 | 5507.423 | 20:42 | 2.7396 | 2.5183 | 0.22128 | 2.9391e-05 | 0
[13 empty] | 20:42 | 1.0859 | 0.91146 | 0 |  | 20:42 | 0 | 0 | 5507.423 | 20:42 | 2.7403 | 2.5189 | 0.22133 | 2.9398e-05 | 0
[13 empty] | 20:43 | 1.0714 | 0.91146 | 0 |  | 20:43 | 0 | 0 | 5507.423 | 20:43 | 2.7409 | 2.5195 | 0.22139 | 2.9406e-05 | 0
[13 empty] | 20:43 | 1.0572 | 0.91146 | 0 |  | 20:43 | 0 | 0 | 5507.423 | 20:43 | 2.7415 | 2.5201 | 0.22145 | 2.9412e-05 | 0
[13 empty] | 20:43 | 1.0434 | 0.91146 | 0 |  | 20:43 | 0 | 0 | 5507.423 | 20:43 | 2.7421 | 2.5206 | 0.22149 | 2.9419e-05 | 0
[13 empty] | 20:44 | 1.0298 | 0.91146 | 0 |  | 20:44 | 0 | 0 | 5507.423 | 20:44 | 2.7428 | 2.5212 | 0.22154 | 2.9425e-05 | 0
[13 empty] | 20:44 | 1.0164 | 0.91146 | 0 |  | 20:44 | 0 | 0 | 5507.423 | 20:44 | 2.7434 | 2.5218 | 0.22158 | 2.9433e-05 | 0
[13 empty] | 20:44 | 1.0034 | 0.91146 | 0 |  | 20:44 | 0 | 0 | 5507.423 | 20:44 | 2.744 | 2.5224 | 0.22164 | 2.9439e-05 | 0
[13 empty] | 20:44 | 0.99062 | 0.91146 | 0 |  | 20:44 | 0 | 0 | 5507.423 | 20:44 | 2.7447 | 2.5229 | 0.2217 | 2.9444e-05 | 0
[13 empty] | 20:44 | 0.97811 | 0.91146 | 0 |  | 20:44 | 0 | 0 | 5507.423 | 20:44 | 2.7453 | 2.5235 | 0.22173 | 2.9452e-05 | 0
[13 empty] | 20:45 | 0.96585 | 0.91146 | 0 |  | 20:45 | 0 | 0 | 5507.423 | 20:45 | 2.7457 | 2.5239 | 0.22179 | 2.9458e-05 | 0
[13 empty] | 20:45 | 0.95385 | 0.91146 | 0 |  | 20:45 | 0 | 0 | 5507.423 | 20:45 | 2.7463 | 2.5245 | 0.22183 | 2.9463e-05 | 0
[13 empty] | 20:45 | 0.94209 | 0.91146 | 0 |  | 20:45 | 0 | 0 | 5507.423 | 20:45 | 2.7469 | 2.525 | 0.22187 | 2.9469e-05 | 0
[13 empty] | 20:46 | 0.93058 | 0.91146 | 0 |  | 20:46 | 0 | 0 | 5507.423 | 20:46 | 2.7476 | 2.5256 | 0.22193 | 2.9477e-05 | 0
[13 empty] | 20:46 | 0.9193 | 0.91146 | 0 |  | 20:46 | 0 | 0 | 5507.423 | 20:46 | 2.748 | 2.526 | 0.22196 | 2.9482e-05 | 0
[13 empty] | 20:46 | 0.90825 | 0.91146 | 0 |  | 20:46 | 0 | 0 | 5507.423 | 20:46 | 2.7486 | 2.5266 | 0.222 | 2.9488e-05 | 0
[13 empty] | 20:46 | 0.89743 | 0.91146 | 0 |  | 20:46 | 0 | 0 | 5507.423 | 20:46 | 2.7492 | 2.5271 | 0.22206 | 2.9494e-05 | 0
[13 empty] | 20:46 | 0.88683 | 0.91146 | 0 |  | 20:46 | 0 | 0 | 5507.423 | 20:46 | 2.7496 | 2.5275 | 0.2221 | 2.95e-05 | 0
[13 empty] | 20:47 | 0.87645 | 0.91146 | 0 |  | 20:47 | 0 | 0 | 5507.423 | 20:47 | 2.7502 | 2.5281 | 0.22214 | 2.9505e-05 | 0
[13 empty] | 20:47 | 0.86628 | 0.91146 | 0 |  | 20:47 | 0 | 0 | 5507.423 | 20:47 | 2.7507 | 2.5285 | 0.22217 | 2.9511e-05 | 0
[13 empty] | 20:47 | 0.85633 | 0.91146 | 0 |  | 20:47 | 0 | 0 | 5507.423 | 20:47 | 2.7513 | 2.529 | 0.22223 | 2.9517e-05 | 0
[13 empty] | 20:48 | 0.84657 | 0.91146 | 0 |  | 20:48 | 0 | 0 | 5507.423 | 20:48 | 2.7517 | 2.5294 | 0.22227 | 2.9523e-05 | 0
[13 empty] | 20:48 | 0.83702 | 0.91146 | 0 |  | 20:48 | 0 | 0 | 5507.423 | 20:48 | 2.7523 | 2.53 | 0.22231 | 2.9526e-05 | 0
[13 empty] | 20:48 | 0.82766 | 0.91146 | 0 |  | 20:48 | 0 | 0 | 5507.423 | 20:48 | 2.7527 | 2.5304 | 0.22235 | 2.9532e-05 | 0
[13 empty] | 20:48 | 0.8185 | 0.91146 | 0 |  | 20:48 | 0 | 0 | 5507.423 | 20:48 | 2.7534 | 2.5309 | 0.22238 | 2.9538e-05 | 0
[13 empty] | 20:48 | 0.80952 | 0.91146 | 0 |  | 20:48 | 0 | 0 | 5507.423 | 20:48 | 2.7538 | 2.5313 | 0.22242 | 2.9544e-05 | 0
[13 empty] | 20:49 | 0.80073 | 0.91146 | 0 |  | 20:49 | 0 | 0 | 5507.423 | 20:49 | 2.7542 | 2.5317 | 0.22246 | 2.9549e-05 | 0
[13 empty] | 20:49 | 0.79211 | 0.91146 | 0 |  | 20:49 | 0 | 0 | 5507.423 | 20:49 | 2.7548 | 2.5323 | 0.2225 | 2.9553e-05 | 0
[13 empty] | 20:49 | 0.78368 | 0.91146 | 0 |  | 20:49 | 0 | 0 | 5507.423 | 20:49 | 2.7552 | 2.5327 | 0.22254 | 2.9559e-05 | 0
[13 empty] | 20:50 | 0.77542 | 0.91146 | 0 |  | 20:50 | 0 | 0 | 5507.423 | 20:50 | 2.7557 | 2.533 | 0.22258 | 2.9565e-05 | 0
[13 empty] | 20:50 | 0.76733 | 0.91146 | 0 |  | 20:50 | 0 | 0 | 5507.423 | 20:50 | 2.7561 | 2.5334 | 0.22261 | 2.9568e-05 | 0
[13 empty] | 20:50 | 0.7594 | 0.91146 | 0 |  | 20:50 | 0 | 0 | 5507.423 | 20:50 | 2.7567 | 2.534 | 0.22265 | 2.9574e-05 | 0
[13 empty] | 20:50 | 0.75164 | 0.91146 | 0 |  | 20:50 | 0 | 0 | 5507.423 | 20:50 | 2.7571 | 2.5344 | 0.22269 | 2.9578e-05 | 0
[13 empty] | 20:50 | 0.74403 | 0.91146 | 0 |  | 20:50 | 0 | 0 | 5507.423 | 20:50 | 2.7575 | 2.5348 | 0.22273 | 2.9584e-05 | 0
[13 empty] | 20:51 | 0.73658 | 0.91146 | 0 |  | 20:51 | 0 | 0 | 5507.423 | 20:51 | 2.7579 | 2.5351 | 0.22277 | 2.9588e-05 | 0
[13 empty] | 20:51 | 0.72929 | 0.91146 | 0 |  | 20:51 | 0 | 0 | 5507.423 | 20:51 | 2.7584 | 2.5355 | 0.2228 | 2.9593e-05 | 0
[13 empty] | 20:51 | 1.1629 | 0.91146 | 0 |  | 20:51 | 0 | 0 | 5507.423 | 20:51 | 2.7592 | 2.5363 | 0.22286 | 2.9601e-05 | 0
[13 empty] | 20:52 | 1.1468 | 0.91146 | 0 |  | 20:52 | 0 | 0 | 5507.423 | 20:52 | 2.7598 | 2.5369 | 0.22292 | 2.9609e-05 | 0
[13 empty] | 20:52 | 1.1311 | 0.91146 | 0 |  | 20:52 | 0 | 0 | 5507.423 | 20:52 | 2.7604 | 2.5374 | 0.22298 | 2.9616e-05 | 0
[13 empty] | 20:52 | 1.1157 | 0.91146 | 0 |  | 20:52 | 0 | 0 | 5507.423 | 20:52 | 2.7611 | 2.538 | 0.22303 | 2.9622e-05 | 0
[13 empty] | 20:52 | 1.1006 | 0.91146 | 0 |  | 20:52 | 0 | 0 | 5507.423 | 20:52 | 2.7619 | 2.5388 | 0.22307 | 2.963e-05 | 0
[13 empty] | 20:52 | 1.0859 | 0.91146 | 0 |  | 20:52 | 0 | 0 | 5507.423 | 20:52 | 2.7625 | 2.5393 | 0.22313 | 2.9637e-05 | 0
[13 empty] | 20:53 | 1.0714 | 0.91146 | 0 |  | 20:53 | 0 | 0 | 5507.423 | 20:53 | 2.7631 | 2.5399 | 0.22319 | 2.9643e-05 | 0
[13 empty] | 20:53 | 1.0572 | 0.91146 | 0 |  | 20:53 | 0 | 0 | 5507.423 | 20:53 | 2.7638 | 2.5405 | 0.22324 | 2.9651e-05 | 0
[13 empty] | 20:53 | 1.0434 | 0.91146 | 0 |  | 20:53 | 0 | 0 | 5507.423 | 20:53 | 2.7644 | 2.5411 | 0.22328 | 2.9658e-05 | 0
[13 empty] | 20:54 | 1.0298 | 0.91146 | 0 |  | 20:54 | 0 | 0 | 5507.423 | 20:54 | 2.765 | 2.5416 | 0.22334 | 2.9664e-05 | 0
[13 empty] | 20:54 | 1.0164 | 0.91146 | 0 |  | 20:54 | 0 | 0 | 5507.423 | 20:54 | 2.7656 | 2.5422 | 0.22338 | 2.967e-05 | 0
[13 empty] | 20:54 | 1.0034 | 0.91146 | 0 |  | 20:54 | 0 | 0 | 5507.423 | 20:54 | 2.7663 | 2.5428 | 0.22343 | 2.9677e-05 | 0
[13 empty] | 20:54 | 0.99062 | 0.91146 | 0 |  | 20:54 | 0 | 0 | 5507.423 | 20:54 | 2.7669 | 2.5434 | 0.22349 | 2.9683e-05 | 0
[13 empty] | 20:54 | 0.97811 | 0.91146 | 0 |  | 20:54 | 0 | 0 | 5507.423 | 20:54 | 2.7675 | 2.5439 | 0.22353 | 2.9691e-05 | 0
[13 empty] | 20:55 | 0.96585 | 0.91146 | 0 |  | 20:55 | 0 | 0 | 5507.423 | 20:55 | 2.7679 | 2.5443 | 0.22359 | 2.9696e-05 | 0
[13 empty] | 20:55 | 0.95385 | 0.91146 | 0 |  | 20:55 | 0 | 0 | 5507.423 | 20:55 | 2.7685 | 2.5449 | 0.22363 | 2.9702e-05 | 0
[13 empty] | 20:55 | 0.94209 | 0.91146 | 0 |  | 20:55 | 0 | 0 | 5507.423 | 20:55 | 2.7692 | 2.5455 | 0.22366 | 2.9708e-05 | 0
[13 empty] | 20:56 | 0.93058 | 0.91146 | 0 |  | 20:56 | 0 | 0 | 5507.423 | 20:56 | 2.7698 | 2.546 | 0.22372 | 2.9714e-05 | 0
[13 empty] | 20:56 | 0.9193 | 0.91146 | 0 |  | 20:56 | 0 | 0 | 5507.423 | 20:56 | 2.7702 | 2.5464 | 0.22376 | 2.9721e-05 | 0
[13 empty] | 20:56 | 0.90825 | 0.91146 | 0 |  | 20:56 | 0 | 0 | 5507.423 | 20:56 | 2.7708 | 2.547 | 0.2238 | 2.9727e-05 | 0
[13 empty] | 20:56 | 0.89743 | 0.91146 | 0 |  | 20:56 | 0 | 0 | 5507.423 | 20:56 | 2.7714 | 2.5476 | 0.22385 | 2.9733e-05 | 0
[13 empty] | 20:56 | 0.88683 | 0.91146 | 0 |  | 20:56 | 0 | 0 | 5507.423 | 20:56 | 2.7719 | 2.5479 | 0.22389 | 2.9738e-05 | 0
[13 empty] | 20:57 | 0.87645 | 0.91146 | 0 |  | 20:57 | 0 | 0 | 5507.423 | 20:57 | 2.7725 | 2.5485 | 0.22393 | 2.9744e-05 | 0
[13 empty] | 20:57 | 0.86628 | 0.91146 | 0 |  | 20:57 | 0 | 0 | 5507.423 | 20:57 | 2.7729 | 2.5489 | 0.22397 | 2.975e-05 | 0
[13 empty] | 20:57 | 0.85633 | 0.91146 | 0 |  | 20:57 | 0 | 0 | 5507.423 | 20:57 | 2.7735 | 2.5495 | 0.22403 | 2.9756e-05 | 0
[13 empty] | 20:58 | 0.84657 | 0.91146 | 0 |  | 20:58 | 0 | 0 | 5507.423 | 20:58 | 2.7739 | 2.5499 | 0.22406 | 2.9759e-05 | 0
[13 empty] | 20:58 | 0.83702 | 0.91146 | 0 |  | 20:58 | 0 | 0 | 5507.423 | 20:58 | 2.7746 | 2.5504 | 0.2241 | 2.9765e-05 | 0
[13 empty] | 20:58 | 0.82766 | 0.91146 | 0 |  | 20:58 | 0 | 0 | 5507.423 | 20:58 | 2.775 | 2.5508 | 0.22414 | 2.9771e-05 | 0
[13 empty] | 20:58 | 0.8185 | 0.91146 | 0 |  | 20:58 | 0 | 0 | 5507.423 | 20:58 | 2.7756 | 2.5514 | 0.22418 | 2.9777e-05 | 0
[13 empty] | 20:58 | 0.80952 | 0.91146 | 0 |  | 20:58 | 0 | 0 | 5507.423 | 20:58 | 2.776 | 2.5518 | 0.22422 | 2.9782e-05 | 0
[13 empty] | 20:59 | 0.80073 | 0.91146 | 0 |  | 20:59 | 0 | 0 | 5507.423 | 20:59 | 2.7764 | 2.5521 | 0.22426 | 2.9786e-05 | 0
[13 empty] | 20:59 | 0.79211 | 0.91146 | 0 |  | 20:59 | 0 | 0 | 5507.423 | 20:59 | 2.777 | 2.5527 | 0.22429 | 2.9792e-05 | 0
[13 empty] | 20:59 | 0.78368 | 0.91146 | 0 |  | 20:59 | 0 | 0 | 5507.423 | 20:59 | 2.7775 | 2.5531 | 0.22433 | 2.9798e-05 | 0
[13 empty] | 21:00 | 0.77542 | 0.91146 | 0 |  | 21:00 | 0 | 0 | 5507.423 | 21:00 | 2.7779 | 2.5535 | 0.22437 | 2.9801e-05 | 0
[13 empty] | 21:00 | 0.76733 | 0.91146 | 0 |  | 21:00 | 0 | 0 | 5507.423 | 21:00 | 2.7783 | 2.5539 | 0.22441 | 2.9807e-05 | 0
[13 empty] | 21:00 | 0.7594 | 0.91146 | 0 |  | 21:00 | 0 | 0 | 5507.423 | 21:00 | 2.7789 | 2.5544 | 0.22445 | 2.9813e-05 | 0
[13 empty] | 21:00 | 0.75164 | 0.91146 | 0 |  | 21:00 | 0 | 0 | 5507.423 | 21:00 | 2.7793 | 2.5548 | 0.22448 | 2.9817e-05 | 0
[13 empty] | 21:00 | 0.74403 | 0.91146 | 0 |  | 21:00 | 0 | 0 | 5507.423 | 21:00 | 2.7798 | 2.5552 | 0.22452 | 2.9822e-05 | 0
[13 empty] | 21:01 | 0.73658 | 0.91146 | 0 |  | 21:01 | 0 | 0 | 5507.423 | 21:01 | 2.7802 | 2.5556 | 0.22456 | 2.9826e-05 | 0
[13 empty] | 21:01 | 0.72929 | 0.91146 | 0 |  | 21:01 | 0 | 0 | 5507.423 | 21:01 | 2.7806 | 2.556 | 0.2246 | 2.9832e-05 | 0
[13 empty] | 21:01 | 1.1629 | 0.91146 | 0 |  | 21:01 | 0 | 0 | 5507.423 | 21:01 | 2.7814 | 2.5567 | 0.22466 | 2.984e-05 | 0
[13 empty] | 21:02 | 1.1468 | 0.91146 | 0 |  | 21:02 | 0 | 0 | 5507.423 | 21:02 | 2.782 | 2.5573 | 0.22471 | 2.9847e-05 | 0
[13 empty] | 21:02 | 1.1311 | 0.91146 | 0 |  | 21:02 | 0 | 0 | 5507.423 | 21:02 | 2.7827 | 2.5579 | 0.22477 | 2.9853e-05 | 0
[13 empty] | 21:02 | 1.1157 | 0.91146 | 0 |  | 21:02 | 0 | 0 | 5507.423 | 21:02 | 2.7833 | 2.5584 | 0.22483 | 2.9861e-05 | 0
[13 empty] | 21:02 | 1.1006 | 0.91146 | 0 |  | 21:02 | 0 | 0 | 5507.423 | 21:02 | 2.7841 | 2.5592 | 0.22487 | 2.9868e-05 | 0
[13 empty] | 21:02 | 1.0859 | 0.91146 | 0 |  | 21:02 | 0 | 0 | 5507.423 | 21:02 | 2.7847 | 2.5598 | 0.22492 | 2.9876e-05 | 0
[13 empty] | 21:03 | 1.0714 | 0.91146 | 0 |  | 21:03 | 0 | 0 | 5507.423 | 21:03 | 2.7854 | 2.5604 | 0.22498 | 2.9882e-05 | 0
[13 empty] | 21:03 | 1.0572 | 0.91146 | 0 |  | 21:03 | 0 | 0 | 5507.423 | 21:03 | 2.786 | 2.5609 | 0.22504 | 2.9889e-05 | 0
[13 empty] | 21:03 | 1.0434 | 0.91146 | 0 |  | 21:03 | 0 | 0 | 5507.423 | 21:03 | 2.7866 | 2.5615 | 0.22508 | 2.9895e-05 | 0
[13 empty] | 21:04 | 1.0298 | 0.91146 | 0 |  | 21:04 | 0 | 0 | 5507.423 | 21:04 | 2.7872 | 2.5621 | 0.22513 | 2.9903e-05 | 0
[13 empty] | 21:04 | 1.0164 | 0.91146 | 0 |  | 21:04 | 0 | 0 | 5507.423 | 21:04 | 2.7879 | 2.5626 | 0.22517 | 2.9908e-05 | 0
[13 empty] | 21:04 | 1.0034 | 0.91146 | 0 |  | 21:04 | 0 | 0 | 5507.423 | 21:04 | 2.7885 | 2.5632 | 0.22523 | 2.9916e-05 | 0
[13 empty] | 21:04 | 0.99062 | 0.91146 | 0 |  | 21:04 | 0 | 0 | 5507.423 | 21:04 | 2.7891 | 2.5638 | 0.22529 | 2.9922e-05 | 0
[13 empty] | 21:04 | 0.97811 | 0.91146 | 0 |  | 21:04 | 0 | 0 | 5507.423 | 21:04 | 2.7897 | 2.5644 | 0.22533 | 2.9927e-05 | 0
[13 empty] | 21:05 | 0.96585 | 0.91146 | 0 |  | 21:05 | 0 | 0 | 5507.423 | 21:05 | 2.7902 | 2.5648 | 0.22538 | 2.9935e-05 | 0
[13 empty] | 21:05 | 0.95385 | 0.91146 | 0 |  | 21:05 | 0 | 0 | 5507.423 | 21:05 | 2.7908 | 2.5653 | 0.22542 | 2.9941e-05 | 0
[13 empty] | 21:05 | 0.94209 | 0.91146 | 0 |  | 21:05 | 0 | 0 | 5507.423 | 21:05 | 2.7914 | 2.5659 | 0.22546 | 2.9947e-05 | 0
[13 empty] | 21:06 | 0.93058 | 0.91146 | 0 |  | 21:06 | 0 | 0 | 5507.423 | 21:06 | 2.792 | 2.5665 | 0.22552 | 2.9952e-05 | 0
[13 empty] | 21:06 | 0.9193 | 0.91146 | 0 |  | 21:06 | 0 | 0 | 5507.423 | 21:06 | 2.7924 | 2.5669 | 0.22555 | 2.9958e-05 | 0
[13 empty] | 21:06 | 0.90825 | 0.91146 | 0 |  | 21:06 | 0 | 0 | 5507.423 | 21:06 | 2.793 | 2.5674 | 0.22559 | 2.9966e-05 | 0
[13 empty] | 21:06 | 0.89743 | 0.91146 | 0 |  | 21:06 | 0 | 0 | 5507.423 | 21:06 | 2.7937 | 2.568 | 0.22565 | 2.9971e-05 | 0
[13 empty] | 21:06 | 0.88683 | 0.91146 | 0 |  | 21:06 | 0 | 0 | 5507.423 | 21:06 | 2.7941 | 2.5684 | 0.22569 | 2.9977e-05 | 0
[13 empty] | 21:07 | 0.87645 | 0.91146 | 0 |  | 21:07 | 0 | 0 | 5507.423 | 21:07 | 2.7947 | 2.569 | 0.22573 | 2.9983e-05 | 0
[13 empty] | 21:07 | 0.86628 | 0.91146 | 0 |  | 21:07 | 0 | 0 | 5507.423 | 21:07 | 2.7951 | 2.5693 | 0.22578 | 2.9989e-05 | 0
[13 empty] | 21:07 | 0.85633 | 0.91146 | 0 |  | 21:07 | 0 | 0 | 5507.423 | 21:07 | 2.7958 | 2.5699 | 0.22582 | 2.9992e-05 | 0
[13 empty] | 21:08 | 0.84657 | 0.91146 | 0 |  | 21:08 | 0 | 0 | 5507.423 | 21:08 | 2.7962 | 2.5703 | 0.22586 | 2.9998e-05 | 0
[13 empty] | 21:08 | 0.83702 | 0.91146 | 0 |  | 21:08 | 0 | 0 | 5507.423 | 21:08 | 2.7968 | 2.5709 | 0.2259 | 3.0004e-05 | 0
[13 empty] | 21:08 | 0.82766 | 0.91146 | 0 |  | 21:08 | 0 | 0 | 5507.423 | 21:08 | 2.7972 | 2.5712 | 0.22594 | 3.001e-05 | 0
[13 empty] | 21:08 | 0.8185 | 0.91146 | 0 |  | 21:08 | 0 | 0 | 5507.423 | 21:08 | 2.7978 | 2.5718 | 0.22597 | 3.0015e-05 | 0
[13 empty] | 21:08 | 0.80952 | 0.91146 | 0 |  | 21:08 | 0 | 0 | 5507.423 | 21:08 | 2.7982 | 2.5722 | 0.22601 | 3.0021e-05 | 0
[13 empty] | 21:09 | 0.80073 | 0.91146 | 0 |  | 21:09 | 0 | 0 | 5507.423 | 21:09 | 2.7987 | 2.5726 | 0.22605 | 3.0025e-05 | 0
[13 empty] | 21:09 | 0.79211 | 0.91146 | 0 |  | 21:09 | 0 | 0 | 5507.423 | 21:09 | 2.7993 | 2.5732 | 0.22609 | 3.0031e-05 | 0
[13 empty] | 21:09 | 0.78368 | 0.91146 | 0 |  | 21:09 | 0 | 0 | 5507.423 | 21:09 | 2.7997 | 2.5735 | 0.22613 | 3.0036e-05 | 0
[13 empty] | 21:10 | 0.77542 | 0.91146 | 0 |  | 21:10 | 0 | 0 | 5507.423 | 21:10 | 2.8001 | 2.5739 | 0.22617 | 3.004e-05 | 0
[13 empty] | 21:10 | 0.76733 | 0.91146 | 0 |  | 21:10 | 0 | 0 | 5507.423 | 21:10 | 2.8005 | 2.5743 | 0.2262 | 3.0046e-05 | 0
[13 empty] | 21:10 | 0.7594 | 0.91146 | 0 |  | 21:10 | 0 | 0 | 5507.423 | 21:10 | 2.801 | 2.5747 | 0.22624 | 3.005e-05 | 0
[13 empty] | 21:10 | 0.75164 | 0.91146 | 0 |  | 21:10 | 0 | 0 | 5507.423 | 21:10 | 2.8016 | 2.5753 | 0.22628 | 3.0055e-05 | 0
[13 empty] | 21:10 | 0.74403 | 0.91146 | 0 |  | 21:10 | 0 | 0 | 5507.423 | 21:10 | 2.802 | 2.5756 | 0.22632 | 3.0061e-05 | 0
[13 empty] | 21:11 | 0.73658 | 0.91146 | 0 |  | 21:11 | 0 | 0 | 5507.423 | 21:11 | 2.8024 | 2.576 | 0.22636 | 3.0065e-05 | 0
[13 empty] | 21:11 | 0.72929 | 0.91146 | 0 |  | 21:11 | 0 | 0 | 5507.423 | 21:11 | 2.8028 | 2.5764 | 0.22639 | 3.0071e-05 | 0
[13 empty] | 21:11 | 1.1629 | 0.91146 | 0 |  | 21:11 | 0 | 0 | 5507.423 | 21:11 | 2.8036 | 2.5772 | 0.22645 | 3.0076e-05 | 0
[13 empty] | 21:12 | 1.1468 | 0.91146 | 0 |  | 21:12 | 0 | 0 | 5507.423 | 21:12 | 2.8043 | 2.5777 | 0.22651 | 3.0084e-05 | 0
[13 empty] | 21:12 | 1.1311 | 0.91146 | 0 |  | 21:12 | 0 | 0 | 5507.423 | 21:12 | 2.8049 | 2.5783 | 0.22657 | 3.0092e-05 | 0
[13 empty] | 21:12 | 1.1157 | 0.91146 | 0 |  | 21:12 | 0 | 0 | 5507.423 | 21:12 | 2.8055 | 2.5789 | 0.22662 | 3.0099e-05 | 0
[13 empty] | 21:12 | 1.1006 | 0.91146 | 0 |  | 21:12 | 0 | 0 | 5507.423 | 21:12 | 2.8063 | 2.5796 | 0.22666 | 3.0107e-05 | 0
[13 empty] | 21:12 | 1.0859 | 0.91146 | 0 |  | 21:12 | 0 | 0 | 5507.423 | 21:12 | 2.807 | 2.5802 | 0.22672 | 3.0113e-05 | 0
[13 empty] | 21:13 | 1.0714 | 0.91146 | 0 |  | 21:13 | 0 | 0 | 5507.423 | 21:13 | 2.8076 | 2.5808 | 0.22678 | 3.012e-05 | 0
[13 empty] | 21:13 | 1.0572 | 0.91146 | 0 |  | 21:13 | 0 | 0 | 5507.423 | 21:13 | 2.8082 | 2.5814 | 0.22683 | 3.0128e-05 | 0
[13 empty] | 21:13 | 1.0434 | 0.91146 | 0 |  | 21:13 | 0 | 0 | 5507.423 | 21:13 | 2.8088 | 2.5819 | 0.22687 | 3.0134e-05 | 0
[13 empty] | 21:14 | 1.0298 | 0.91146 | 0 |  | 21:14 | 0 | 0 | 5507.423 | 21:14 | 2.8095 | 2.5825 | 0.22693 | 3.0141e-05 | 0
[13 empty] | 21:14 | 1.0164 | 0.91146 | 0 |  | 21:14 | 0 | 0 | 5507.423 | 21:14 | 2.8101 | 2.5831 | 0.22697 | 3.0147e-05 | 0
[13 empty] | 21:14 | 1.0034 | 0.91146 | 0 |  | 21:14 | 0 | 0 | 5507.423 | 21:14 | 2.8107 | 2.5837 | 0.22702 | 3.0155e-05 | 0
[13 empty] | 21:14 | 0.99062 | 0.91146 | 0 |  | 21:14 | 0 | 0 | 5507.423 | 21:14 | 2.8113 | 2.5842 | 0.22708 | 3.016e-05 | 0
[13 empty] | 21:14 | 0.97811 | 0.91146 | 0 |  | 21:14 | 0 | 0 | 5507.423 | 21:14 | 2.812 | 2.5848 | 0.22712 | 3.0166e-05 | 0
[13 empty] | 21:15 | 0.96585 | 0.91146 | 0 |  | 21:15 | 0 | 0 | 5507.423 | 21:15 | 2.8124 | 2.5852 | 0.22718 | 3.0174e-05 | 0
[13 empty] | 21:15 | 0.95385 | 0.91146 | 0 |  | 21:15 | 0 | 0 | 5507.423 | 21:15 | 2.813 | 2.5858 | 0.22722 | 3.018e-05 | 0
[13 empty] | 21:15 | 0.94209 | 0.91146 | 0 |  | 21:15 | 0 | 0 | 5507.423 | 21:15 | 2.8136 | 2.5863 | 0.22725 | 3.0185e-05 | 0
[13 empty] | 21:16 | 0.93058 | 0.91146 | 0 |  | 21:16 | 0 | 0 | 5507.423 | 21:16 | 2.8142 | 2.5869 | 0.22731 | 3.0191e-05 | 0
[13 empty] | 21:16 | 0.9193 | 0.91146 | 0 |  | 21:16 | 0 | 0 | 5507.423 | 21:16 | 2.8147 | 2.5873 | 0.22735 | 3.0197e-05 | 0
[13 empty] | 21:16 | 0.90825 | 0.91146 | 0 |  | 21:16 | 0 | 0 | 5507.423 | 21:16 | 2.8153 | 2.5879 | 0.22739 | 3.0203e-05 | 0
[13 empty] | 21:16 | 0.89743 | 0.91146 | 0 |  | 21:16 | 0 | 0 | 5507.423 | 21:16 | 2.8159 | 2.5884 | 0.22745 | 3.0208e-05 | 0
[13 empty] | 21:16 | 0.88683 | 0.91146 | 0 |  | 21:16 | 0 | 0 | 5507.423 | 21:16 | 2.8163 | 2.5888 | 0.22748 | 3.0216e-05 | 0
[13 empty] | 21:17 | 0.87645 | 0.91146 | 0 |  | 21:17 | 0 | 0 | 5507.423 | 21:17 | 2.8169 | 2.5894 | 0.22752 | 3.022e-05 | 0
[13 empty] | 21:17 | 0.86628 | 0.91146 | 0 |  | 21:17 | 0 | 0 | 5507.423 | 21:17 | 2.8174 | 2.5898 | 0.22758 | 3.0225e-05 | 0
[13 empty] | 21:17 | 0.85633 | 0.91146 | 0 |  | 21:17 | 0 | 0 | 5507.423 | 21:17 | 2.818 | 2.5903 | 0.22762 | 3.0231e-05 | 0
[13 empty] | 21:18 | 0.84657 | 0.91146 | 0 |  | 21:18 | 0 | 0 | 5507.423 | 21:18 | 2.8184 | 2.5907 | 0.22766 | 3.0237e-05 | 0
[13 empty] | 21:18 | 0.83702 | 0.91146 | 0 |  | 21:18 | 0 | 0 | 5507.423 | 21:18 | 2.819 | 2.5913 | 0.22769 | 3.0243e-05 | 0
[13 empty] | 21:18 | 0.82766 | 0.91146 | 0 |  | 21:18 | 0 | 0 | 5507.423 | 21:18 | 2.8194 | 2.5917 | 0.22773 | 3.0248e-05 | 0
[13 empty] | 21:18 | 0.8185 | 0.91146 | 0 |  | 21:18 | 0 | 0 | 5507.423 | 21:18 | 2.8199 | 2.5921 | 0.22777 | 3.0254e-05 | 0
[13 empty] | 21:18 | 0.80952 | 0.91146 | 0 |  | 21:18 | 0 | 0 | 5507.423 | 21:18 | 2.8205 | 2.5926 | 0.22781 | 3.0258e-05 | 0
[13 empty] | 21:19 | 0.80073 | 0.91146 | 0 |  | 21:19 | 0 | 0 | 5507.423 | 21:19 | 2.8209 | 2.593 | 0.22785 | 3.0264e-05 | 0
[13 empty] | 21:19 | 0.79211 | 0.91146 | 0 |  | 21:19 | 0 | 0 | 5507.423 | 21:19 | 2.8213 | 2.5934 | 0.22788 | 3.0269e-05 | 0
[13 empty] | 21:19 | 0.78368 | 0.91146 | 0 |  | 21:19 | 0 | 0 | 5507.423 | 21:19 | 2.8219 | 2.594 | 0.22792 | 3.0275e-05 | 0
[13 empty] | 21:20 | 0.77542 | 0.91146 | 0 |  | 21:20 | 0 | 0 | 5507.423 | 21:20 | 2.8223 | 2.5944 | 0.22796 | 3.0279e-05 | 0
[13 empty] | 21:20 | 0.76733 | 0.91146 | 0 |  | 21:20 | 0 | 0 | 5507.423 | 21:20 | 2.8228 | 2.5947 | 0.228 | 3.0285e-05 | 0
[13 empty] | 21:20 | 0.7594 | 0.91146 | 0 |  | 21:20 | 0 | 0 | 5507.423 | 21:20 | 2.8232 | 2.5951 | 0.22804 | 3.0288e-05 | 0
[13 empty] | 21:20 | 0.75164 | 0.91146 | 0 |  | 21:20 | 0 | 0 | 5507.423 | 21:20 | 2.8238 | 2.5957 | 0.22808 | 3.0294e-05 | 0
[13 empty] | 21:20 | 0.74403 | 0.91146 | 0 |  | 21:20 | 0 | 0 | 5507.423 | 21:20 | 2.8242 | 2.5961 | 0.22811 | 3.0298e-05 | 0
[13 empty] | 21:21 | 0.73658 | 0.91146 | 0 |  | 21:21 | 0 | 0 | 5507.423 | 21:21 | 2.8246 | 2.5965 | 0.22815 | 3.0304e-05 | 0
[13 empty] | 21:21 | 0.72929 | 0.91146 | 0 |  | 21:21 | 0 | 0 | 5507.423 | 21:21 | 2.8251 | 2.5968 | 0.22819 | 3.0308e-05 | 0
[13 empty] | 21:21 | 1.1629 | 0.91146 | 0 |  | 21:21 | 0 | 0 | 5507.423 | 21:21 | 2.8257 | 2.5974 | 0.22825 | 3.0315e-05 | 0
[13 empty] | 21:22 | 1.1468 | 0.91146 | 0 |  | 21:22 | 0 | 0 | 5507.423 | 21:22 | 2.8265 | 2.5982 | 0.2283 | 3.0323e-05 | 0
[13 empty] | 21:22 | 1.1311 | 0.91146 | 0 |  | 21:22 | 0 | 0 | 5507.423 | 21:22 | 2.8271 | 2.5987 | 0.22836 | 3.033e-05 | 0
[13 empty] | 21:22 | 1.1157 | 0.91146 | 0 |  | 21:22 | 0 | 0 | 5507.423 | 21:22 | 2.8278 | 2.5993 | 0.22842 | 3.0338e-05 | 0
[13 empty] | 21:22 | 1.1006 | 0.91146 | 0 |  | 21:22 | 0 | 0 | 5507.423 | 21:22 | 2.8286 | 2.6001 | 0.22846 | 3.0346e-05 | 0
[13 empty] | 21:22 | 1.0859 | 0.91146 | 0 |  | 21:22 | 0 | 0 | 5507.423 | 21:22 | 2.8292 | 2.6007 | 0.22851 | 3.0351e-05 | 0
[13 empty] | 21:23 | 1.0714 | 0.91146 | 0 |  | 21:23 | 0 | 0 | 5507.423 | 21:23 | 2.8298 | 2.6012 | 0.22857 | 3.0359e-05 | 0
[13 empty] | 21:23 | 1.0572 | 0.91146 | 0 |  | 21:23 | 0 | 0 | 5507.423 | 21:23 | 2.8305 | 2.6018 | 0.22863 | 3.0367e-05 | 0
[13 empty] | 21:23 | 1.0434 | 0.91146 | 0 |  | 21:23 | 0 | 0 | 5507.423 | 21:23 | 2.8311 | 2.6024 | 0.22867 | 3.0372e-05 | 0
[13 empty] | 21:24 | 1.0298 | 0.91146 | 0 |  | 21:24 | 0 | 0 | 5507.423 | 21:24 | 2.8317 | 2.6029 | 0.22872 | 3.038e-05 | 0
[13 empty] | 21:24 | 1.0164 | 0.91146 | 0 |  | 21:24 | 0 | 0 | 5507.423 | 21:24 | 2.8323 | 2.6035 | 0.22876 | 3.0386e-05 | 0
[13 empty] | 21:24 | 1.0034 | 0.91146 | 0 |  | 21:24 | 0 | 0 | 5507.423 | 21:24 | 2.8329 | 2.6041 | 0.22882 | 3.0392e-05 | 0
[13 empty] | 21:24 | 0.99062 | 0.91146 | 0 |  | 21:24 | 0 | 0 | 5507.423 | 21:24 | 2.8336 | 2.6047 | 0.22888 | 3.0399e-05 | 0
[13 empty] | 21:25 | 0.97811 | 0.91146 | 0 |  | 21:25 | 0 | 0 | 5507.423 | 21:25 | 2.8342 | 2.6052 | 0.22892 | 3.0405e-05 | 0
[13 empty] | 21:25 | 0.96585 | 0.91146 | 0 |  | 21:25 | 0 | 0 | 5507.423 | 21:25 | 2.8346 | 2.6056 | 0.22897 | 3.0411e-05 | 0
[13 empty] | 21:25 | 0.95385 | 0.91146 | 0 |  | 21:25 | 0 | 0 | 5507.423 | 21:25 | 2.8352 | 2.6062 | 0.22901 | 3.0418e-05 | 0
[13 empty] | 21:25 | 0.94209 | 0.91146 | 0 |  | 21:25 | 0 | 0 | 5507.423 | 21:25 | 2.8358 | 2.6068 | 0.22905 | 3.0424e-05 | 0
[13 empty] | 21:26 | 0.93058 | 0.91146 | 0 |  | 21:26 | 0 | 0 | 5507.423 | 21:26 | 2.8365 | 2.6073 | 0.22911 | 3.043e-05 | 0
[13 empty] | 21:26 | 0.9193 | 0.91146 | 0 |  | 21:26 | 0 | 0 | 5507.423 | 21:26 | 2.8369 | 2.6077 | 0.22914 | 3.0436e-05 | 0
[13 empty] | 21:26 | 0.90825 | 0.91146 | 0 |  | 21:26 | 0 | 0 | 5507.423 | 21:26 | 2.8375 | 2.6083 | 0.22918 | 3.0441e-05 | 0
[13 empty] | 21:26 | 0.89743 | 0.91146 | 0 |  | 21:26 | 0 | 0 | 5507.423 | 21:26 | 2.8381 | 2.6089 | 0.22924 | 3.0447e-05 | 0
[13 empty] | 21:26 | 0.88683 | 0.91146 | 0 |  | 21:26 | 0 | 0 | 5507.423 | 21:26 | 2.8386 | 2.6092 | 0.22928 | 3.0453e-05 | 0
[13 empty] | 21:27 | 0.87645 | 0.91146 | 0 |  | 21:27 | 0 | 0 | 5507.423 | 21:27 | 2.8392 | 2.6098 | 0.22932 | 3.0458e-05 | 0
[13 empty] | 21:27 | 0.86628 | 0.91146 | 0 |  | 21:27 | 0 | 0 | 5507.423 | 21:27 | 2.8396 | 2.6102 | 0.22937 | 3.0464e-05 | 0
[13 empty] | 21:27 | 0.85633 | 0.91146 | 0 |  | 21:27 | 0 | 0 | 5507.423 | 21:27 | 2.8402 | 2.6108 | 0.22941 | 3.047e-05 | 0
[13 empty] | 21:28 | 0.84657 | 0.91146 | 0 |  | 21:28 | 0 | 0 | 5507.423 | 21:28 | 2.8406 | 2.6112 | 0.22945 | 3.0476e-05 | 0
[13 empty] | 21:28 | 0.83702 | 0.91146 | 0 |  | 21:28 | 0 | 0 | 5507.423 | 21:28 | 2.8413 | 2.6117 | 0.22949 | 3.0481e-05 | 0
[13 empty] | 21:28 | 0.82766 | 0.91146 | 0 |  | 21:28 | 0 | 0 | 5507.423 | 21:28 | 2.8417 | 2.6121 | 0.22953 | 3.0487e-05 | 0
[13 empty] | 21:28 | 0.8185 | 0.91146 | 0 |  | 21:28 | 0 | 0 | 5507.423 | 21:28 | 2.8421 | 2.6125 | 0.22957 | 3.0493e-05 | 0
[13 empty] | 21:29 | 0.80952 | 0.91146 | 0 |  | 21:29 | 0 | 0 | 5507.423 | 21:29 | 2.8427 | 2.6131 | 0.2296 | 3.0497e-05 | 0
[13 empty] | 21:29 | 0.80073 | 0.91146 | 0 |  | 21:29 | 0 | 0 | 5507.423 | 21:29 | 2.8431 | 2.6135 | 0.22964 | 3.0502e-05 | 0
[13 empty] | 21:29 | 0.79211 | 0.91146 | 0 |  | 21:29 | 0 | 0 | 5507.423 | 21:29 | 2.8435 | 2.6138 | 0.22968 | 3.0508e-05 | 0
[13 empty] | 21:29 | 0.78368 | 0.91146 | 0 |  | 21:29 | 0 | 0 | 5507.423 | 21:29 | 2.8442 | 2.6144 | 0.22972 | 3.0512e-05 | 0
[13 empty] | 21:30 | 0.77542 | 0.91146 | 0 |  | 21:30 | 0 | 0 | 5507.423 | 21:30 | 2.8446 | 2.6148 | 0.22976 | 3.0518e-05 | 0
[13 empty] | 21:30 | 0.76733 | 0.91146 | 0 |  | 21:30 | 0 | 0 | 5507.423 | 21:30 | 2.845 | 2.6152 | 0.22979 | 3.0523e-05 | 0
[13 empty] | 21:30 | 0.7594 | 0.91146 | 0 |  | 21:30 | 0 | 0 | 5507.423 | 21:30 | 2.8454 | 2.6156 | 0.22983 | 3.0527e-05 | 0
[13 empty] | 21:30 | 0.75164 | 0.91146 | 0 |  | 21:30 | 0 | 0 | 5507.423 | 21:30 | 2.846 | 2.6161 | 0.22987 | 3.0533e-05 | 0
[13 empty] | 21:30 | 0.74403 | 0.91146 | 0 |  | 21:30 | 0 | 0 | 5507.423 | 21:30 | 2.8464 | 2.6165 | 0.22991 | 3.0537e-05 | 0
[13 empty] | 21:31 | 0.73658 | 0.91146 | 0 |  | 21:31 | 0 | 0 | 5507.423 | 21:31 | 2.8469 | 2.6169 | 0.22995 | 3.0542e-05 | 0
[13 empty] | 21:31 | 0.72929 | 0.91146 | 0 |  | 21:31 | 0 | 0 | 5507.423 | 21:31 | 2.8473 | 2.6173 | 0.22999 | 3.0546e-05 | 0
[13 empty] | 21:31 | 1.1629 | 0.91146 | 0 |  | 21:31 | 0 | 0 | 5507.423 | 21:31 | 2.8479 | 2.6178 | 0.23004 | 3.0554e-05 | 0
[13 empty] | 21:32 | 1.1468 | 0.91146 | 0 |  | 21:32 | 0 | 0 | 5507.423 | 21:32 | 2.8487 | 2.6186 | 0.2301 | 3.0562e-05 | 0
[13 empty] | 21:32 | 1.1311 | 0.91146 | 0 |  | 21:32 | 0 | 0 | 5507.423 | 21:32 | 2.8494 | 2.6192 | 0.23016 | 3.0569e-05 | 0
[13 empty] | 21:32 | 1.1157 | 0.91146 | 0 |  | 21:32 | 0 | 0 | 5507.423 | 21:32 | 2.85 | 2.6198 | 0.23021 | 3.0577e-05 | 0
[13 empty] | 21:32 | 1.1006 | 0.91146 | 0 |  | 21:32 | 0 | 0 | 5507.423 | 21:32 | 2.8508 | 2.6205 | 0.23025 | 3.0584e-05 | 0
[13 empty] | 21:33 | 1.0859 | 0.91146 | 0 |  | 21:33 | 0 | 0 | 5507.423 | 21:33 | 2.8514 | 2.6211 | 0.23031 | 3.059e-05 | 0
[13 empty] | 21:33 | 1.0714 | 0.91146 | 0 |  | 21:33 | 0 | 0 | 5507.423 | 21:33 | 2.8521 | 2.6217 | 0.23037 | 3.0598e-05 | 0
[13 empty] | 21:33 | 1.0572 | 0.91146 | 0 |  | 21:33 | 0 | 0 | 5507.423 | 21:33 | 2.8527 | 2.6222 | 0.23042 | 3.0604e-05 | 0
[13 empty] | 21:33 | 1.0434 | 0.91146 | 0 |  | 21:33 | 0 | 0 | 5507.423 | 21:33 | 2.8533 | 2.6228 | 0.23046 | 3.0611e-05 | 0
[13 empty] | 21:34 | 1.0298 | 0.91146 | 0 |  | 21:34 | 0 | 0 | 5507.423 | 21:34 | 2.8539 | 2.6234 | 0.23052 | 3.0617e-05 | 0
[13 empty] | 21:34 | 1.0164 | 0.91146 | 0 |  | 21:34 | 0 | 0 | 5507.423 | 21:34 | 2.8545 | 2.624 | 0.23056 | 3.0625e-05 | 0
[13 empty] | 21:34 | 1.0034 | 0.91146 | 0 |  | 21:34 | 0 | 0 | 5507.423 | 21:34 | 2.8552 | 2.6245 | 0.23062 | 3.063e-05 | 0
[13 empty] | 21:34 | 0.99062 | 0.91146 | 0 |  | 21:34 | 0 | 0 | 5507.423 | 21:34 | 2.8558 | 2.6251 | 0.23067 | 3.0638e-05 | 0
[13 empty] | 21:34 | 0.97811 | 0.91146 | 0 |  | 21:34 | 0 | 0 | 5507.423 | 21:34 | 2.8564 | 2.6257 | 0.23071 | 3.0644e-05 | 0
[13 empty] | 21:35 | 0.96585 | 0.91146 | 0 |  | 21:35 | 0 | 0 | 5507.423 | 21:35 | 2.8569 | 2.6261 | 0.23077 | 3.0649e-05 | 0
[13 empty] | 21:35 | 0.95385 | 0.91146 | 0 |  | 21:35 | 0 | 0 | 5507.423 | 21:35 | 2.8575 | 2.6266 | 0.23081 | 3.0657e-05 | 0
[13 empty] | 21:35 | 0.94209 | 0.91146 | 0 |  | 21:35 | 0 | 0 | 5507.423 | 21:35 | 2.8581 | 2.6272 | 0.23084 | 3.0663e-05 | 0
[13 empty] | 21:36 | 0.93058 | 0.91146 | 0 |  | 21:36 | 0 | 0 | 5507.423 | 21:36 | 2.8587 | 2.6278 | 0.2309 | 3.0669e-05 | 0
[13 empty] | 21:36 | 0.9193 | 0.91146 | 0 |  | 21:36 | 0 | 0 | 5507.423 | 21:36 | 2.8591 | 2.6282 | 0.23094 | 3.0674e-05 | 0
[13 empty] | 21:36 | 0.90825 | 0.91146 | 0 |  | 21:36 | 0 | 0 | 5507.423 | 21:36 | 2.8597 | 2.6287 | 0.23098 | 3.068e-05 | 0
[13 empty] | 21:36 | 0.89743 | 0.91146 | 0 |  | 21:36 | 0 | 0 | 5507.423 | 21:36 | 2.8604 | 2.6293 | 0.23104 | 3.0686e-05 | 0
[13 empty] | 21:36 | 0.88683 | 0.91146 | 0 |  | 21:36 | 0 | 0 | 5507.423 | 21:36 | 2.8608 | 2.6297 | 0.23107 | 3.0691e-05 | 0
[13 empty] | 21:37 | 0.87645 | 0.91146 | 0 |  | 21:37 | 0 | 0 | 5507.423 | 21:37 | 2.8614 | 2.6303 | 0.23111 | 3.0697e-05 | 0
[13 empty] | 21:37 | 0.86628 | 0.91146 | 0 |  | 21:37 | 0 | 0 | 5507.423 | 21:37 | 2.8618 | 2.6306 | 0.23117 | 3.0703e-05 | 0
[13 empty] | 21:37 | 0.85633 | 0.91146 | 0 |  | 21:37 | 0 | 0 | 5507.423 | 21:37 | 2.8625 | 2.6312 | 0.23121 | 3.0709e-05 | 0
[13 empty] | 21:38 | 0.84657 | 0.91146 | 0 |  | 21:38 | 0 | 0 | 5507.423 | 21:38 | 2.8629 | 2.6316 | 0.23125 | 3.0714e-05 | 0
[13 empty] | 21:38 | 0.83702 | 0.91146 | 0 |  | 21:38 | 0 | 0 | 5507.423 | 21:38 | 2.8635 | 2.6322 | 0.23128 | 3.072e-05 | 0
[13 empty] | 21:38 | 0.82766 | 0.91146 | 0 |  | 21:38 | 0 | 0 | 5507.423 | 21:38 | 2.8639 | 2.6326 | 0.23132 | 3.0726e-05 | 0
[13 empty] | 21:38 | 0.8185 | 0.91146 | 0 |  | 21:38 | 0 | 0 | 5507.423 | 21:38 | 2.8643 | 2.6329 | 0.23136 | 3.073e-05 | 0
[13 empty] | 21:38 | 0.80952 | 0.91146 | 0 |  | 21:38 | 0 | 0 | 5507.423 | 21:38 | 2.8649 | 2.6335 | 0.2314 | 3.0735e-05 | 0
[13 empty] | 21:39 | 0.80073 | 0.91146 | 0 |  | 21:39 | 0 | 0 | 5507.423 | 21:39 | 2.8654 | 2.6339 | 0.23144 | 3.0741e-05 | 0
[13 empty] | 21:39 | 0.79211 | 0.91146 | 0 |  | 21:39 | 0 | 0 | 5507.423 | 21:39 | 2.8658 | 2.6343 | 0.23147 | 3.0747e-05 | 0
[13 empty] | 21:39 | 0.78368 | 0.91146 | 0 |  | 21:39 | 0 | 0 | 5507.423 | 21:39 | 2.8664 | 2.6348 | 0.23151 | 3.0751e-05 | 0
[13 empty] | 21:40 | 0.77542 | 0.91146 | 0 |  | 21:40 | 0 | 0 | 5507.423 | 21:40 | 2.8668 | 2.6352 | 0.23155 | 3.0756e-05 | 0
[13 empty] | 21:40 | 0.76733 | 0.91146 | 0 |  | 21:40 | 0 | 0 | 5507.423 | 21:40 | 2.8672 | 2.6356 | 0.23159 | 3.076e-05 | 0
[13 empty] | 21:40 | 0.7594 | 0.91146 | 0 |  | 21:40 | 0 | 0 | 5507.423 | 21:40 | 2.8676 | 2.636 | 0.23163 | 3.0766e-05 | 0
[13 empty] | 21:40 | 0.75164 | 0.91146 | 0 |  | 21:40 | 0 | 0 | 5507.423 | 21:40 | 2.8683 | 2.6366 | 0.23167 | 3.0772e-05 | 0
[13 empty] | 21:40 | 0.74403 | 0.91146 | 0 |  | 21:40 | 0 | 0 | 5507.423 | 21:40 | 2.8687 | 2.6369 | 0.2317 | 3.0775e-05 | 0
[13 empty] | 21:41 | 0.73658 | 0.91146 | 0 |  | 21:41 | 0 | 0 | 5507.423 | 21:41 | 2.8691 | 2.6373 | 0.23174 | 3.0781e-05 | 0
[13 empty] | 21:41 | 0.72929 | 0.91146 | 0 |  | 21:41 | 0 | 0 | 5507.423 | 21:41 | 2.8695 | 2.6377 | 0.23178 | 3.0785e-05 | 0
[13 empty] | 21:41 | 1.1629 | 0.91146 | 0 |  | 21:41 | 0 | 0 | 5507.423 | 21:41 | 2.8701 | 2.6383 | 0.23184 | 3.0793e-05 | 0
[13 empty] | 21:42 | 1.1468 | 0.91146 | 0 |  | 21:42 | 0 | 0 | 5507.423 | 21:42 | 2.871 | 2.639 | 0.2319 | 3.08e-05 | 0
[13 empty] | 21:42 | 1.1311 | 0.91146 | 0 |  | 21:42 | 0 | 0 | 5507.423 | 21:42 | 2.8716 | 2.6396 | 0.23195 | 3.0808e-05 | 0
[13 empty] | 21:42 | 1.1157 | 0.91146 | 0 |  | 21:42 | 0 | 0 | 5507.423 | 21:42 | 2.8722 | 2.6402 | 0.23201 | 3.0816e-05 | 0
[13 empty] | 21:42 | 1.1006 | 0.91146 | 0 |  | 21:42 | 0 | 0 | 5507.423 | 21:42 | 2.873 | 2.641 | 0.23205 | 3.0821e-05 | 0
[13 empty] | 21:42 | 1.0859 | 0.91146 | 0 |  | 21:42 | 0 | 0 | 5507.423 | 21:42 | 2.8737 | 2.6415 | 0.23211 | 3.0829e-05 | 0
[13 empty] | 21:43 | 1.0714 | 0.91146 | 0 |  | 21:43 | 0 | 0 | 5507.423 | 21:43 | 2.8743 | 2.6421 | 0.23216 | 3.0837e-05 | 0
[13 empty] | 21:43 | 1.0572 | 0.91146 | 0 |  | 21:43 | 0 | 0 | 5507.423 | 21:43 | 2.8749 | 2.6427 | 0.23222 | 3.0842e-05 | 0
[13 empty] | 21:43 | 1.0434 | 0.91146 | 0 |  | 21:43 | 0 | 0 | 5507.423 | 21:43 | 2.8755 | 2.6432 | 0.23226 | 3.085e-05 | 0
[13 empty] | 21:44 | 1.0298 | 0.91146 | 0 |  | 21:44 | 0 | 0 | 5507.423 | 21:44 | 2.8762 | 2.6438 | 0.23232 | 3.0856e-05 | 0
[13 empty] | 21:44 | 1.0164 | 0.91146 | 0 |  | 21:44 | 0 | 0 | 5507.423 | 21:44 | 2.8768 | 2.6444 | 0.23237 | 3.0863e-05 | 0
[13 empty] | 21:44 | 1.0034 | 0.91146 | 0 |  | 21:44 | 0 | 0 | 5507.423 | 21:44 | 2.8774 | 2.645 | 0.23241 | 3.0869e-05 | 0
[13 empty] | 21:44 | 0.99062 | 0.91146 | 0 |  | 21:44 | 0 | 0 | 5507.423 | 21:44 | 2.878 | 2.6455 | 0.23247 | 3.0877e-05 | 0
[13 empty] | 21:44 | 0.97811 | 0.91146 | 0 |  | 21:44 | 0 | 0 | 5507.423 | 21:44 | 2.8786 | 2.6461 | 0.23251 | 3.0882e-05 | 0
[13 empty] | 21:45 | 0.96585 | 0.91146 | 0 |  | 21:45 | 0 | 0 | 5507.423 | 21:45 | 2.8791 | 2.6465 | 0.23256 | 3.0888e-05 | 0
[13 empty] | 21:45 | 0.95385 | 0.91146 | 0 |  | 21:45 | 0 | 0 | 5507.423 | 21:45 | 2.8797 | 2.6471 | 0.2326 | 3.0894e-05 | 0
[13 empty] | 21:45 | 0.94209 | 0.91146 | 0 |  | 21:45 | 0 | 0 | 5507.423 | 21:45 | 2.8803 | 2.6476 | 0.23264 | 3.0902e-05 | 0
[13 empty] | 21:46 | 0.93058 | 0.91146 | 0 |  | 21:46 | 0 | 0 | 5507.423 | 21:46 | 2.8809 | 2.6482 | 0.2327 | 3.0907e-05 | 0
[13 empty] | 21:46 | 0.9193 | 0.91146 | 0 |  | 21:46 | 0 | 0 | 5507.423 | 21:46 | 2.8814 | 2.6486 | 0.23274 | 3.0913e-05 | 0
[13 empty] | 21:46 | 0.90825 | 0.91146 | 0 |  | 21:46 | 0 | 0 | 5507.423 | 21:46 | 2.882 | 2.6492 | 0.23279 | 3.0919e-05 | 0
[13 empty] | 21:46 | 0.89743 | 0.91146 | 0 |  | 21:46 | 0 | 0 | 5507.423 | 21:46 | 2.8826 | 2.6497 | 0.23283 | 3.0924e-05 | 0
[13 empty] | 21:46 | 0.88683 | 0.91146 | 0 |  | 21:46 | 0 | 0 | 5507.423 | 21:46 | 2.883 | 2.6501 | 0.23287 | 3.093e-05 | 0
[13 empty] | 21:47 | 0.87645 | 0.91146 | 0 |  | 21:47 | 0 | 0 | 5507.423 | 21:47 | 2.8836 | 2.6507 | 0.23291 | 3.0936e-05 | 0
[13 empty] | 21:47 | 0.86628 | 0.91146 | 0 |  | 21:47 | 0 | 0 | 5507.423 | 21:47 | 2.8841 | 2.6511 | 0.23296 | 3.0942e-05 | 0
[13 empty] | 21:47 | 0.85633 | 0.91146 | 0 |  | 21:47 | 0 | 0 | 5507.423 | 21:47 | 2.8847 | 2.6516 | 0.233 | 3.0947e-05 | 0
[13 empty] | 21:48 | 0.84657 | 0.91146 | 0 |  | 21:48 | 0 | 0 | 5507.423 | 21:48 | 2.8851 | 2.652 | 0.23304 | 3.0953e-05 | 0
[13 empty] | 21:48 | 0.83702 | 0.91146 | 0 |  | 21:48 | 0 | 0 | 5507.423 | 21:48 | 2.8857 | 2.6526 | 0.23308 | 3.0959e-05 | 0
[13 empty] | 21:48 | 0.82766 | 0.91146 | 0 |  | 21:48 | 0 | 0 | 5507.423 | 21:48 | 2.8861 | 2.653 | 0.23312 | 3.0963e-05 | 0
[13 empty] | 21:48 | 0.8185 | 0.91146 | 0 |  | 21:48 | 0 | 0 | 5507.423 | 21:48 | 2.8866 | 2.6534 | 0.23316 | 3.0968e-05 | 0
[13 empty] | 21:48 | 0.80952 | 0.91146 | 0 |  | 21:48 | 0 | 0 | 5507.423 | 21:48 | 2.8872 | 2.6539 | 0.23319 | 3.0974e-05 | 0
[13 empty] | 21:49 | 0.80073 | 0.91146 | 0 |  | 21:49 | 0 | 0 | 5507.423 | 21:49 | 2.8876 | 2.6543 | 0.23323 | 3.098e-05 | 0
[13 empty] | 21:49 | 0.79211 | 0.91146 | 0 |  | 21:49 | 0 | 0 | 5507.423 | 21:49 | 2.888 | 2.6547 | 0.23327 | 3.0984e-05 | 0
[13 empty] | 21:49 | 0.78368 | 0.91146 | 0 |  | 21:49 | 0 | 0 | 5507.423 | 21:49 | 2.8886 | 2.6553 | 0.23331 | 3.0989e-05 | 0
[13 empty] | 21:50 | 0.77542 | 0.91146 | 0 |  | 21:50 | 0 | 0 | 5507.423 | 21:50 | 2.889 | 2.6557 | 0.23335 | 3.0995e-05 | 0
[13 empty] | 21:50 | 0.76733 | 0.91146 | 0 |  | 21:50 | 0 | 0 | 5507.423 | 21:50 | 2.8895 | 2.656 | 0.23338 | 3.0999e-05 | 0
[13 empty] | 21:50 | 0.7594 | 0.91146 | 0 |  | 21:50 | 0 | 0 | 5507.423 | 21:50 | 2.8899 | 2.6564 | 0.23342 | 3.1005e-05 | 0
[13 empty] | 21:50 | 0.75164 | 0.91146 | 0 |  | 21:50 | 0 | 0 | 5507.423 | 21:50 | 2.8905 | 2.657 | 0.23346 | 3.1008e-05 | 0
[13 empty] | 21:50 | 0.74403 | 0.91146 | 0 |  | 21:50 | 0 | 0 | 5507.423 | 21:50 | 2.8909 | 2.6574 | 0.2335 | 3.1014e-05 | 0
[13 empty] | 21:51 | 0.73658 | 0.91146 | 0 |  | 21:51 | 0 | 0 | 5507.423 | 21:51 | 2.8913 | 2.6578 | 0.23354 | 3.102e-05 | 0
[13 empty] | 21:51 | 0.72929 | 0.91146 | 0 |  | 21:51 | 0 | 0 | 5507.423 | 21:51 | 2.8917 | 2.6581 | 0.23358 | 3.1024e-05 | 0
[13 empty] | 21:51 | 1.1629 | 0.91146 | 0 |  | 21:51 | 0 | 0 | 5507.423 | 21:51 | 2.8924 | 2.6587 | 0.23363 | 3.1031e-05 | 0
[13 empty] | 21:52 | 1.1468 | 0.91146 | 0 |  | 21:52 | 0 | 0 | 5507.423 | 21:52 | 2.8932 | 2.6595 | 0.23369 | 3.1039e-05 | 0
[13 empty] | 21:52 | 1.1311 | 0.91146 | 0 |  | 21:52 | 0 | 0 | 5507.423 | 21:52 | 2.8938 | 2.6601 | 0.23375 | 3.1047e-05 | 0
[13 empty] | 21:52 | 1.1157 | 0.91146 | 0 |  | 21:52 | 0 | 0 | 5507.423 | 21:52 | 2.8945 | 2.6606 | 0.2338 | 3.1052e-05 | 0
[13 empty] | 21:52 | 1.1006 | 0.91146 | 0 |  | 21:52 | 0 | 0 | 5507.423 | 21:52 | 2.8953 | 2.6614 | 0.23384 | 3.106e-05 | 0
[13 empty] | 21:52 | 1.0859 | 0.91146 | 0 |  | 21:52 | 0 | 0 | 5507.423 | 21:52 | 2.8959 | 2.662 | 0.2339 | 3.1068e-05 | 0
[13 empty] | 21:53 | 1.0714 | 0.91146 | 0 |  | 21:53 | 0 | 0 | 5507.423 | 21:53 | 2.8965 | 2.6625 | 0.23396 | 3.1075e-05 | 0
[13 empty] | 21:53 | 1.0572 | 0.91146 | 0 |  | 21:53 | 0 | 0 | 5507.423 | 21:53 | 2.8972 | 2.6631 | 0.23402 | 3.1081e-05 | 0
[13 empty] | 21:53 | 1.0434 | 0.91146 | 0 |  | 21:53 | 0 | 0 | 5507.423 | 21:53 | 2.8978 | 2.6637 | 0.23405 | 3.1089e-05 | 0
[13 empty] | 21:54 | 1.0298 | 0.91146 | 0 |  | 21:54 | 0 | 0 | 5507.423 | 21:54 | 2.8984 | 2.6643 | 0.23411 | 3.1094e-05 | 0
[13 empty] | 21:54 | 1.0164 | 0.91146 | 0 |  | 21:54 | 0 | 0 | 5507.423 | 21:54 | 2.899 | 2.6648 | 0.23417 | 3.1102e-05 | 0
[13 empty] | 21:54 | 1.0034 | 0.91146 | 0 |  | 21:54 | 0 | 0 | 5507.423 | 21:54 | 2.8996 | 2.6654 | 0.23421 | 3.1108e-05 | 0
[13 empty] | 21:54 | 0.99062 | 0.91146 | 0 |  | 21:54 | 0 | 0 | 5507.423 | 21:54 | 2.9003 | 2.666 | 0.23426 | 3.1114e-05 | 0
[13 empty] | 21:54 | 0.97811 | 0.91146 | 0 |  | 21:54 | 0 | 0 | 5507.423 | 21:54 | 2.9009 | 2.6665 | 0.2343 | 3.1121e-05 | 0
[13 empty] | 21:55 | 0.96585 | 0.91146 | 0 |  | 21:55 | 0 | 0 | 5507.423 | 21:55 | 2.9013 | 2.6669 | 0.23436 | 3.1127e-05 | 0
[13 empty] | 21:55 | 0.95385 | 0.91146 | 0 |  | 21:55 | 0 | 0 | 5507.423 | 21:55 | 2.9019 | 2.6675 | 0.2344 | 3.1133e-05 | 0
[13 empty] | 21:55 | 0.94209 | 0.91146 | 0 |  | 21:55 | 0 | 0 | 5507.423 | 21:55 | 2.9025 | 2.6681 | 0.23444 | 3.114e-05 | 0
[13 empty] | 21:56 | 0.93058 | 0.91146 | 0 |  | 21:56 | 0 | 0 | 5507.423 | 21:56 | 2.9032 | 2.6686 | 0.23449 | 3.1146e-05 | 0
[13 empty] | 21:56 | 0.9193 | 0.91146 | 0 |  | 21:56 | 0 | 0 | 5507.423 | 21:56 | 2.9036 | 2.669 | 0.23453 | 3.1152e-05 | 0
[13 empty] | 21:56 | 0.90825 | 0.91146 | 0 |  | 21:56 | 0 | 0 | 5507.423 | 21:56 | 2.9042 | 2.6696 | 0.23459 | 3.1157e-05 | 0
[13 empty] | 21:56 | 0.89743 | 0.91146 | 0 |  | 21:56 | 0 | 0 | 5507.423 | 21:56 | 2.9048 | 2.6702 | 0.23463 | 3.1163e-05 | 0
[13 empty] | 21:56 | 0.88683 | 0.91146 | 0 |  | 21:56 | 0 | 0 | 5507.423 | 21:56 | 2.9053 | 2.6706 | 0.23466 | 3.1169e-05 | 0
[13 empty] | 21:57 | 0.87645 | 0.91146 | 0 |  | 21:57 | 0 | 0 | 5507.423 | 21:57 | 2.9059 | 2.6711 | 0.2347 | 3.1175e-05 | 0
[13 empty] | 21:57 | 0.86628 | 0.91146 | 0 |  | 21:57 | 0 | 0 | 5507.423 | 21:57 | 2.9063 | 2.6715 | 0.23476 | 3.118e-05 | 0
[13 empty] | 21:57 | 0.85633 | 0.91146 | 0 |  | 21:57 | 0 | 0 | 5507.423 | 21:57 | 2.9069 | 2.6721 | 0.2348 | 3.1186e-05 | 0
[13 empty] | 21:57 | 0.84657 | 0.91146 | 0 |  | 21:57 | 0 | 0 | 5507.423 | 21:57 | 2.9073 | 2.6725 | 0.23484 | 3.1192e-05 | 0
[13 empty] | 21:58 | 0.83702 | 0.91146 | 0 |  | 21:58 | 0 | 0 | 5507.423 | 21:58 | 2.9079 | 2.673 | 0.23487 | 3.1198e-05 | 0
[13 empty] | 21:58 | 0.82766 | 0.91146 | 0 |  | 21:58 | 0 | 0 | 5507.423 | 21:58 | 2.9084 | 2.6734 | 0.23491 | 3.1201e-05 | 0
[13 empty] | 21:58 | 0.8185 | 0.91146 | 0 |  | 21:58 | 0 | 0 | 5507.423 | 21:58 | 2.9088 | 2.6738 | 0.23495 | 3.1207e-05 | 0
[13 empty] | 21:58 | 0.80952 | 0.91146 | 0 |  | 21:58 | 0 | 0 | 5507.423 | 21:58 | 2.9094 | 2.6744 | 0.23499 | 3.1213e-05 | 0
[13 empty] | 21:59 | 0.80073 | 0.91146 | 0 |  | 21:59 | 0 | 0 | 5507.423 | 21:59 | 2.9098 | 2.6748 | 0.23503 | 3.1219e-05 | 0
[13 empty] | 21:59 | 0.79211 | 0.91146 | 0 |  | 21:59 | 0 | 0 | 5507.423 | 21:59 | 2.9102 | 2.6751 | 0.23507 | 3.1222e-05 | 0
[13 empty] | 21:59 | 0.78368 | 0.91146 | 0 |  | 21:59 | 0 | 0 | 5507.423 | 21:59 | 2.9108 | 2.6757 | 0.2351 | 3.1228e-05 | 0
[13 empty] | 22:00 | 0.77542 | 0.91146 | 0 |  | 22:00 | 0 | 0 | 5507.423 | 22:00 | 2.9113 | 2.6761 | 0.23514 | 3.1234e-05 | 0
[13 empty] | 22:00 | 0.76733 | 0.91146 | 0 |  | 22:00 | 0 | 0 | 5507.423 | 22:00 | 2.9117 | 2.6765 | 0.23518 | 3.1238e-05 | 0
[13 empty] | 22:00 | 0.7594 | 0.91146 | 0 |  | 22:00 | 0 | 0 | 5507.423 | 22:00 | 2.9121 | 2.6769 | 0.23522 | 3.1243e-05 | 0
[13 empty] | 22:00 | 0.75164 | 0.91146 | 0 |  | 22:00 | 0 | 0 | 5507.423 | 22:00 | 2.9127 | 2.6774 | 0.23526 | 3.1247e-05 | 0
[13 empty] | 22:00 | 0.74403 | 0.91146 | 0 |  | 22:00 | 0 | 0 | 5507.423 | 22:00 | 2.9131 | 2.6778 | 0.23529 | 3.1253e-05 | 0
[13 empty] | 22:01 | 0.73658 | 0.91146 | 0 |  | 22:01 | 0 | 0 | 5507.423 | 22:01 | 2.9136 | 2.6782 | 0.23533 | 3.1257e-05 | 0
[13 empty] | 22:01 | 0.72929 | 0.91146 | 0 |  | 22:01 | 0 | 0 | 5507.423 | 22:01 | 2.914 | 2.6786 | 0.23537 | 3.1262e-05 | 0
[13 empty] | 22:01 | 1.1629 | 0.91146 | 0 |  | 22:01 | 0 | 0 | 5507.423 | 22:01 | 2.9146 | 2.6792 | 0.23543 | 3.127e-05 | 0
[13 empty] | 22:01 | 1.1468 | 0.91146 | 0 |  | 22:01 | 0 | 0 | 5507.423 | 22:01 | 2.9154 | 2.6799 | 0.23549 | 3.1278e-05 | 0
[13 empty] | 22:02 | 1.1311 | 0.91146 | 0 |  | 22:02 | 0 | 0 | 5507.423 | 22:02 | 2.9161 | 2.6805 | 0.23554 | 3.1285e-05 | 0
[13 empty] | 22:02 | 1.1157 | 0.91146 | 0 |  | 22:02 | 0 | 0 | 5507.423 | 22:02 | 2.9167 | 2.6811 | 0.2356 | 3.1291e-05 | 0
[13 empty] | 22:02 | 1.1006 | 0.91146 | 0 |  | 22:02 | 0 | 0 | 5507.423 | 22:02 | 2.9175 | 2.6818 | 0.23564 | 3.1299e-05 | 0
[13 empty] | 22:02 | 1.0859 | 0.91146 | 0 |  | 22:02 | 0 | 0 | 5507.423 | 22:02 | 2.9181 | 2.6824 | 0.2357 | 3.1306e-05 | 0
[13 empty] | 22:03 | 1.0714 | 0.91146 | 0 |  | 22:03 | 0 | 0 | 5507.423 | 22:03 | 2.9188 | 2.683 | 0.23575 | 3.1312e-05 | 0
[13 empty] | 22:03 | 1.0572 | 0.91146 | 0 |  | 22:03 | 0 | 0 | 5507.423 | 22:03 | 2.9194 | 2.6835 | 0.23581 | 3.132e-05 | 0
[13 empty] | 22:03 | 1.0434 | 0.91146 | 0 |  | 22:03 | 0 | 0 | 5507.423 | 22:03 | 2.92 | 2.6841 | 0.23585 | 3.1327e-05 | 0
[13 empty] | 22:04 | 1.0298 | 0.91146 | 0 |  | 22:04 | 0 | 0 | 5507.423 | 22:04 | 2.9206 | 2.6847 | 0.23591 | 3.1333e-05 | 0
[13 empty] | 22:04 | 1.0164 | 0.91146 | 0 |  | 22:04 | 0 | 0 | 5507.423 | 22:04 | 2.9213 | 2.6853 | 0.23596 | 3.1341e-05 | 0
[13 empty] | 22:04 | 1.0034 | 0.91146 | 0 |  | 22:04 | 0 | 0 | 5507.423 | 22:04 | 2.9219 | 2.6858 | 0.236 | 3.1347e-05 | 0
[13 empty] | 22:04 | 0.99062 | 0.91146 | 0 |  | 22:04 | 0 | 0 | 5507.423 | 22:04 | 2.9225 | 2.6864 | 0.23606 | 3.1352e-05 | 0
[13 empty] | 22:04 | 0.97811 | 0.91146 | 0 |  | 22:04 | 0 | 0 | 5507.423 | 22:04 | 2.9231 | 2.687 | 0.2361 | 3.136e-05 | 0
[13 empty] | 22:05 | 0.96585 | 0.91146 | 0 |  | 22:05 | 0 | 0 | 5507.423 | 22:05 | 2.9235 | 2.6874 | 0.23615 | 3.1366e-05 | 0
[13 empty] | 22:05 | 0.95385 | 0.91146 | 0 |  | 22:05 | 0 | 0 | 5507.423 | 22:05 | 2.9242 | 2.6879 | 0.23619 | 3.1371e-05 | 0
[13 empty] | 22:05 | 0.94209 | 0.91146 | 0 |  | 22:05 | 0 | 0 | 5507.423 | 22:05 | 2.9248 | 2.6885 | 0.23623 | 3.1377e-05 | 0
[13 empty] | 22:05 | 0.93058 | 0.91146 | 0 |  | 22:05 | 0 | 0 | 5507.423 | 22:05 | 2.9254 | 2.6891 | 0.23629 | 3.1385e-05 | 0
[13 empty] | 22:06 | 0.9193 | 0.91146 | 0 |  | 22:06 | 0 | 0 | 5507.423 | 22:06 | 2.9258 | 2.6895 | 0.23633 | 3.139e-05 | 0
[13 empty] | 22:06 | 0.90825 | 0.91146 | 0 |  | 22:06 | 0 | 0 | 5507.423 | 22:06 | 2.9265 | 2.69 | 0.23638 | 3.1396e-05 | 0
[13 empty] | 22:06 | 0.89743 | 0.91146 | 0 |  | 22:06 | 0 | 0 | 5507.423 | 22:06 | 2.9271 | 2.6906 | 0.23642 | 3.1402e-05 | 0
[13 empty] | 22:06 | 0.88683 | 0.91146 | 0 |  | 22:06 | 0 | 0 | 5507.423 | 22:06 | 2.9275 | 2.691 | 0.23646 | 3.1408e-05 | 0
[13 empty] | 22:07 | 0.87645 | 0.91146 | 0 |  | 22:07 | 0 | 0 | 5507.423 | 22:07 | 2.9281 | 2.6916 | 0.2365 | 3.1413e-05 | 0
[13 empty] | 22:07 | 0.86628 | 0.91146 | 0 |  | 22:07 | 0 | 0 | 5507.423 | 22:07 | 2.9285 | 2.6919 | 0.23656 | 3.1419e-05 | 0
[13 empty] | 22:07 | 0.85633 | 0.91146 | 0 |  | 22:07 | 0 | 0 | 5507.423 | 22:07 | 2.9291 | 2.6925 | 0.23659 | 3.1425e-05 | 0
[13 empty] | 22:08 | 0.84657 | 0.91146 | 0 |  | 22:08 | 0 | 0 | 5507.423 | 22:08 | 2.9296 | 2.6929 | 0.23663 | 3.1431e-05 | 0
[13 empty] | 22:08 | 0.83702 | 0.91146 | 0 |  | 22:08 | 0 | 0 | 5507.423 | 22:08 | 2.9302 | 2.6935 | 0.23667 | 3.1434e-05 | 0
[13 empty] | 22:08 | 0.82766 | 0.91146 | 0 |  | 22:08 | 0 | 0 | 5507.423 | 22:08 | 2.9306 | 2.6939 | 0.23671 | 3.144e-05 | 0
[13 empty] | 22:08 | 0.8185 | 0.91146 | 0 |  | 22:08 | 0 | 0 | 5507.423 | 22:08 | 2.931 | 2.6942 | 0.23675 | 3.1446e-05 | 0
[13 empty] | 22:08 | 0.80952 | 0.91146 | 0 |  | 22:08 | 0 | 0 | 5507.423 | 22:08 | 2.9316 | 2.6948 | 0.23678 | 3.1452e-05 | 0
[13 empty] | 22:09 | 0.80073 | 0.91146 | 0 |  | 22:09 | 0 | 0 | 5507.423 | 22:09 | 2.932 | 2.6952 | 0.23682 | 3.1455e-05 | 0
[13 empty] | 22:09 | 0.79211 | 0.91146 | 0 |  | 22:09 | 0 | 0 | 5507.423 | 22:09 | 2.9325 | 2.6956 | 0.23686 | 3.1461e-05 | 0
[13 empty] | 22:09 | 0.78368 | 0.91146 | 0 |  | 22:09 | 0 | 0 | 5507.423 | 22:09 | 2.9331 | 2.6961 | 0.2369 | 3.1467e-05 | 0
[13 empty] | 22:10 | 0.77542 | 0.91146 | 0 |  | 22:10 | 0 | 0 | 5507.423 | 22:10 | 2.9335 | 2.6965 | 0.23694 | 3.1471e-05 | 0
[13 empty] | 22:10 | 0.76733 | 0.91146 | 0 |  | 22:10 | 0 | 0 | 5507.423 | 22:10 | 2.9339 | 2.6969 | 0.23698 | 3.1476e-05 | 0
[13 empty] | 22:10 | 0.7594 | 0.91146 | 0 |  | 22:10 | 0 | 0 | 5507.423 | 22:10 | 2.9343 | 2.6973 | 0.23701 | 3.1482e-05 | 0
[13 empty] | 22:10 | 0.75164 | 0.91146 | 0 |  | 22:10 | 0 | 0 | 5507.423 | 22:10 | 2.935 | 2.6979 | 0.23705 | 3.1486e-05 | 0
[13 empty] | 22:10 | 0.74403 | 0.91146 | 0 |  | 22:10 | 0 | 0 | 5507.423 | 22:10 | 2.9354 | 2.6982 | 0.23709 | 3.1492e-05 | 0
[13 empty] | 22:11 | 0.73658 | 0.91146 | 0 |  | 22:11 | 0 | 0 | 5507.423 | 22:11 | 2.9358 | 2.6986 | 0.23713 | 3.1495e-05 | 0
[13 empty] | 22:11 | 0.72929 | 0.91146 | 0 |  | 22:11 | 0 | 0 | 5507.423 | 22:11 | 2.9362 | 2.699 | 0.23717 | 3.1501e-05 | 0
[13 empty] | 22:11 | 1.1629 | 0.91146 | 0 |  | 22:11 | 0 | 0 | 5507.423 | 22:11 | 2.9368 | 2.6996 | 0.23722 | 3.1509e-05 | 0
[13 empty] | 22:12 | 1.1468 | 0.91146 | 0 |  | 22:12 | 0 | 0 | 5507.423 | 22:12 | 2.9377 | 2.7004 | 0.23728 | 3.1516e-05 | 0
[13 empty] | 22:12 | 1.1311 | 0.91146 | 0 |  | 22:12 | 0 | 0 | 5507.423 | 22:12 | 2.9383 | 2.7009 | 0.23734 | 3.1522e-05 | 0
[13 empty] | 22:12 | 1.1157 | 0.91146 | 0 |  | 22:12 | 0 | 0 | 5507.423 | 22:12 | 2.9389 | 2.7015 | 0.2374 | 3.153e-05 | 0
[13 empty] | 22:12 | 1.1006 | 0.91146 | 0 |  | 22:12 | 0 | 0 | 5507.423 | 22:12 | 2.9397 | 2.7023 | 0.23743 | 3.1538e-05 | 0
[13 empty] | 22:12 | 1.0859 | 0.91146 | 0 |  | 22:12 | 0 | 0 | 5507.423 | 22:12 | 2.9404 | 2.7028 | 0.23749 | 3.1545e-05 | 0
[13 empty] | 22:13 | 1.0714 | 0.91146 | 0 |  | 22:13 | 0 | 0 | 5507.423 | 22:13 | 2.941 | 2.7034 | 0.23755 | 3.1551e-05 | 0
[13 empty] | 22:13 | 1.0572 | 0.91146 | 0 |  | 22:13 | 0 | 0 | 5507.423 | 22:13 | 2.9416 | 2.704 | 0.23761 | 3.1559e-05 | 0
[13 empty] | 22:13 | 1.0434 | 0.91146 | 0 |  | 22:13 | 0 | 0 | 5507.423 | 22:13 | 2.9422 | 2.7046 | 0.23764 | 3.1564e-05 | 0
[13 empty] | 22:14 | 1.0298 | 0.91146 | 0 |  | 22:14 | 0 | 0 | 5507.423 | 22:14 | 2.9429 | 2.7051 | 0.2377 | 3.1572e-05 | 0
[13 empty] | 22:14 | 1.0164 | 0.91146 | 0 |  | 22:14 | 0 | 0 | 5507.423 | 22:14 | 2.9435 | 2.7057 | 0.23776 | 3.1578e-05 | 0
[13 empty] | 22:14 | 1.0034 | 0.91146 | 0 |  | 22:14 | 0 | 0 | 5507.423 | 22:14 | 2.9441 | 2.7063 | 0.2378 | 3.1585e-05 | 0
[13 empty] | 22:14 | 0.99062 | 0.91146 | 0 |  | 22:14 | 0 | 0 | 5507.423 | 22:14 | 2.9447 | 2.7068 | 0.23785 | 3.1591e-05 | 0
[13 empty] | 22:14 | 0.97811 | 0.91146 | 0 |  | 22:14 | 0 | 0 | 5507.423 | 22:14 | 2.9453 | 2.7074 | 0.23789 | 3.1599e-05 | 0
[13 empty] | 22:15 | 0.96585 | 0.91146 | 0 |  | 22:15 | 0 | 0 | 5507.423 | 22:15 | 2.9458 | 2.7078 | 0.23795 | 3.1604e-05 | 0
[13 empty] | 22:15 | 0.95385 | 0.91146 | 0 |  | 22:15 | 0 | 0 | 5507.423 | 22:15 | 2.9464 | 2.7084 | 0.23799 | 3.161e-05 | 0
[13 empty] | 22:15 | 0.94209 | 0.91146 | 0 |  | 22:15 | 0 | 0 | 5507.423 | 22:15 | 2.947 | 2.7089 | 0.23803 | 3.1616e-05 | 0
[13 empty] | 22:16 | 0.93058 | 0.91146 | 0 |  | 22:16 | 0 | 0 | 5507.423 | 22:16 | 2.9476 | 2.7095 | 0.23808 | 3.1622e-05 | 0
[13 empty] | 22:16 | 0.9193 | 0.91146 | 0 |  | 22:16 | 0 | 0 | 5507.423 | 22:16 | 2.9481 | 2.7099 | 0.23812 | 3.1629e-05 | 0
[13 empty] | 22:16 | 0.90825 | 0.91146 | 0 |  | 22:16 | 0 | 0 | 5507.423 | 22:16 | 2.9487 | 2.7105 | 0.23818 | 3.1635e-05 | 0
[13 empty] | 22:16 | 0.89743 | 0.91146 | 0 |  | 22:16 | 0 | 0 | 5507.423 | 22:16 | 2.9493 | 2.711 | 0.23822 | 3.1641e-05 | 0
[13 empty] | 22:16 | 0.88683 | 0.91146 | 0 |  | 22:16 | 0 | 0 | 5507.423 | 22:16 | 2.9497 | 2.7114 | 0.23825 | 3.1646e-05 | 0
[13 empty] | 22:17 | 0.87645 | 0.91146 | 0 |  | 22:17 | 0 | 0 | 5507.423 | 22:17 | 2.9503 | 2.712 | 0.23829 | 3.1652e-05 | 0
[13 empty] | 22:17 | 0.86628 | 0.91146 | 0 |  | 22:17 | 0 | 0 | 5507.423 | 22:17 | 2.9508 | 2.7124 | 0.23835 | 3.1658e-05 | 0
[13 empty] | 22:17 | 0.85633 | 0.91146 | 0 |  | 22:17 | 0 | 0 | 5507.423 | 22:17 | 2.9514 | 2.713 | 0.23839 | 3.1664e-05 | 0
[13 empty] | 22:18 | 0.84657 | 0.91146 | 0 |  | 22:18 | 0 | 0 | 5507.423 | 22:18 | 2.9518 | 2.7133 | 0.23843 | 3.1667e-05 | 0
[13 empty] | 22:18 | 0.83702 | 0.91146 | 0 |  | 22:18 | 0 | 0 | 5507.423 | 22:18 | 2.9524 | 2.7139 | 0.23847 | 3.1673e-05 | 0
[13 empty] | 22:18 | 0.82766 | 0.91146 | 0 |  | 22:18 | 0 | 0 | 5507.423 | 22:18 | 2.9528 | 2.7143 | 0.2385 | 3.1679e-05 | 0
[13 empty] | 22:18 | 0.8185 | 0.91146 | 0 |  | 22:18 | 0 | 0 | 5507.423 | 22:18 | 2.9532 | 2.7147 | 0.23854 | 3.1685e-05 | 0
[13 empty] | 22:18 | 0.80952 | 0.91146 | 0 |  | 22:18 | 0 | 0 | 5507.423 | 22:18 | 2.9539 | 2.7152 | 0.23858 | 3.169e-05 | 0
[13 empty] | 22:19 | 0.80073 | 0.91146 | 0 |  | 22:19 | 0 | 0 | 5507.423 | 22:19 | 2.9543 | 2.7156 | 0.23862 | 3.1694e-05 | 0
[13 empty] | 22:19 | 0.79211 | 0.91146 | 0 |  | 22:19 | 0 | 0 | 5507.423 | 22:19 | 2.9547 | 2.716 | 0.23866 | 3.17e-05 | 0
[13 empty] | 22:19 | 0.78368 | 0.91146 | 0 |  | 22:19 | 0 | 0 | 5507.423 | 22:19 | 2.9553 | 2.7166 | 0.23869 | 3.1706e-05 | 0
[13 empty] | 22:20 | 0.77542 | 0.91146 | 0 |  | 22:20 | 0 | 0 | 5507.423 | 22:20 | 2.9557 | 2.717 | 0.23873 | 3.1709e-05 | 0
[13 empty] | 22:20 | 0.76733 | 0.91146 | 0 |  | 22:20 | 0 | 0 | 5507.423 | 22:20 | 2.9562 | 2.7173 | 0.23877 | 3.1715e-05 | 0
[13 empty] | 22:20 | 0.7594 | 0.91146 | 0 |  | 22:20 | 0 | 0 | 5507.423 | 22:20 | 2.9566 | 2.7177 | 0.23881 | 3.1721e-05 | 0
[13 empty] | 22:20 | 0.75164 | 0.91146 | 0 |  | 22:20 | 0 | 0 | 5507.423 | 22:20 | 2.9572 | 2.7183 | 0.23885 | 3.1725e-05 | 0
[13 empty] | 22:20 | 0.74403 | 0.91146 | 0 |  | 22:20 | 0 | 0 | 5507.423 | 22:20 | 2.9576 | 2.7187 | 0.23889 | 3.173e-05 | 0
[13 empty] | 22:21 | 0.73658 | 0.91146 | 0 |  | 22:21 | 0 | 0 | 5507.423 | 22:21 | 2.958 | 2.7191 | 0.23892 | 3.1734e-05 | 0
[13 empty] | 22:21 | 0.72929 | 0.91146 | 0 |  | 22:21 | 0 | 0 | 5507.423 | 22:21 | 2.9584 | 2.7194 | 0.23896 | 3.174e-05 | 0
[13 empty] | 22:21 | 1.1629 | 0.91146 | 0 |  | 22:21 | 0 | 0 | 5507.423 | 22:21 | 2.9591 | 2.72 | 0.23902 | 3.1748e-05 | 0
[13 empty] | 22:22 | 1.1468 | 0.91146 | 0 |  | 22:22 | 0 | 0 | 5507.423 | 22:22 | 2.9599 | 2.7208 | 0.23908 | 3.1753e-05 | 0
[13 empty] | 22:22 | 1.1311 | 0.91146 | 0 |  | 22:22 | 0 | 0 | 5507.423 | 22:22 | 2.9605 | 2.7214 | 0.23913 | 3.1761e-05 | 0
[13 empty] | 22:22 | 1.1157 | 0.91146 | 0 |  | 22:22 | 0 | 0 | 5507.423 | 22:22 | 2.9612 | 2.7219 | 0.23919 | 3.1769e-05 | 0
[13 empty] | 22:22 | 1.1006 | 0.91146 | 0 |  | 22:22 | 0 | 0 | 5507.423 | 22:22 | 2.9618 | 2.7225 | 0.23923 | 3.1776e-05 | 0
[13 empty] | 22:22 | 1.0859 | 0.91146 | 0 |  | 22:22 | 0 | 0 | 5507.423 | 22:22 | 2.9626 | 2.7233 | 0.23929 | 3.1784e-05 | 0
[13 empty] | 22:23 | 1.0714 | 0.91146 | 0 |  | 22:23 | 0 | 0 | 5507.423 | 22:23 | 2.9632 | 2.7238 | 0.23934 | 3.179e-05 | 0
[13 empty] | 22:23 | 1.0572 | 0.91146 | 0 |  | 22:23 | 0 | 0 | 5507.423 | 22:23 | 2.9638 | 2.7244 | 0.2394 | 3.1797e-05 | 0
[13 empty] | 22:23 | 1.0434 | 0.91146 | 0 |  | 22:23 | 0 | 0 | 5507.423 | 22:23 | 2.9645 | 2.725 | 0.23944 | 3.1803e-05 | 0
[13 empty] | 22:24 | 1.0298 | 0.91146 | 0 |  | 22:24 | 0 | 0 | 5507.423 | 22:24 | 2.9651 | 2.7256 | 0.2395 | 3.1811e-05 | 0
[13 empty] | 22:24 | 1.0164 | 0.91146 | 0 |  | 22:24 | 0 | 0 | 5507.423 | 22:24 | 2.9657 | 2.7261 | 0.23955 | 3.1816e-05 | 0
[13 empty] | 22:24 | 1.0034 | 0.91146 | 0 |  | 22:24 | 0 | 0 | 5507.423 | 22:24 | 2.9663 | 2.7267 | 0.23959 | 3.1824e-05 | 0
[13 empty] | 22:24 | 0.99062 | 0.91146 | 0 |  | 22:24 | 0 | 0 | 5507.423 | 22:24 | 2.967 | 2.7273 | 0.23965 | 3.183e-05 | 0
[13 empty] | 22:24 | 0.97811 | 0.91146 | 0 |  | 22:24 | 0 | 0 | 5507.423 | 22:24 | 2.9676 | 2.7279 | 0.23969 | 3.1835e-05 | 0
[13 empty] | 22:25 | 0.96585 | 0.91146 | 0 |  | 22:25 | 0 | 0 | 5507.423 | 22:25 | 2.968 | 2.7282 | 0.23974 | 3.1843e-05 | 0
[13 empty] | 22:25 | 0.95385 | 0.91146 | 0 |  | 22:25 | 0 | 0 | 5507.423 | 22:25 | 2.9686 | 2.7288 | 0.23978 | 3.1849e-05 | 0
[13 empty] | 22:25 | 0.94209 | 0.91146 | 0 |  | 22:25 | 0 | 0 | 5507.423 | 22:25 | 2.9692 | 2.7294 | 0.23982 | 3.1855e-05 | 0
[13 empty] | 22:26 | 0.93058 | 0.91146 | 0 |  | 22:26 | 0 | 0 | 5507.423 | 22:26 | 2.9699 | 2.73 | 0.23988 | 3.186e-05 | 0
[13 empty] | 22:26 | 0.9193 | 0.91146 | 0 |  | 22:26 | 0 | 0 | 5507.423 | 22:26 | 2.9703 | 2.7303 | 0.23992 | 3.1866e-05 | 0
[13 empty] | 22:26 | 0.90825 | 0.91146 | 0 |  | 22:26 | 0 | 0 | 5507.423 | 22:26 | 2.9709 | 2.7309 | 0.23997 | 3.1872e-05 | 0
[13 empty] | 22:26 | 0.89743 | 0.91146 | 0 |  | 22:26 | 0 | 0 | 5507.423 | 22:26 | 2.9715 | 2.7315 | 0.24001 | 3.1879e-05 | 0
[13 empty] | 22:26 | 0.88683 | 0.91146 | 0 |  | 22:26 | 0 | 0 | 5507.423 | 22:26 | 2.9719 | 2.7319 | 0.24005 | 3.1885e-05 | 0
[13 empty] | 22:27 | 0.87645 | 0.91146 | 0 |  | 22:27 | 0 | 0 | 5507.423 | 22:27 | 2.9726 | 2.7324 | 0.24009 | 3.1891e-05 | 0
[13 empty] | 22:27 | 0.86628 | 0.91146 | 0 |  | 22:27 | 0 | 0 | 5507.423 | 22:27 | 2.973 | 2.7328 | 0.24015 | 3.1895e-05 | 0
[13 empty] | 22:27 | 0.85633 | 0.91146 | 0 |  | 22:27 | 0 | 0 | 5507.423 | 22:27 | 2.9736 | 2.7334 | 0.24018 | 3.19e-05 | 0
[13 empty] | 22:28 | 0.84657 | 0.91146 | 0 |  | 22:28 | 0 | 0 | 5507.423 | 22:28 | 2.974 | 2.7338 | 0.24022 | 3.1906e-05 | 0
[13 empty] | 22:28 | 0.83702 | 0.91146 | 0 |  | 22:28 | 0 | 0 | 5507.423 | 22:28 | 2.9746 | 2.7343 | 0.24026 | 3.1912e-05 | 0
[13 empty] | 22:28 | 0.82766 | 0.91146 | 0 |  | 22:28 | 0 | 0 | 5507.423 | 22:28 | 2.9751 | 2.7347 | 0.2403 | 3.1918e-05 | 0
[13 empty] | 22:28 | 0.8185 | 0.91146 | 0 |  | 22:28 | 0 | 0 | 5507.423 | 22:28 | 2.9755 | 2.7351 | 0.24034 | 3.1923e-05 | 0
[13 empty] | 22:28 | 0.80952 | 0.91146 | 0 |  | 22:28 | 0 | 0 | 5507.423 | 22:28 | 2.9761 | 2.7357 | 0.24037 | 3.1927e-05 | 0
[13 empty] | 22:29 | 0.80073 | 0.91146 | 0 |  | 22:29 | 0 | 0 | 5507.423 | 22:29 | 2.9765 | 2.7361 | 0.24041 | 3.1933e-05 | 0
[13 empty] | 22:29 | 0.79211 | 0.91146 | 0 |  | 22:29 | 0 | 0 | 5507.423 | 22:29 | 2.9769 | 2.7364 | 0.24045 | 3.1939e-05 | 0
[13 empty] | 22:29 | 0.78368 | 0.91146 | 0 |  | 22:29 | 0 | 0 | 5507.423 | 22:29 | 2.9775 | 2.737 | 0.24049 | 3.1944e-05 | 0
[13 empty] | 22:30 | 0.77542 | 0.91146 | 0 |  | 22:30 | 0 | 0 | 5507.423 | 22:30 | 2.978 | 2.7374 | 0.24053 | 3.1948e-05 | 0
[13 empty] | 22:30 | 0.76733 | 0.91146 | 0 |  | 22:30 | 0 | 0 | 5507.423 | 22:30 | 2.9784 | 2.7378 | 0.24057 | 3.1954e-05 | 0
[13 empty] | 22:30 | 0.7594 | 0.91146 | 0 |  | 22:30 | 0 | 0 | 5507.423 | 22:30 | 2.9788 | 2.7382 | 0.2406 | 3.1958e-05 | 0
[13 empty] | 22:30 | 0.75164 | 0.91146 | 0 |  | 22:30 | 0 | 0 | 5507.423 | 22:30 | 2.9794 | 2.7387 | 0.24064 | 3.1963e-05 | 0
[13 empty] | 22:30 | 0.74403 | 0.91146 | 0 |  | 22:30 | 0 | 0 | 5507.423 | 22:30 | 2.9798 | 2.7391 | 0.24068 | 3.1967e-05 | 0
[13 empty] | 22:31 | 0.73658 | 0.91146 | 0 |  | 22:31 | 0 | 0 | 5507.423 | 22:31 | 2.9803 | 2.7395 | 0.24072 | 3.1973e-05 | 0
[13 empty] | 22:31 | 0.72929 | 0.91146 | 0 |  | 22:31 | 0 | 0 | 5507.423 | 22:31 | 2.9807 | 2.7399 | 0.24076 | 3.1977e-05 | 0
[13 empty] | 22:31 | 1.1629 | 0.91146 | 0 |  | 22:31 | 0 | 0 | 5507.423 | 22:31 | 2.9813 | 2.7405 | 0.24081 | 3.1984e-05 | 0
[13 empty] | 22:32 | 1.1468 | 0.91146 | 0 |  | 22:32 | 0 | 0 | 5507.423 | 22:32 | 2.9821 | 2.7412 | 0.24087 | 3.1992e-05 | 0
[13 empty] | 22:32 | 1.1311 | 0.91146 | 0 |  | 22:32 | 0 | 0 | 5507.423 | 22:32 | 2.9828 | 2.7418 | 0.24093 | 3.2e-05 | 0
[13 empty] | 22:32 | 1.1157 | 0.91146 | 0 |  | 22:32 | 0 | 0 | 5507.423 | 22:32 | 2.9834 | 2.7424 | 0.24099 | 3.2007e-05 | 0
[13 empty] | 22:32 | 1.1006 | 0.91146 | 0 |  | 22:32 | 0 | 0 | 5507.423 | 22:32 | 2.984 | 2.7429 | 0.24102 | 3.2015e-05 | 0
[13 empty] | 22:32 | 1.0859 | 0.91146 | 0 |  | 22:32 | 0 | 0 | 5507.423 | 22:32 | 2.9848 | 2.7437 | 0.24108 | 3.2021e-05 | 0
[13 empty] | 22:33 | 1.0714 | 0.91146 | 0 |  | 22:33 | 0 | 0 | 5507.423 | 22:33 | 2.9854 | 2.7443 | 0.24114 | 3.2028e-05 | 0
[13 empty] | 22:33 | 1.0572 | 0.91146 | 0 |  | 22:33 | 0 | 0 | 5507.423 | 22:33 | 2.9861 | 2.7448 | 0.2412 | 3.2036e-05 | 0
[13 empty] | 22:33 | 1.0434 | 0.91146 | 0 |  | 22:33 | 0 | 0 | 5507.423 | 22:33 | 2.9867 | 2.7454 | 0.24123 | 3.2042e-05 | 0
[13 empty] | 22:34 | 1.0298 | 0.91146 | 0 |  | 22:34 | 0 | 0 | 5507.423 | 22:34 | 2.9873 | 2.746 | 0.24129 | 3.2049e-05 | 0
[13 empty] | 22:34 | 1.0164 | 0.91146 | 0 |  | 22:34 | 0 | 0 | 5507.423 | 22:34 | 2.9879 | 2.7466 | 0.24135 | 3.2055e-05 | 0
[13 empty] | 22:34 | 1.0034 | 0.91146 | 0 |  | 22:34 | 0 | 0 | 5507.423 | 22:34 | 2.9886 | 2.7471 | 0.24139 | 3.2063e-05 | 0
[13 empty] | 22:34 | 0.99062 | 0.91146 | 0 |  | 22:34 | 0 | 0 | 5507.423 | 22:34 | 2.9892 | 2.7477 | 0.24144 | 3.2068e-05 | 0
[13 empty] | 22:34 | 0.97811 | 0.91146 | 0 |  | 22:34 | 0 | 0 | 5507.423 | 22:34 | 2.9898 | 2.7483 | 0.24148 | 3.2074e-05 | 0
[13 empty] | 22:35 | 0.96585 | 0.91146 | 0 |  | 22:35 | 0 | 0 | 5507.423 | 22:35 | 2.9902 | 2.7487 | 0.24154 | 3.2082e-05 | 0
[13 empty] | 22:35 | 0.95385 | 0.91146 | 0 |  | 22:35 | 0 | 0 | 5507.423 | 22:35 | 2.9909 | 2.7492 | 0.24158 | 3.2088e-05 | 0
[13 empty] | 22:35 | 0.94209 | 0.91146 | 0 |  | 22:35 | 0 | 0 | 5507.423 | 22:35 | 2.9915 | 2.7498 | 0.24162 | 3.2093e-05 | 0
[13 empty] | 22:36 | 0.93058 | 0.91146 | 0 |  | 22:36 | 0 | 0 | 5507.423 | 22:36 | 2.9921 | 2.7504 | 0.24167 | 3.2099e-05 | 0
[13 empty] | 22:36 | 0.9193 | 0.91146 | 0 |  | 22:36 | 0 | 0 | 5507.423 | 22:36 | 2.9925 | 2.7508 | 0.24171 | 3.2105e-05 | 0
[13 empty] | 22:36 | 0.90825 | 0.91146 | 0 |  | 22:36 | 0 | 0 | 5507.423 | 22:36 | 2.9931 | 2.7513 | 0.24177 | 3.211e-05 | 0
[13 empty] | 22:36 | 0.89743 | 0.91146 | 0 |  | 22:36 | 0 | 0 | 5507.423 | 22:36 | 2.9938 | 2.7519 | 0.24181 | 3.2116e-05 | 0
[13 empty] | 22:36 | 0.88683 | 0.91146 | 0 |  | 22:36 | 0 | 0 | 5507.423 | 22:36 | 2.9942 | 2.7523 | 0.24185 | 3.2122e-05 | 0
[13 empty] | 22:37 | 0.87645 | 0.91146 | 0 |  | 22:37 | 0 | 0 | 5507.423 | 22:37 | 2.9948 | 2.7529 | 0.24188 | 3.2128e-05 | 0
[13 empty] | 22:37 | 0.86628 | 0.91146 | 0 |  | 22:37 | 0 | 0 | 5507.423 | 22:37 | 2.9952 | 2.7533 | 0.24194 | 3.2133e-05 | 0
[13 empty] | 22:37 | 0.85633 | 0.91146 | 0 |  | 22:37 | 0 | 0 | 5507.423 | 22:37 | 2.9958 | 2.7538 | 0.24198 | 3.2139e-05 | 0
[13 empty] | 22:38 | 0.84657 | 0.91146 | 0 |  | 22:38 | 0 | 0 | 5507.423 | 22:38 | 2.9963 | 2.7542 | 0.24202 | 3.2145e-05 | 0
[13 empty] | 22:38 | 0.83702 | 0.91146 | 0 |  | 22:38 | 0 | 0 | 5507.423 | 22:38 | 2.9969 | 2.7548 | 0.24206 | 3.2151e-05 | 0
[13 empty] | 22:38 | 0.82766 | 0.91146 | 0 |  | 22:38 | 0 | 0 | 5507.423 | 22:38 | 2.9973 | 2.7552 | 0.24209 | 3.2156e-05 | 0
[13 empty] | 22:38 | 0.8185 | 0.91146 | 0 |  | 22:38 | 0 | 0 | 5507.423 | 22:38 | 2.9977 | 2.7555 | 0.24213 | 3.2162e-05 | 0
[13 empty] | 22:38 | 0.80952 | 0.91146 | 0 |  | 22:38 | 0 | 0 | 5507.423 | 22:38 | 2.9983 | 2.7561 | 0.24217 | 3.2166e-05 | 0
[13 empty] | 22:39 | 0.80073 | 0.91146 | 0 |  | 22:39 | 0 | 0 | 5507.423 | 22:39 | 2.9987 | 2.7565 | 0.24221 | 3.2172e-05 | 0
[13 empty] | 22:39 | 0.79211 | 0.91146 | 0 |  | 22:39 | 0 | 0 | 5507.423 | 22:39 | 2.9992 | 2.7569 | 0.24225 | 3.2177e-05 | 0
[13 empty] | 22:39 | 0.78368 | 0.91146 | 0 |  | 22:39 | 0 | 0 | 5507.423 | 22:39 | 2.9998 | 2.7575 | 0.24228 | 3.2181e-05 | 0
[13 empty] | 22:40 | 0.77542 | 0.91146 | 0 |  | 22:40 | 0 | 0 | 5507.423 | 22:40 | 3.0002 | 2.7578 | 0.24232 | 3.2187e-05 | 0
[13 empty] | 22:40 | 0.76733 | 0.91146 | 0 |  | 22:40 | 0 | 0 | 5507.423 | 22:40 | 3.0006 | 2.7582 | 0.24236 | 3.2193e-05 | 0
[13 empty] | 22:40 | 0.7594 | 0.91146 | 0 |  | 22:40 | 0 | 0 | 5507.423 | 22:40 | 3.001 | 2.7586 | 0.2424 | 3.2196e-05 | 0
[13 empty] | 22:40 | 0.75164 | 0.91146 | 0 |  | 22:40 | 0 | 0 | 5507.423 | 22:40 | 3.0016 | 2.7592 | 0.24244 | 3.2202e-05 | 0
[13 empty] | 22:40 | 0.74403 | 0.91146 | 0 |  | 22:40 | 0 | 0 | 5507.423 | 22:40 | 3.0021 | 2.7596 | 0.24248 | 3.2206e-05 | 0
[13 empty] | 22:41 | 0.73658 | 0.91146 | 0 |  | 22:41 | 0 | 0 | 5507.423 | 22:41 | 3.0025 | 2.7599 | 0.24251 | 3.2212e-05 | 0
[13 empty] | 22:41 | 0.72929 | 0.91146 | 0 |  | 22:41 | 0 | 0 | 5507.423 | 22:41 | 3.0029 | 2.7603 | 0.24255 | 3.2216e-05 | 0
[13 empty] | 22:41 | 1.1629 | 0.91146 | 0 |  | 22:41 | 0 | 0 | 5507.423 | 22:41 | 3.0035 | 2.7609 | 0.24261 | 3.2223e-05 | 0
[13 empty] | 22:42 | 1.1468 | 0.91146 | 0 |  | 22:42 | 0 | 0 | 5507.423 | 22:42 | 3.0044 | 2.7617 | 0.24267 | 3.2231e-05 | 0
[13 empty] | 22:42 | 1.1311 | 0.91146 | 0 |  | 22:42 | 0 | 0 | 5507.423 | 22:42 | 3.005 | 2.7622 | 0.24272 | 3.2238e-05 | 0
[13 empty] | 22:42 | 1.1157 | 0.91146 | 0 |  | 22:42 | 0 | 0 | 5507.423 | 22:42 | 3.0056 | 2.7628 | 0.24278 | 3.2246e-05 | 0
[13 empty] | 22:42 | 1.1006 | 0.91146 | 0 |  | 22:42 | 0 | 0 | 5507.423 | 22:42 | 3.0062 | 2.7634 | 0.24282 | 3.2254e-05 | 0
[13 empty] | 22:42 | 1.0859 | 0.91146 | 0 |  | 22:42 | 0 | 0 | 5507.423 | 22:42 | 3.007 | 2.7641 | 0.24288 | 3.2259e-05 | 0
[13 empty] | 22:43 | 1.0714 | 0.91146 | 0 |  | 22:43 | 0 | 0 | 5507.423 | 22:43 | 3.0077 | 2.7647 | 0.24293 | 3.2267e-05 | 0
[13 empty] | 22:43 | 1.0572 | 0.91146 | 0 |  | 22:43 | 0 | 0 | 5507.423 | 22:43 | 3.0083 | 2.7653 | 0.24299 | 3.2273e-05 | 0
[13 empty] | 22:43 | 1.0434 | 0.91146 | 0 |  | 22:43 | 0 | 0 | 5507.423 | 22:43 | 3.0089 | 2.7659 | 0.24303 | 3.228e-05 | 0
[13 empty] | 22:44 | 1.0298 | 0.91146 | 0 |  | 22:44 | 0 | 0 | 5507.423 | 22:44 | 3.0096 | 2.7664 | 0.24309 | 3.2288e-05 | 0
[13 empty] | 22:44 | 1.0164 | 0.91146 | 0 |  | 22:44 | 0 | 0 | 5507.423 | 22:44 | 3.0102 | 2.767 | 0.24314 | 3.2294e-05 | 0
[13 empty] | 22:44 | 1.0034 | 0.91146 | 0 |  | 22:44 | 0 | 0 | 5507.423 | 22:44 | 3.0108 | 2.7676 | 0.24318 | 3.23e-05 | 0
[13 empty] | 22:44 | 0.99062 | 0.91146 | 0 |  | 22:44 | 0 | 0 | 5507.423 | 22:44 | 3.0114 | 2.7682 | 0.24324 | 3.2307e-05 | 0
[13 empty] | 22:44 | 0.97811 | 0.91146 | 0 |  | 22:44 | 0 | 0 | 5507.423 | 22:44 | 3.0118 | 2.7685 | 0.24328 | 3.2313e-05 | 0
[13 empty] | 22:45 | 0.96585 | 0.91146 | 0 |  | 22:45 | 0 | 0 | 5507.423 | 22:45 | 3.0125 | 2.7691 | 0.24334 | 3.2319e-05 | 0
[13 empty] | 22:45 | 0.95385 | 0.91146 | 0 |  | 22:45 | 0 | 0 | 5507.423 | 22:45 | 3.0131 | 2.7697 | 0.24337 | 3.2326e-05 | 0
[13 empty] | 22:45 | 0.94209 | 0.91146 | 0 |  | 22:45 | 0 | 0 | 5507.423 | 22:45 | 3.0137 | 2.7703 | 0.24341 | 3.2332e-05 | 0
[13 empty] | 22:46 | 0.93058 | 0.91146 | 0 |  | 22:46 | 0 | 0 | 5507.423 | 22:46 | 3.0143 | 2.7708 | 0.24347 | 3.2338e-05 | 0
[13 empty] | 22:46 | 0.9193 | 0.91146 | 0 |  | 22:46 | 0 | 0 | 5507.423 | 22:46 | 3.0147 | 2.7712 | 0.24351 | 3.2343e-05 | 0
[13 empty] | 22:46 | 0.90825 | 0.91146 | 0 |  | 22:46 | 0 | 0 | 5507.423 | 22:46 | 3.0154 | 2.7718 | 0.24356 | 3.2349e-05 | 0
[13 empty] | 22:46 | 0.89743 | 0.91146 | 0 |  | 22:46 | 0 | 0 | 5507.423 | 22:46 | 3.0158 | 2.7722 | 0.2436 | 3.2355e-05 | 0
[13 empty] | 22:46 | 0.88683 | 0.91146 | 0 |  | 22:46 | 0 | 0 | 5507.423 | 22:46 | 3.0164 | 2.7727 | 0.24364 | 3.2361e-05 | 0
[13 empty] | 22:47 | 0.87645 | 0.91146 | 0 |  | 22:47 | 0 | 0 | 5507.423 | 22:47 | 3.017 | 2.7733 | 0.24368 | 3.2366e-05 | 0
[13 empty] | 22:47 | 0.86628 | 0.91146 | 0 |  | 22:47 | 0 | 0 | 5507.423 | 22:47 | 3.0175 | 2.7737 | 0.24374 | 3.2372e-05 | 0
[13 empty] | 22:47 | 0.85633 | 0.91146 | 0 |  | 22:47 | 0 | 0 | 5507.423 | 22:47 | 3.0181 | 2.7743 | 0.24377 | 3.2378e-05 | 0
[13 empty] | 22:48 | 0.84657 | 0.91146 | 0 |  | 22:48 | 0 | 0 | 5507.423 | 22:48 | 3.0185 | 2.7746 | 0.24381 | 3.2384e-05 | 0
[13 empty] | 22:48 | 0.83702 | 0.91146 | 0 |  | 22:48 | 0 | 0 | 5507.423 | 22:48 | 3.0191 | 2.7752 | 0.24385 | 3.2389e-05 | 0
[13 empty] | 22:48 | 0.82766 | 0.91146 | 0 |  | 22:48 | 0 | 0 | 5507.423 | 22:48 | 3.0195 | 2.7756 | 0.24389 | 3.2395e-05 | 0
[13 empty] | 22:48 | 0.8185 | 0.91146 | 0 |  | 22:48 | 0 | 0 | 5507.423 | 22:48 | 3.0199 | 2.776 | 0.24393 | 3.2399e-05 | 0
[13 empty] | 22:48 | 0.80952 | 0.91146 | 0 |  | 22:48 | 0 | 0 | 5507.423 | 22:48 | 3.0206 | 2.7766 | 0.24397 | 3.2405e-05 | 0
[13 empty] | 22:49 | 0.80073 | 0.91146 | 0 |  | 22:49 | 0 | 0 | 5507.423 | 22:49 | 3.021 | 2.7769 | 0.244 | 3.241e-05 | 0
[13 empty] | 22:49 | 0.79211 | 0.91146 | 0 |  | 22:49 | 0 | 0 | 5507.423 | 22:49 | 3.0214 | 2.7773 | 0.24404 | 3.2416e-05 | 0
[13 empty] | 22:49 | 0.78368 | 0.91146 | 0 |  | 22:49 | 0 | 0 | 5507.423 | 22:49 | 3.022 | 2.7779 | 0.24408 | 3.242e-05 | 0
[13 empty] | 22:50 | 0.77542 | 0.91146 | 0 |  | 22:50 | 0 | 0 | 5507.423 | 22:50 | 3.0224 | 2.7783 | 0.24412 | 3.2426e-05 | 0
[13 empty] | 22:50 | 0.76733 | 0.91146 | 0 |  | 22:50 | 0 | 0 | 5507.423 | 22:50 | 3.0228 | 2.7787 | 0.24416 | 3.2431e-05 | 0
[13 empty] | 22:50 | 0.7594 | 0.91146 | 0 |  | 22:50 | 0 | 0 | 5507.423 | 22:50 | 3.0233 | 2.779 | 0.24419 | 3.2435e-05 | 0
[13 empty] | 22:50 | 0.75164 | 0.91146 | 0 |  | 22:50 | 0 | 0 | 5507.423 | 22:50 | 3.0239 | 2.7796 | 0.24423 | 3.2441e-05 | 0
[13 empty] | 22:50 | 0.74403 | 0.91146 | 0 |  | 22:50 | 0 | 0 | 5507.423 | 22:50 | 3.0243 | 2.78 | 0.24427 | 3.2445e-05 | 0
[13 empty] | 22:51 | 0.73658 | 0.91146 | 0 |  | 22:51 | 0 | 0 | 5507.423 | 22:51 | 3.0247 | 2.7804 | 0.24431 | 3.245e-05 | 0
[13 empty] | 22:51 | 0.72929 | 0.91146 | 0 |  | 22:51 | 0 | 0 | 5507.423 | 22:51 | 3.0251 | 2.7808 | 0.24435 | 3.2454e-05 | 0
[13 empty] | 22:51 | 1.1629 | 0.91146 | 0 |  | 22:51 | 0 | 0 | 5507.423 | 22:51 | 3.0258 | 2.7813 | 0.2444 | 3.2462e-05 | 0
[13 empty] | 22:52 | 1.1468 | 0.91146 | 0 |  | 22:52 | 0 | 0 | 5507.423 | 22:52 | 3.0266 | 2.7821 | 0.24446 | 3.247e-05 | 0
[13 empty] | 22:52 | 1.1311 | 0.91146 | 0 |  | 22:52 | 0 | 0 | 5507.423 | 22:52 | 3.0272 | 2.7827 | 0.24452 | 3.2477e-05 | 0
[13 empty] | 22:52 | 1.1157 | 0.91146 | 0 |  | 22:52 | 0 | 0 | 5507.423 | 22:52 | 3.0278 | 2.7832 | 0.24458 | 3.2485e-05 | 0
[13 empty] | 22:52 | 1.1006 | 0.91146 | 0 |  | 22:52 | 0 | 0 | 5507.423 | 22:52 | 3.0285 | 2.7838 | 0.24461 | 3.2491e-05 | 0
[13 empty] | 22:52 | 1.0859 | 0.91146 | 0 |  | 22:52 | 0 | 0 | 5507.423 | 22:52 | 3.0293 | 2.7846 | 0.24467 | 3.2498e-05 | 0
[13 empty] | 22:53 | 1.0714 | 0.91146 | 0 |  | 22:53 | 0 | 0 | 5507.423 | 22:53 | 3.0299 | 2.7851 | 0.24473 | 3.2506e-05 | 0
[13 empty] | 22:53 | 1.0572 | 0.91146 | 0 |  | 22:53 | 0 | 0 | 5507.423 | 22:53 | 3.0305 | 2.7857 | 0.24479 | 3.2512e-05 | 0
[13 empty] | 22:53 | 1.0434 | 0.91146 | 0 |  | 22:53 | 0 | 0 | 5507.423 | 22:53 | 3.0312 | 2.7863 | 0.24482 | 3.2519e-05 | 0
[13 empty] | 22:54 | 1.0298 | 0.91146 | 0 |  | 22:54 | 0 | 0 | 5507.423 | 22:54 | 3.0318 | 2.7869 | 0.24488 | 3.2525e-05 | 0
[13 empty] | 22:54 | 1.0164 | 0.91146 | 0 |  | 22:54 | 0 | 0 | 5507.423 | 22:54 | 3.0324 | 2.7874 | 0.24494 | 3.2533e-05 | 0
[13 empty] | 22:54 | 1.0034 | 0.91146 | 0 |  | 22:54 | 0 | 0 | 5507.423 | 22:54 | 3.033 | 2.788 | 0.24498 | 3.2538e-05 | 0
[13 empty] | 22:54 | 0.99062 | 0.91146 | 0 |  | 22:54 | 0 | 0 | 5507.423 | 22:54 | 3.0337 | 2.7886 | 0.24503 | 3.2546e-05 | 0
[13 empty] | 22:55 | 0.97811 | 0.91146 | 0 |  | 22:55 | 0 | 0 | 5507.423 | 22:55 | 3.0341 | 2.789 | 0.24507 | 3.2552e-05 | 0
[13 empty] | 22:55 | 0.96585 | 0.91146 | 0 |  | 22:55 | 0 | 0 | 5507.423 | 22:55 | 3.0347 | 2.7895 | 0.24513 | 3.2557e-05 | 0
[13 empty] | 22:55 | 0.95385 | 0.91146 | 0 |  | 22:55 | 0 | 0 | 5507.423 | 22:55 | 3.0353 | 2.7901 | 0.24517 | 3.2563e-05 | 0
[13 empty] | 22:55 | 0.94209 | 0.91146 | 0 |  | 22:55 | 0 | 0 | 5507.423 | 22:55 | 3.0359 | 2.7907 | 0.24521 | 3.2571e-05 | 0
[13 empty] | 22:56 | 0.93058 | 0.91146 | 0 |  | 22:56 | 0 | 0 | 5507.423 | 22:56 | 3.0366 | 2.7913 | 0.24526 | 3.2576e-05 | 0
[13 empty] | 22:56 | 0.9193 | 0.91146 | 0 |  | 22:56 | 0 | 0 | 5507.423 | 22:56 | 3.037 | 2.7916 | 0.2453 | 3.2582e-05 | 0
[13 empty] | 22:56 | 0.90825 | 0.91146 | 0 |  | 22:56 | 0 | 0 | 5507.423 | 22:56 | 3.0376 | 2.7922 | 0.24536 | 3.2588e-05 | 0
[13 empty] | 22:56 | 0.89743 | 0.91146 | 0 |  | 22:56 | 0 | 0 | 5507.423 | 22:56 | 3.038 | 2.7926 | 0.2454 | 3.2594e-05 | 0
[13 empty] | 22:56 | 0.88683 | 0.91146 | 0 |  | 22:56 | 0 | 0 | 5507.423 | 22:56 | 3.0386 | 2.7932 | 0.24544 | 3.2599e-05 | 0
[13 empty] | 22:57 | 0.87645 | 0.91146 | 0 |  | 22:57 | 0 | 0 | 5507.423 | 22:57 | 3.0392 | 2.7937 | 0.24547 | 3.2605e-05 | 0
[13 empty] | 22:57 | 0.86628 | 0.91146 | 0 |  | 22:57 | 0 | 0 | 5507.423 | 22:57 | 3.0397 | 2.7941 | 0.24553 | 3.2611e-05 | 0
[13 empty] | 22:57 | 0.85633 | 0.91146 | 0 |  | 22:57 | 0 | 0 | 5507.423 | 22:57 | 3.0403 | 2.7947 | 0.24557 | 3.2617e-05 | 0
[13 empty] | 22:58 | 0.84657 | 0.91146 | 0 |  | 22:58 | 0 | 0 | 5507.423 | 22:58 | 3.0407 | 2.7951 | 0.24561 | 3.2622e-05 | 0
[13 empty] | 22:58 | 0.83702 | 0.91146 | 0 |  | 22:58 | 0 | 0 | 5507.423 | 22:58 | 3.0413 | 2.7957 | 0.24565 | 3.2628e-05 | 0
[13 empty] | 22:58 | 0.82766 | 0.91146 | 0 |  | 22:58 | 0 | 0 | 5507.423 | 22:58 | 3.0418 | 2.796 | 0.24568 | 3.2634e-05 | 0
[13 empty] | 22:58 | 0.8185 | 0.91146 | 0 |  | 22:58 | 0 | 0 | 5507.423 | 22:58 | 3.0422 | 2.7964 | 0.24572 | 3.2638e-05 | 0
[13 empty] | 22:59 | 0.80952 | 0.91146 | 0 |  | 22:59 | 0 | 0 | 5507.423 | 22:59 | 3.0428 | 2.797 | 0.24576 | 3.2643e-05 | 0
[13 empty] | 22:59 | 0.80073 | 0.91146 | 0 |  | 22:59 | 0 | 0 | 5507.423 | 22:59 | 3.0432 | 2.7974 | 0.2458 | 3.2649e-05 | 0
[13 empty] | 22:59 | 0.79211 | 0.91146 | 0 |  | 22:59 | 0 | 0 | 5507.423 | 22:59 | 3.0436 | 2.7978 | 0.24584 | 3.2653e-05 | 0
[13 empty] | 22:59 | 0.78368 | 0.91146 | 0 |  | 22:59 | 0 | 0 | 5507.423 | 22:59 | 3.0442 | 2.7983 | 0.24588 | 3.2659e-05 | 0
[13 empty] | 23:00 | 0.77542 | 0.91146 | 0 |  | 23:00 | 0 | 0 | 5507.423 | 23:00 | 3.0447 | 2.7987 | 0.24591 | 3.2664e-05 | 0
[13 empty] | 23:00 | 0.76733 | 0.91146 | 0 |  | 23:00 | 0 | 0 | 5507.423 | 23:00 | 3.0451 | 2.7991 | 0.24595 | 3.2668e-05 | 0
[13 empty] | 23:00 | 0.7594 | 0.91146 | 0 |  | 23:00 | 0 | 0 | 5507.423 | 23:00 | 3.0455 | 2.7995 | 0.24599 | 3.2674e-05 | 0
[13 empty] | 23:00 | 0.75164 | 0.91146 | 0 |  | 23:00 | 0 | 0 | 5507.423 | 23:00 | 3.0461 | 2.8 | 0.24603 | 3.268e-05 | 0
[13 empty] | 23:00 | 0.74403 | 0.91146 | 0 |  | 23:00 | 0 | 0 | 5507.423 | 23:00 | 3.0465 | 2.8004 | 0.24607 | 3.2683e-05 | 0
[13 empty] | 23:01 | 0.73658 | 0.91146 | 0 |  | 23:01 | 0 | 0 | 5507.423 | 23:01 | 3.0469 | 2.8008 | 0.2461 | 3.2689e-05 | 0
[13 empty] | 23:01 | 0.72929 | 0.91146 | 0 |  | 23:01 | 0 | 0 | 5507.423 | 23:01 | 3.0474 | 2.8012 | 0.24614 | 3.2693e-05 | 0
[13 empty] | 23:01 | 1.1629 | 0.91146 | 0 |  | 23:01 | 0 | 0 | 5507.423 | 23:01 | 3.048 | 2.8018 | 0.2462 | 3.2701e-05 | 0
[13 empty] | 23:02 | 1.1468 | 0.91146 | 0 |  | 23:02 | 0 | 0 | 5507.423 | 23:02 | 3.0488 | 2.8025 | 0.24626 | 3.2708e-05 | 0
[13 empty] | 23:02 | 1.1311 | 0.91146 | 0 |  | 23:02 | 0 | 0 | 5507.423 | 23:02 | 3.0494 | 2.8031 | 0.24631 | 3.2716e-05 | 0
[13 empty] | 23:02 | 1.1157 | 0.91146 | 0 |  | 23:02 | 0 | 0 | 5507.423 | 23:02 | 3.0501 | 2.8037 | 0.24637 | 3.2724e-05 | 0
[13 empty] | 23:02 | 1.1006 | 0.91146 | 0 |  | 23:02 | 0 | 0 | 5507.423 | 23:02 | 3.0507 | 2.8042 | 0.24641 | 3.2729e-05 | 0
[13 empty] | 23:03 | 1.0859 | 0.91146 | 0 |  | 23:03 | 0 | 0 | 5507.423 | 23:03 | 3.0515 | 2.805 | 0.24647 | 3.2737e-05 | 0
[13 empty] | 23:03 | 1.0714 | 0.91146 | 0 |  | 23:03 | 0 | 0 | 5507.423 | 23:03 | 3.0521 | 2.8056 | 0.24652 | 3.2745e-05 | 0
[13 empty] | 23:03 | 1.0572 | 0.91146 | 0 |  | 23:03 | 0 | 0 | 5507.423 | 23:03 | 3.0528 | 2.8062 | 0.24658 | 3.275e-05 | 0
[13 empty] | 23:03 | 1.0434 | 0.91146 | 0 |  | 23:03 | 0 | 0 | 5507.423 | 23:03 | 3.0534 | 2.8067 | 0.24662 | 3.2758e-05 | 0
[13 empty] | 23:04 | 1.0298 | 0.91146 | 0 |  | 23:04 | 0 | 0 | 5507.423 | 23:04 | 3.054 | 2.8073 | 0.24668 | 3.2764e-05 | 0
[13 empty] | 23:04 | 1.0164 | 0.91146 | 0 |  | 23:04 | 0 | 0 | 5507.423 | 23:04 | 3.0546 | 2.8079 | 0.24673 | 3.2771e-05 | 0
[13 empty] | 23:04 | 1.0034 | 0.91146 | 0 |  | 23:04 | 0 | 0 | 5507.423 | 23:04 | 3.0553 | 2.8084 | 0.24677 | 3.2777e-05 | 0
[13 empty] | 23:04 | 0.99062 | 0.91146 | 0 |  | 23:04 | 0 | 0 | 5507.423 | 23:04 | 3.0559 | 2.809 | 0.24683 | 3.2783e-05 | 0
[13 empty] | 23:04 | 0.97811 | 0.91146 | 0 |  | 23:04 | 0 | 0 | 5507.423 | 23:04 | 3.0563 | 2.8094 | 0.24687 | 3.279e-05 | 0
[13 empty] | 23:05 | 0.96585 | 0.91146 | 0 |  | 23:05 | 0 | 0 | 5507.423 | 23:05 | 3.0569 | 2.81 | 0.24693 | 3.2796e-05 | 0
[13 empty] | 23:05 | 0.95385 | 0.91146 | 0 |  | 23:05 | 0 | 0 | 5507.423 | 23:05 | 3.0575 | 2.8105 | 0.24696 | 3.2802e-05 | 0
[13 empty] | 23:05 | 0.94209 | 0.91146 | 0 |  | 23:05 | 0 | 0 | 5507.423 | 23:05 | 3.0582 | 2.8111 | 0.24702 | 3.2809e-05 | 0
[13 empty] | 23:06 | 0.93058 | 0.91146 | 0 |  | 23:06 | 0 | 0 | 5507.423 | 23:06 | 3.0588 | 2.8117 | 0.24706 | 3.2815e-05 | 0
[13 empty] | 23:06 | 0.9193 | 0.91146 | 0 |  | 23:06 | 0 | 0 | 5507.423 | 23:06 | 3.0592 | 2.8121 | 0.2471 | 3.2821e-05 | 0
[13 empty] | 23:06 | 0.90825 | 0.91146 | 0 |  | 23:06 | 0 | 0 | 5507.423 | 23:06 | 3.0598 | 2.8126 | 0.24715 | 3.2827e-05 | 0
[13 empty] | 23:06 | 0.89743 | 0.91146 | 0 |  | 23:06 | 0 | 0 | 5507.423 | 23:06 | 3.0603 | 2.813 | 0.24719 | 3.2832e-05 | 0
[13 empty] | 23:06 | 0.88683 | 0.91146 | 0 |  | 23:06 | 0 | 0 | 5507.423 | 23:06 | 3.0609 | 2.8136 | 0.24723 | 3.2838e-05 | 0
[13 empty] | 23:07 | 0.87645 | 0.91146 | 0 |  | 23:07 | 0 | 0 | 5507.423 | 23:07 | 3.0615 | 2.8142 | 0.24727 | 3.2844e-05 | 0
[13 empty] | 23:07 | 0.86628 | 0.91146 | 0 |  | 23:07 | 0 | 0 | 5507.423 | 23:07 | 3.0619 | 2.8146 | 0.24733 | 3.285e-05 | 0
[13 empty] | 23:07 | 0.85633 | 0.91146 | 0 |  | 23:07 | 0 | 0 | 5507.423 | 23:07 | 3.0625 | 2.8151 | 0.24736 | 3.2855e-05 | 0
[13 empty] | 23:08 | 0.84657 | 0.91146 | 0 |  | 23:08 | 0 | 0 | 5507.423 | 23:08 | 3.063 | 2.8155 | 0.2474 | 3.2861e-05 | 0
[13 empty] | 23:08 | 0.83702 | 0.91146 | 0 |  | 23:08 | 0 | 0 | 5507.423 | 23:08 | 3.0636 | 2.8161 | 0.24744 | 3.2867e-05 | 0
[13 empty] | 23:08 | 0.82766 | 0.91146 | 0 |  | 23:08 | 0 | 0 | 5507.423 | 23:08 | 3.064 | 2.8165 | 0.24748 | 3.2871e-05 | 0
[13 empty] | 23:08 | 0.8185 | 0.91146 | 0 |  | 23:08 | 0 | 0 | 5507.423 | 23:08 | 3.0644 | 2.8169 | 0.24752 | 3.2876e-05 | 0
[13 empty] | 23:08 | 0.80952 | 0.91146 | 0 |  | 23:08 | 0 | 0 | 5507.423 | 23:08 | 3.065 | 2.8174 | 0.24756 | 3.2882e-05 | 0
[13 empty] | 23:09 | 0.80073 | 0.91146 | 0 |  | 23:09 | 0 | 0 | 5507.423 | 23:09 | 3.0654 | 2.8178 | 0.24759 | 3.2888e-05 | 0
[13 empty] | 23:09 | 0.79211 | 0.91146 | 0 |  | 23:09 | 0 | 0 | 5507.423 | 23:09 | 3.0659 | 2.8182 | 0.24763 | 3.2892e-05 | 0
[13 empty] | 23:09 | 0.78368 | 0.91146 | 0 |  | 23:09 | 0 | 0 | 5507.423 | 23:09 | 3.0665 | 2.8188 | 0.24767 | 3.2897e-05 | 0
[13 empty] | 23:10 | 0.77542 | 0.91146 | 0 |  | 23:10 | 0 | 0 | 5507.423 | 23:10 | 3.0669 | 2.8191 | 0.24771 | 3.2903e-05 | 0
[13 empty] | 23:10 | 0.76733 | 0.91146 | 0 |  | 23:10 | 0 | 0 | 5507.423 | 23:10 | 3.0673 | 2.8195 | 0.24775 | 3.2907e-05 | 0
[13 empty] | 23:10 | 0.7594 | 0.91146 | 0 |  | 23:10 | 0 | 0 | 5507.423 | 23:10 | 3.0677 | 2.8199 | 0.24779 | 3.2913e-05 | 0
[13 empty] | 23:10 | 0.75164 | 0.91146 | 0 |  | 23:10 | 0 | 0 | 5507.423 | 23:10 | 3.0681 | 2.8203 | 0.24782 | 3.2916e-05 | 0
[13 empty] | 23:10 | 0.74403 | 0.91146 | 0 |  | 23:10 | 0 | 0 | 5507.423 | 23:10 | 3.0688 | 2.8209 | 0.24786 | 3.2922e-05 | 0
[13 empty] | 23:11 | 0.73658 | 0.91146 | 0 |  | 23:11 | 0 | 0 | 5507.423 | 23:11 | 3.0692 | 2.8212 | 0.2479 | 3.2926e-05 | 0
[13 empty] | 23:11 | 0.72929 | 0.91146 | 0 |  | 23:11 | 0 | 0 | 5507.423 | 23:11 | 3.0696 | 2.8216 | 0.24794 | 3.2932e-05 | 0
[13 empty] | 23:11 | 1.1629 | 0.91146 | 0 |  | 23:11 | 0 | 0 | 5507.423 | 23:11 | 3.0702 | 2.8222 | 0.248 | 3.2939e-05 | 0
[13 empty] | 23:12 | 1.1468 | 0.91146 | 0 |  | 23:12 | 0 | 0 | 5507.423 | 23:12 | 3.071 | 2.823 | 0.24805 | 3.2947e-05 | 0
[13 empty] | 23:12 | 1.1311 | 0.91146 | 0 |  | 23:12 | 0 | 0 | 5507.423 | 23:12 | 3.0717 | 2.8235 | 0.24811 | 3.2955e-05 | 0
[13 empty] | 23:12 | 1.1157 | 0.91146 | 0 |  | 23:12 | 0 | 0 | 5507.423 | 23:12 | 3.0723 | 2.8241 | 0.24817 | 3.296e-05 | 0
[13 empty] | 23:12 | 1.1006 | 0.91146 | 0 |  | 23:12 | 0 | 0 | 5507.423 | 23:12 | 3.0729 | 2.8247 | 0.24821 | 3.2968e-05 | 0
[13 empty] | 23:12 | 1.0859 | 0.91146 | 0 |  | 23:12 | 0 | 0 | 5507.423 | 23:12 | 3.0737 | 2.8254 | 0.24826 | 3.2976e-05 | 0
[13 empty] | 23:13 | 1.0714 | 0.91146 | 0 |  | 23:13 | 0 | 0 | 5507.423 | 23:13 | 3.0744 | 2.826 | 0.24832 | 3.2981e-05 | 0
[13 empty] | 23:13 | 1.0572 | 0.91146 | 0 |  | 23:13 | 0 | 0 | 5507.423 | 23:13 | 3.075 | 2.8266 | 0.24838 | 3.2989e-05 | 0
[13 empty] | 23:13 | 1.0434 | 0.91146 | 0 |  | 23:13 | 0 | 0 | 5507.423 | 23:13 | 3.0756 | 2.8272 | 0.24842 | 3.2997e-05 | 0
[13 empty] | 23:14 | 1.0298 | 0.91146 | 0 |  | 23:14 | 0 | 0 | 5507.423 | 23:14 | 3.0762 | 2.8277 | 0.24847 | 3.3002e-05 | 0
[13 empty] | 23:14 | 1.0164 | 0.91146 | 0 |  | 23:14 | 0 | 0 | 5507.423 | 23:14 | 3.0769 | 2.8283 | 0.24853 | 3.301e-05 | 0
[13 empty] | 23:14 | 1.0034 | 0.91146 | 0 |  | 23:14 | 0 | 0 | 5507.423 | 23:14 | 3.0775 | 2.8289 | 0.24857 | 3.3016e-05 | 0
[13 empty] | 23:14 | 0.99062 | 0.91146 | 0 |  | 23:14 | 0 | 0 | 5507.423 | 23:14 | 3.0781 | 2.8295 | 0.24863 | 3.3021e-05 | 0
[13 empty] | 23:14 | 0.97811 | 0.91146 | 0 |  | 23:14 | 0 | 0 | 5507.423 | 23:14 | 3.0785 | 2.8298 | 0.24866 | 3.3029e-05 | 0
[13 empty] | 23:15 | 0.96585 | 0.91146 | 0 |  | 23:15 | 0 | 0 | 5507.423 | 23:15 | 3.0792 | 2.8304 | 0.24872 | 3.3035e-05 | 0
[13 empty] | 23:15 | 0.95385 | 0.91146 | 0 |  | 23:15 | 0 | 0 | 5507.423 | 23:15 | 3.0798 | 2.831 | 0.24876 | 3.3041e-05 | 0
[13 empty] | 23:15 | 0.94209 | 0.91146 | 0 |  | 23:15 | 0 | 0 | 5507.423 | 23:15 | 3.0804 | 2.8316 | 0.24882 | 3.3046e-05 | 0
[13 empty] | 23:16 | 0.93058 | 0.91146 | 0 |  | 23:16 | 0 | 0 | 5507.423 | 23:16 | 3.0808 | 2.8319 | 0.24885 | 3.3054e-05 | 0
[13 empty] | 23:16 | 0.9193 | 0.91146 | 0 |  | 23:16 | 0 | 0 | 5507.423 | 23:16 | 3.0814 | 2.8325 | 0.24889 | 3.306e-05 | 0
[13 empty] | 23:16 | 0.90825 | 0.91146 | 0 |  | 23:16 | 0 | 0 | 5507.423 | 23:16 | 3.0821 | 2.8331 | 0.24895 | 3.3065e-05 | 0
[13 empty] | 23:16 | 0.89743 | 0.91146 | 0 |  | 23:16 | 0 | 0 | 5507.423 | 23:16 | 3.0825 | 2.8335 | 0.24899 | 3.3071e-05 | 0
[13 empty] | 23:16 | 0.88683 | 0.91146 | 0 |  | 23:16 | 0 | 0 | 5507.423 | 23:16 | 3.0831 | 2.834 | 0.24903 | 3.3077e-05 | 0
[13 empty] | 23:17 | 0.87645 | 0.91146 | 0 |  | 23:17 | 0 | 0 | 5507.423 | 23:17 | 3.0837 | 2.8346 | 0.24906 | 3.3083e-05 | 0
[13 empty] | 23:17 | 0.86628 | 0.91146 | 0 |  | 23:17 | 0 | 0 | 5507.423 | 23:17 | 3.0842 | 2.835 | 0.24912 | 3.3088e-05 | 0
[13 empty] | 23:17 | 0.85633 | 0.91146 | 0 |  | 23:17 | 0 | 0 | 5507.423 | 23:17 | 3.0848 | 2.8356 | 0.24916 | 3.3094e-05 | 0
[13 empty] | 23:18 | 0.84657 | 0.91146 | 0 |  | 23:18 | 0 | 0 | 5507.423 | 23:18 | 3.0852 | 2.836 | 0.2492 | 3.31e-05 | 0
[13 empty] | 23:18 | 0.83702 | 0.91146 | 0 |  | 23:18 | 0 | 0 | 5507.423 | 23:18 | 3.0858 | 2.8365 | 0.24924 | 3.3104e-05 | 0
[13 empty] | 23:18 | 0.82766 | 0.91146 | 0 |  | 23:18 | 0 | 0 | 5507.423 | 23:18 | 3.0862 | 2.8369 | 0.24927 | 3.3109e-05 | 0
[13 empty] | 23:18 | 0.8185 | 0.91146 | 0 |  | 23:18 | 0 | 0 | 5507.423 | 23:18 | 3.0866 | 2.8373 | 0.24931 | 3.3115e-05 | 0
[13 empty] | 23:18 | 0.80952 | 0.91146 | 0 |  | 23:18 | 0 | 0 | 5507.423 | 23:18 | 3.0872 | 2.8379 | 0.24935 | 3.3121e-05 | 0
[13 empty] | 23:19 | 0.80073 | 0.91146 | 0 |  | 23:19 | 0 | 0 | 5507.423 | 23:19 | 3.0877 | 2.8382 | 0.24939 | 3.3127e-05 | 0
[13 empty] | 23:19 | 0.79211 | 0.91146 | 0 |  | 23:19 | 0 | 0 | 5507.423 | 23:19 | 3.0881 | 2.8386 | 0.24943 | 3.313e-05 | 0
[13 empty] | 23:19 | 0.78368 | 0.91146 | 0 |  | 23:19 | 0 | 0 | 5507.423 | 23:19 | 3.0887 | 2.8392 | 0.24947 | 3.3136e-05 | 0
[13 empty] | 23:20 | 0.77542 | 0.91146 | 0 |  | 23:20 | 0 | 0 | 5507.423 | 23:20 | 3.0891 | 2.8396 | 0.2495 | 3.314e-05 | 0
[13 empty] | 23:20 | 0.76733 | 0.91146 | 0 |  | 23:20 | 0 | 0 | 5507.423 | 23:20 | 3.0895 | 2.84 | 0.24954 | 3.3146e-05 | 0
[13 empty] | 23:20 | 0.7594 | 0.91146 | 0 |  | 23:20 | 0 | 0 | 5507.423 | 23:20 | 3.09 | 2.8403 | 0.24958 | 3.3151e-05 | 0
[13 empty] | 23:20 | 0.75164 | 0.91146 | 0 |  | 23:20 | 0 | 0 | 5507.423 | 23:20 | 3.0904 | 2.8407 | 0.24962 | 3.3155e-05 | 0
[13 empty] | 23:20 | 0.74403 | 0.91146 | 0 |  | 23:20 | 0 | 0 | 5507.423 | 23:20 | 3.091 | 2.8413 | 0.24966 | 3.3161e-05 | 0
[13 empty] | 23:21 | 0.73658 | 0.91146 | 0 |  | 23:21 | 0 | 0 | 5507.423 | 23:21 | 3.0914 | 2.8417 | 0.2497 | 3.3165e-05 | 0
[13 empty] | 23:21 | 0.72929 | 0.91146 | 0 |  | 23:21 | 0 | 0 | 5507.423 | 23:21 | 3.0918 | 2.8421 | 0.24973 | 3.317e-05 | 0
[13 empty] | 23:21 | 1.1629 | 0.91146 | 0 |  | 23:21 | 0 | 0 | 5507.423 | 23:21 | 3.0925 | 2.8426 | 0.24979 | 3.3178e-05 | 0
[13 empty] | 23:22 | 1.1468 | 0.91146 | 0 |  | 23:22 | 0 | 0 | 5507.423 | 23:22 | 3.0933 | 2.8434 | 0.24985 | 3.3186e-05 | 0
[13 empty] | 23:22 | 1.1311 | 0.91146 | 0 |  | 23:22 | 0 | 0 | 5507.423 | 23:22 | 3.0939 | 2.844 | 0.24991 | 3.3191e-05 | 0
[13 empty] | 23:22 | 1.1157 | 0.91146 | 0 |  | 23:22 | 0 | 0 | 5507.423 | 23:22 | 3.0945 | 2.8445 | 0.24996 | 3.3199e-05 | 0
[13 empty] | 23:22 | 1.1006 | 0.91146 | 0 |  | 23:22 | 0 | 0 | 5507.423 | 23:22 | 3.0952 | 2.8451 | 0.25 | 3.3207e-05 | 0
[13 empty] | 23:22 | 1.0859 | 0.91146 | 0 |  | 23:22 | 0 | 0 | 5507.423 | 23:22 | 3.096 | 2.8459 | 0.25006 | 3.3214e-05 | 0
[13 empty] | 23:23 | 1.0714 | 0.91146 | 0 |  | 23:23 | 0 | 0 | 5507.423 | 23:23 | 3.0966 | 2.8465 | 0.25012 | 3.322e-05 | 0
[13 empty] | 23:23 | 1.0572 | 0.91146 | 0 |  | 23:23 | 0 | 0 | 5507.423 | 23:23 | 3.0972 | 2.847 | 0.25017 | 3.3228e-05 | 0
[13 empty] | 23:23 | 1.0434 | 0.91146 | 0 |  | 23:23 | 0 | 0 | 5507.423 | 23:23 | 3.0978 | 2.8476 | 0.25021 | 3.3233e-05 | 0
[13 empty] | 23:24 | 1.0298 | 0.91146 | 0 |  | 23:24 | 0 | 0 | 5507.423 | 23:24 | 3.0985 | 2.8482 | 0.25027 | 3.3241e-05 | 0
[13 empty] | 23:24 | 1.0164 | 0.91146 | 0 |  | 23:24 | 0 | 0 | 5507.423 | 23:24 | 3.0991 | 2.8487 | 0.25033 | 3.3247e-05 | 0
[13 empty] | 23:24 | 1.0034 | 0.91146 | 0 |  | 23:24 | 0 | 0 | 5507.423 | 23:24 | 3.0997 | 2.8493 | 0.25036 | 3.3254e-05 | 0
[13 empty] | 23:24 | 0.99062 | 0.91146 | 0 |  | 23:24 | 0 | 0 | 5507.423 | 23:24 | 3.1003 | 2.8499 | 0.25042 | 3.326e-05 | 0
[13 empty] | 23:24 | 0.97811 | 0.91146 | 0 |  | 23:24 | 0 | 0 | 5507.423 | 23:24 | 3.1008 | 2.8503 | 0.25046 | 3.3268e-05 | 0
[13 empty] | 23:25 | 0.96585 | 0.91146 | 0 |  | 23:25 | 0 | 0 | 5507.423 | 23:25 | 3.1014 | 2.8508 | 0.25052 | 3.3274e-05 | 0
[13 empty] | 23:25 | 0.95385 | 0.91146 | 0 |  | 23:25 | 0 | 0 | 5507.423 | 23:25 | 3.102 | 2.8514 | 0.25055 | 3.3279e-05 | 0
[13 empty] | 23:25 | 0.94209 | 0.91146 | 0 |  | 23:25 | 0 | 0 | 5507.423 | 23:25 | 3.1026 | 2.852 | 0.25061 | 3.3285e-05 | 0
[13 empty] | 23:26 | 0.93058 | 0.91146 | 0 |  | 23:26 | 0 | 0 | 5507.423 | 23:26 | 3.1031 | 2.8524 | 0.25065 | 3.3291e-05 | 0
[13 empty] | 23:26 | 0.9193 | 0.91146 | 0 |  | 23:26 | 0 | 0 | 5507.423 | 23:26 | 3.1037 | 2.8529 | 0.25069 | 3.3298e-05 | 0
[13 empty] | 23:26 | 0.90825 | 0.91146 | 0 |  | 23:26 | 0 | 0 | 5507.423 | 23:26 | 3.1043 | 2.8535 | 0.25075 | 3.3304e-05 | 0
[13 empty] | 23:26 | 0.89743 | 0.91146 | 0 |  | 23:26 | 0 | 0 | 5507.423 | 23:26 | 3.1047 | 2.8539 | 0.25078 | 3.331e-05 | 0
[13 empty] | 23:26 | 0.88683 | 0.91146 | 0 |  | 23:26 | 0 | 0 | 5507.423 | 23:26 | 3.1053 | 2.8545 | 0.25082 | 3.3316e-05 | 0
[13 empty] | 23:27 | 0.87645 | 0.91146 | 0 |  | 23:27 | 0 | 0 | 5507.423 | 23:27 | 3.1059 | 2.855 | 0.25086 | 3.3321e-05 | 0
[13 empty] | 23:27 | 0.86628 | 0.91146 | 0 |  | 23:27 | 0 | 0 | 5507.423 | 23:27 | 3.1064 | 2.8554 | 0.25092 | 3.3327e-05 | 0
[13 empty] | 23:27 | 0.85633 | 0.91146 | 0 |  | 23:27 | 0 | 0 | 5507.423 | 23:27 | 3.107 | 2.856 | 0.25096 | 3.3333e-05 | 0
[13 empty] | 23:27 | 0.84657 | 0.91146 | 0 |  | 23:27 | 0 | 0 | 5507.423 | 23:27 | 3.1074 | 2.8564 | 0.25099 | 3.3337e-05 | 0
[13 empty] | 23:28 | 0.83702 | 0.91146 | 0 |  | 23:28 | 0 | 0 | 5507.423 | 23:28 | 3.1078 | 2.8568 | 0.25103 | 3.3342e-05 | 0
[13 empty] | 23:28 | 0.82766 | 0.91146 | 0 |  | 23:28 | 0 | 0 | 5507.423 | 23:28 | 3.1084 | 2.8573 | 0.25107 | 3.3348e-05 | 0
[13 empty] | 23:28 | 0.8185 | 0.91146 | 0 |  | 23:28 | 0 | 0 | 5507.423 | 23:28 | 3.1089 | 2.8577 | 0.25111 | 3.3354e-05 | 0
[13 empty] | 23:28 | 0.80952 | 0.91146 | 0 |  | 23:28 | 0 | 0 | 5507.423 | 23:28 | 3.1095 | 2.8583 | 0.25115 | 3.336e-05 | 0
[13 empty] | 23:29 | 0.80073 | 0.91146 | 0 |  | 23:29 | 0 | 0 | 5507.423 | 23:29 | 3.1099 | 2.8587 | 0.25118 | 3.3363e-05 | 0
[13 empty] | 23:29 | 0.79211 | 0.91146 | 0 |  | 23:29 | 0 | 0 | 5507.423 | 23:29 | 3.1103 | 2.8591 | 0.25122 | 3.3369e-05 | 0
[13 empty] | 23:29 | 0.78368 | 0.91146 | 0 |  | 23:29 | 0 | 0 | 5507.423 | 23:29 | 3.1109 | 2.8596 | 0.25126 | 3.3375e-05 | 0
[13 empty] | 23:30 | 0.77542 | 0.91146 | 0 |  | 23:30 | 0 | 0 | 5507.423 | 23:30 | 3.1113 | 2.86 | 0.2513 | 3.3379e-05 | 0
[13 empty] | 23:30 | 0.76733 | 0.91146 | 0 |  | 23:30 | 0 | 0 | 5507.423 | 23:30 | 3.1118 | 2.8604 | 0.25134 | 3.3384e-05 | 0
[13 empty] | 23:30 | 0.7594 | 0.91146 | 0 |  | 23:30 | 0 | 0 | 5507.423 | 23:30 | 3.1122 | 2.8608 | 0.25138 | 3.339e-05 | 0
[13 empty] | 23:30 | 0.75164 | 0.91146 | 0 |  | 23:30 | 0 | 0 | 5507.423 | 23:30 | 3.1126 | 2.8612 | 0.25141 | 3.3394e-05 | 0
[13 empty] | 23:30 | 0.74403 | 0.91146 | 0 |  | 23:30 | 0 | 0 | 5507.423 | 23:30 | 3.1132 | 2.8617 | 0.25145 | 3.34e-05 | 0
[13 empty] | 23:31 | 0.73658 | 0.91146 | 0 |  | 23:31 | 0 | 0 | 5507.423 | 23:31 | 3.1136 | 2.8621 | 0.25149 | 3.3403e-05 | 0
[13 empty] | 23:31 | 0.72929 | 0.91146 | 0 |  | 23:31 | 0 | 0 | 5507.423 | 23:31 | 3.1141 | 2.8625 | 0.25153 | 3.3409e-05 | 0
[13 empty] | 23:31 | 1.1629 | 0.91146 | 0 |  | 23:31 | 0 | 0 | 5507.423 | 23:31 | 3.1147 | 2.8631 | 0.25159 | 3.3417e-05 | 0
[13 empty] | 23:31 | 1.1468 | 0.91146 | 0 |  | 23:31 | 0 | 0 | 5507.423 | 23:31 | 3.1155 | 2.8638 | 0.25164 | 3.3423e-05 | 0
[13 empty] | 23:32 | 1.1311 | 0.91146 | 0 |  | 23:32 | 0 | 0 | 5507.423 | 23:32 | 3.1161 | 2.8644 | 0.2517 | 3.343e-05 | 0
[13 empty] | 23:32 | 1.1157 | 0.91146 | 0 |  | 23:32 | 0 | 0 | 5507.423 | 23:32 | 3.1168 | 2.865 | 0.25176 | 3.3438e-05 | 0
[13 empty] | 23:32 | 1.1006 | 0.91146 | 0 |  | 23:32 | 0 | 0 | 5507.423 | 23:32 | 3.1174 | 2.8656 | 0.2518 | 3.3445e-05 | 0
[13 empty] | 23:32 | 1.0859 | 0.91146 | 0 |  | 23:32 | 0 | 0 | 5507.423 | 23:32 | 3.1182 | 2.8663 | 0.25185 | 3.3453e-05 | 0
[13 empty] | 23:33 | 1.0714 | 0.91146 | 0 |  | 23:33 | 0 | 0 | 5507.423 | 23:33 | 3.1188 | 2.8669 | 0.25191 | 3.3459e-05 | 0
[13 empty] | 23:33 | 1.0572 | 0.91146 | 0 |  | 23:33 | 0 | 0 | 5507.423 | 23:33 | 3.1195 | 2.8675 | 0.25197 | 3.3466e-05 | 0
[13 empty] | 23:33 | 1.0434 | 0.91146 | 0 |  | 23:33 | 0 | 0 | 5507.423 | 23:33 | 3.1201 | 2.868 | 0.25201 | 3.3472e-05 | 0
[13 empty] | 23:34 | 1.0298 | 0.91146 | 0 |  | 23:34 | 0 | 0 | 5507.423 | 23:34 | 3.1207 | 2.8686 | 0.25206 | 3.348e-05 | 0
[13 empty] | 23:34 | 1.0164 | 0.91146 | 0 |  | 23:34 | 0 | 0 | 5507.423 | 23:34 | 3.1213 | 2.8692 | 0.25212 | 3.3486e-05 | 0
[13 empty] | 23:34 | 1.0034 | 0.91146 | 0 |  | 23:34 | 0 | 0 | 5507.423 | 23:34 | 3.1219 | 2.8698 | 0.25216 | 3.3493e-05 | 0
[13 empty] | 23:34 | 0.99062 | 0.91146 | 0 |  | 23:34 | 0 | 0 | 5507.423 | 23:34 | 3.1226 | 2.8703 | 0.25222 | 3.3499e-05 | 0
[13 empty] | 23:34 | 0.97811 | 0.91146 | 0 |  | 23:34 | 0 | 0 | 5507.423 | 23:34 | 3.123 | 2.8707 | 0.25225 | 3.3505e-05 | 0
[13 empty] | 23:35 | 0.96585 | 0.91146 | 0 |  | 23:35 | 0 | 0 | 5507.423 | 23:35 | 3.1236 | 2.8713 | 0.25231 | 3.3512e-05 | 0
[13 empty] | 23:35 | 0.95385 | 0.91146 | 0 |  | 23:35 | 0 | 0 | 5507.423 | 23:35 | 3.1242 | 2.8719 | 0.25235 | 3.3518e-05 | 0
[13 empty] | 23:35 | 0.94209 | 0.91146 | 0 |  | 23:35 | 0 | 0 | 5507.423 | 23:35 | 3.1249 | 2.8724 | 0.25241 | 3.3524e-05 | 0
[13 empty] | 23:35 | 0.93058 | 0.91146 | 0 |  | 23:35 | 0 | 0 | 5507.423 | 23:35 | 3.1253 | 2.8728 | 0.25245 | 3.3529e-05 | 0
[13 empty] | 23:36 | 0.9193 | 0.91146 | 0 |  | 23:36 | 0 | 0 | 5507.423 | 23:36 | 3.1259 | 2.8734 | 0.25248 | 3.3535e-05 | 0
[13 empty] | 23:36 | 0.90825 | 0.91146 | 0 |  | 23:36 | 0 | 0 | 5507.423 | 23:36 | 3.1265 | 2.874 | 0.25254 | 3.3543e-05 | 0
[13 empty] | 23:36 | 0.89743 | 0.91146 | 0 |  | 23:36 | 0 | 0 | 5507.423 | 23:36 | 3.127 | 2.8743 | 0.25258 | 3.3549e-05 | 0
[13 empty] | 23:36 | 0.88683 | 0.91146 | 0 |  | 23:36 | 0 | 0 | 5507.423 | 23:36 | 3.1276 | 2.8749 | 0.25262 | 3.3554e-05 | 0
[13 empty] | 23:37 | 0.87645 | 0.91146 | 0 |  | 23:37 | 0 | 0 | 5507.423 | 23:37 | 3.1282 | 2.8755 | 0.25266 | 3.356e-05 | 0
[13 empty] | 23:37 | 0.86628 | 0.91146 | 0 |  | 23:37 | 0 | 0 | 5507.423 | 23:37 | 3.1286 | 2.8759 | 0.25271 | 3.3566e-05 | 0
[13 empty] | 23:37 | 0.85633 | 0.91146 | 0 |  | 23:37 | 0 | 0 | 5507.423 | 23:37 | 3.1292 | 2.8764 | 0.25275 | 3.357e-05 | 0
[13 empty] | 23:38 | 0.84657 | 0.91146 | 0 |  | 23:38 | 0 | 0 | 5507.423 | 23:38 | 3.1296 | 2.8768 | 0.25279 | 3.3575e-05 | 0
[13 empty] | 23:38 | 0.83702 | 0.91146 | 0 |  | 23:38 | 0 | 0 | 5507.423 | 23:38 | 3.1301 | 2.8772 | 0.25283 | 3.3581e-05 | 0
[13 empty] | 23:38 | 0.82766 | 0.91146 | 0 |  | 23:38 | 0 | 0 | 5507.423 | 23:38 | 3.1307 | 2.8778 | 0.25287 | 3.3587e-05 | 0
[13 empty] | 23:38 | 0.8185 | 0.91146 | 0 |  | 23:38 | 0 | 0 | 5507.423 | 23:38 | 3.1311 | 2.8782 | 0.2529 | 3.3593e-05 | 0
[13 empty] | 23:38 | 0.80952 | 0.91146 | 0 |  | 23:38 | 0 | 0 | 5507.423 | 23:38 | 3.1317 | 2.8787 | 0.25294 | 3.3598e-05 | 0
[13 empty] | 23:39 | 0.80073 | 0.91146 | 0 |  | 23:39 | 0 | 0 | 5507.423 | 23:39 | 3.1321 | 2.8791 | 0.25298 | 3.3602e-05 | 0
[13 empty] | 23:39 | 0.79211 | 0.91146 | 0 |  | 23:39 | 0 | 0 | 5507.423 | 23:39 | 3.1325 | 2.8795 | 0.25302 | 3.3608e-05 | 0
[13 empty] | 23:39 | 0.78368 | 0.91146 | 0 |  | 23:39 | 0 | 0 | 5507.423 | 23:39 | 3.1332 | 2.8801 | 0.25306 | 3.3614e-05 | 0
[13 empty] | 23:40 | 0.77542 | 0.91146 | 0 |  | 23:40 | 0 | 0 | 5507.423 | 23:40 | 3.1336 | 2.8804 | 0.25309 | 3.3617e-05 | 0
[13 empty] | 23:40 | 0.76733 | 0.91146 | 0 |  | 23:40 | 0 | 0 | 5507.423 | 23:40 | 3.134 | 2.8808 | 0.25313 | 3.3623e-05 | 0
[13 empty] | 23:40 | 0.7594 | 0.91146 | 0 |  | 23:40 | 0 | 0 | 5507.423 | 23:40 | 3.1344 | 2.8812 | 0.25317 | 3.3627e-05 | 0
[13 empty] | 23:40 | 0.75164 | 0.91146 | 0 |  | 23:40 | 0 | 0 | 5507.423 | 23:40 | 3.1348 | 2.8816 | 0.25321 | 3.3633e-05 | 0
[13 empty] | 23:40 | 0.74403 | 0.91146 | 0 |  | 23:40 | 0 | 0 | 5507.423 | 23:40 | 3.1354 | 2.8822 | 0.25325 | 3.3638e-05 | 0
[13 empty] | 23:41 | 0.73658 | 0.91146 | 0 |  | 23:41 | 0 | 0 | 5507.423 | 23:41 | 3.1359 | 2.8826 | 0.25329 | 3.3642e-05 | 0
[13 empty] | 23:41 | 0.72929 | 0.91146 | 0 |  | 23:41 | 0 | 0 | 5507.423 | 23:41 | 3.1363 | 2.8829 | 0.25332 | 3.3646e-05 | 0
[13 empty] | 23:41 | 1.1629 | 0.91146 | 0 |  | 23:41 | 0 | 0 | 5507.423 | 23:41 | 3.1369 | 2.8835 | 0.25338 | 3.3654e-05 | 0
[13 empty] | 23:42 | 1.1468 | 0.91146 | 0 |  | 23:42 | 0 | 0 | 5507.423 | 23:42 | 3.1377 | 2.8843 | 0.25344 | 3.3661e-05 | 0
[13 empty] | 23:42 | 1.1311 | 0.91146 | 0 |  | 23:42 | 0 | 0 | 5507.423 | 23:42 | 3.1384 | 2.8848 | 0.2535 | 3.3669e-05 | 0
[13 empty] | 23:42 | 1.1157 | 0.91146 | 0 |  | 23:42 | 0 | 0 | 5507.423 | 23:42 | 3.139 | 2.8854 | 0.25355 | 3.3677e-05 | 0
[13 empty] | 23:42 | 1.1006 | 0.91146 | 0 |  | 23:42 | 0 | 0 | 5507.423 | 23:42 | 3.1396 | 2.886 | 0.25359 | 3.3684e-05 | 0
[13 empty] | 23:42 | 1.0859 | 0.91146 | 0 |  | 23:42 | 0 | 0 | 5507.423 | 23:42 | 3.1404 | 2.8868 | 0.25365 | 3.369e-05 | 0
[13 empty] | 23:43 | 1.0714 | 0.91146 | 0 |  | 23:43 | 0 | 0 | 5507.423 | 23:43 | 3.1411 | 2.8873 | 0.25371 | 3.3698e-05 | 0
[13 empty] | 23:43 | 1.0572 | 0.91146 | 0 |  | 23:43 | 0 | 0 | 5507.423 | 23:43 | 3.1417 | 2.8879 | 0.25376 | 3.3705e-05 | 0
[13 empty] | 23:43 | 1.0434 | 0.91146 | 0 |  | 23:43 | 0 | 0 | 5507.423 | 23:43 | 3.1423 | 2.8885 | 0.2538 | 3.3711e-05 | 0
[13 empty] | 23:44 | 1.0298 | 0.91146 | 0 |  | 23:44 | 0 | 0 | 5507.423 | 23:44 | 3.1429 | 2.889 | 0.25386 | 3.3719e-05 | 0
[13 empty] | 23:44 | 1.0164 | 0.91146 | 0 |  | 23:44 | 0 | 0 | 5507.423 | 23:44 | 3.1436 | 2.8896 | 0.25392 | 3.3724e-05 | 0
[13 empty] | 23:44 | 1.0034 | 0.91146 | 0 |  | 23:44 | 0 | 0 | 5507.423 | 23:44 | 3.1442 | 2.8902 | 0.25395 | 3.3732e-05 | 0
[13 empty] | 23:44 | 0.99062 | 0.91146 | 0 |  | 23:44 | 0 | 0 | 5507.423 | 23:44 | 3.1448 | 2.8908 | 0.25401 | 3.3738e-05 | 0
[13 empty] | 23:44 | 0.97811 | 0.91146 | 0 |  | 23:44 | 0 | 0 | 5507.423 | 23:44 | 3.1452 | 2.8911 | 0.25405 | 3.3743e-05 | 0
[13 empty] | 23:45 | 0.96585 | 0.91146 | 0 |  | 23:45 | 0 | 0 | 5507.423 | 23:45 | 3.1459 | 2.8917 | 0.25411 | 3.3751e-05 | 0
[13 empty] | 23:45 | 0.95385 | 0.91146 | 0 |  | 23:45 | 0 | 0 | 5507.423 | 23:45 | 3.1465 | 2.8923 | 0.25414 | 3.3757e-05 | 0
[13 empty] | 23:45 | 0.94209 | 0.91146 | 0 |  | 23:45 | 0 | 0 | 5507.423 | 23:45 | 3.1471 | 2.8929 | 0.2542 | 3.3762e-05 | 0
[13 empty] | 23:46 | 0.93058 | 0.91146 | 0 |  | 23:46 | 0 | 0 | 5507.423 | 23:46 | 3.1475 | 2.8932 | 0.25424 | 3.3768e-05 | 0
[13 empty] | 23:46 | 0.9193 | 0.91146 | 0 |  | 23:46 | 0 | 0 | 5507.423 | 23:46 | 3.1481 | 2.8938 | 0.25428 | 3.3774e-05 | 0
[13 empty] | 23:46 | 0.90825 | 0.91146 | 0 |  | 23:46 | 0 | 0 | 5507.423 | 23:46 | 3.1488 | 2.8944 | 0.25434 | 3.378e-05 | 0
[13 empty] | 23:46 | 0.89743 | 0.91146 | 0 |  | 23:46 | 0 | 0 | 5507.423 | 23:46 | 3.1492 | 2.8948 | 0.25437 | 3.3785e-05 | 0
[13 empty] | 23:46 | 0.88683 | 0.91146 | 0 |  | 23:46 | 0 | 0 | 5507.423 | 23:46 | 3.1498 | 2.8953 | 0.25441 | 3.3791e-05 | 0
[13 empty] | 23:47 | 0.87645 | 0.91146 | 0 |  | 23:47 | 0 | 0 | 5507.423 | 23:47 | 3.1504 | 2.8959 | 0.25445 | 3.3797e-05 | 0
[13 empty] | 23:47 | 0.86628 | 0.91146 | 0 |  | 23:47 | 0 | 0 | 5507.423 | 23:47 | 3.1508 | 2.8963 | 0.25451 | 3.3803e-05 | 0
[13 empty] | 23:47 | 0.85633 | 0.91146 | 0 |  | 23:47 | 0 | 0 | 5507.423 | 23:47 | 3.1515 | 2.8969 | 0.25455 | 3.3808e-05 | 0
[13 empty] | 23:48 | 0.84657 | 0.91146 | 0 |  | 23:48 | 0 | 0 | 5507.423 | 23:48 | 3.1519 | 2.8973 | 0.25458 | 3.3814e-05 | 0
[13 empty] | 23:48 | 0.83702 | 0.91146 | 0 |  | 23:48 | 0 | 0 | 5507.423 | 23:48 | 3.1523 | 2.8976 | 0.25462 | 3.382e-05 | 0
[13 empty] | 23:48 | 0.82766 | 0.91146 | 0 |  | 23:48 | 0 | 0 | 5507.423 | 23:48 | 3.1529 | 2.8982 | 0.25466 | 3.3826e-05 | 0
[13 empty] | 23:48 | 0.8185 | 0.91146 | 0 |  | 23:48 | 0 | 0 | 5507.423 | 23:48 | 3.1533 | 2.8986 | 0.2547 | 3.3831e-05 | 0
[13 empty] | 23:48 | 0.80952 | 0.91146 | 0 |  | 23:48 | 0 | 0 | 5507.423 | 23:48 | 3.1539 | 2.8992 | 0.25474 | 3.3835e-05 | 0
[13 empty] | 23:49 | 0.80073 | 0.91146 | 0 |  | 23:49 | 0 | 0 | 5507.423 | 23:49 | 3.1544 | 2.8995 | 0.25478 | 3.3841e-05 | 0
[13 empty] | 23:49 | 0.79211 | 0.91146 | 0 |  | 23:49 | 0 | 0 | 5507.423 | 23:49 | 3.1548 | 2.8999 | 0.25481 | 3.3847e-05 | 0
[13 empty] | 23:49 | 0.78368 | 0.91146 | 0 |  | 23:49 | 0 | 0 | 5507.423 | 23:49 | 3.1554 | 2.9005 | 0.25487 | 3.385e-05 | 0
[13 empty] | 23:50 | 0.77542 | 0.91146 | 0 |  | 23:50 | 0 | 0 | 5507.423 | 23:50 | 3.1558 | 2.9009 | 0.25489 | 3.3856e-05 | 0
[13 empty] | 23:50 | 0.76733 | 0.91146 | 0 |  | 23:50 | 0 | 0 | 5507.423 | 23:50 | 3.1562 | 2.9013 | 0.25493 | 3.3862e-05 | 0
[13 empty] | 23:50 | 0.7594 | 0.91146 | 0 |  | 23:50 | 0 | 0 | 5507.423 | 23:50 | 3.1566 | 2.9016 | 0.25497 | 3.3866e-05 | 0
[13 empty] | 23:50 | 0.75164 | 0.91146 | 0 |  | 23:50 | 0 | 0 | 5507.423 | 23:50 | 3.1571 | 2.902 | 0.255 | 3.3871e-05 | 0
[13 empty] | 23:50 | 0.74403 | 0.91146 | 0 |  | 23:50 | 0 | 0 | 5507.423 | 23:50 | 3.1577 | 2.9026 | 0.25504 | 3.3875e-05 | 0
[13 empty] | 23:51 | 0.73658 | 0.91146 | 0 |  | 23:51 | 0 | 0 | 5507.423 | 23:51 | 3.1581 | 2.903 | 0.25508 | 3.3881e-05 | 0
[13 empty] | 23:51 | 0.72929 | 0.91146 | 0 |  | 23:51 | 0 | 0 | 5507.423 | 23:51 | 3.1585 | 2.9034 | 0.25512 | 3.3885e-05 | 0
[13 empty] | 23:51 | 1.1629 | 0.91146 | 0 |  | 23:51 | 0 | 0 | 5507.423 | 23:51 | 3.1592 | 2.9039 | 0.25518 | 3.3892e-05 | 0
[13 empty] | 23:52 | 1.1468 | 0.91146 | 0 |  | 23:52 | 0 | 0 | 5507.423 | 23:52 | 3.16 | 2.9047 | 0.25523 | 3.39e-05 | 0
[13 empty] | 23:52 | 1.1311 | 0.91146 | 0 |  | 23:52 | 0 | 0 | 5507.423 | 23:52 | 3.1606 | 2.9053 | 0.25529 | 3.3908e-05 | 0
[13 empty] | 23:52 | 1.1157 | 0.91146 | 0 |  | 23:52 | 0 | 0 | 5507.423 | 23:52 | 3.1612 | 2.9059 | 0.25535 | 3.3915e-05 | 0
[13 empty] | 23:52 | 1.1006 | 0.91146 | 0 |  | 23:52 | 0 | 0 | 5507.423 | 23:52 | 3.1618 | 2.9064 | 0.25539 | 3.3923e-05 | 0
[13 empty] | 23:52 | 1.0859 | 0.91146 | 0 |  | 23:52 | 0 | 0 | 5507.423 | 23:52 | 3.1627 | 2.9072 | 0.25544 | 3.3929e-05 | 0
[13 empty] | 23:53 | 1.0714 | 0.91146 | 0 |  | 23:53 | 0 | 0 | 5507.423 | 23:53 | 3.1633 | 2.9078 | 0.2555 | 3.3936e-05 | 0
[13 empty] | 23:53 | 1.0572 | 0.91146 | 0 |  | 23:53 | 0 | 0 | 5507.423 | 23:53 | 3.1639 | 2.9083 | 0.25556 | 3.3944e-05 | 0
[13 empty] | 23:53 | 1.0434 | 0.91146 | 0 |  | 23:53 | 0 | 0 | 5507.423 | 23:53 | 3.1645 | 2.9089 | 0.2556 | 3.395e-05 | 0
[13 empty] | 23:54 | 1.0298 | 0.91146 | 0 |  | 23:54 | 0 | 0 | 5507.423 | 23:54 | 3.1652 | 2.9095 | 0.25565 | 3.3957e-05 | 0
[13 empty] | 23:54 | 1.0164 | 0.91146 | 0 |  | 23:54 | 0 | 0 | 5507.423 | 23:54 | 3.1658 | 2.9101 | 0.25571 | 3.3963e-05 | 0
[13 empty] | 23:54 | 1.0034 | 0.91146 | 0 |  | 23:54 | 0 | 0 | 5507.423 | 23:54 | 3.1664 | 2.9106 | 0.25575 | 3.3969e-05 | 0
[13 empty] | 23:54 | 0.99062 | 0.91146 | 0 |  | 23:54 | 0 | 0 | 5507.423 | 23:54 | 3.167 | 2.9112 | 0.25581 | 3.3976e-05 | 0
[13 empty] | 23:54 | 0.97811 | 0.91146 | 0 |  | 23:54 | 0 | 0 | 5507.423 | 23:54 | 3.1675 | 2.9116 | 0.25584 | 3.3982e-05 | 0
[13 empty] | 23:55 | 0.96585 | 0.91146 | 0 |  | 23:55 | 0 | 0 | 5507.423 | 23:55 | 3.1681 | 2.9122 | 0.2559 | 3.3988e-05 | 0
[13 empty] | 23:55 | 0.95385 | 0.91146 | 0 |  | 23:55 | 0 | 0 | 5507.423 | 23:55 | 3.1687 | 2.9127 | 0.25594 | 3.3995e-05 | 0
[13 empty] | 23:55 | 0.94209 | 0.91146 | 0 |  | 23:55 | 0 | 0 | 5507.423 | 23:55 | 3.1693 | 2.9133 | 0.256 | 3.4001e-05 | 0
[13 empty] | 23:56 | 0.93058 | 0.91146 | 0 |  | 23:56 | 0 | 0 | 5507.423 | 23:56 | 3.1698 | 2.9137 | 0.25604 | 3.4007e-05 | 0
[13 empty] | 23:56 | 0.9193 | 0.91146 | 0 |  | 23:56 | 0 | 0 | 5507.423 | 23:56 | 3.1704 | 2.9143 | 0.25607 | 3.4013e-05 | 0
[13 empty] | 23:56 | 0.90825 | 0.91146 | 0 |  | 23:56 | 0 | 0 | 5507.423 | 23:56 | 3.171 | 2.9148 | 0.25613 | 3.4018e-05 | 0
[13 empty] | 23:56 | 0.89743 | 0.91146 | 0 |  | 23:56 | 0 | 0 | 5507.423 | 23:56 | 3.1714 | 2.9152 | 0.25617 | 3.4024e-05 | 0
[13 empty] | 23:56 | 0.88683 | 0.91146 | 0 |  | 23:56 | 0 | 0 | 5507.423 | 23:56 | 3.172 | 2.9158 | 0.25621 | 3.403e-05 | 0
[13 empty] | 23:57 | 0.87645 | 0.91146 | 0 |  | 23:57 | 0 | 0 | 5507.423 | 23:57 | 3.1726 | 2.9164 | 0.25625 | 3.4036e-05 | 0
[13 empty] | 23:57 | 0.86628 | 0.91146 | 0 |  | 23:57 | 0 | 0 | 5507.423 | 23:57 | 3.1731 | 2.9167 | 0.2563 | 3.4041e-05 | 0
[13 empty] | 23:57 | 0.85633 | 0.91146 | 0 |  | 23:57 | 0 | 0 | 5507.423 | 23:57 | 3.1737 | 2.9173 | 0.25634 | 3.4047e-05 | 0
[13 empty] | 23:58 | 0.84657 | 0.91146 | 0 |  | 23:58 | 0 | 0 | 5507.423 | 23:58 | 3.1741 | 2.9177 | 0.25638 | 3.4053e-05 | 0
[13 empty] | 23:58 | 0.83702 | 0.91146 | 0 |  | 23:58 | 0 | 0 | 5507.423 | 23:58 | 3.1745 | 2.9181 | 0.25642 | 3.4059e-05 | 0
[13 empty] | 23:58 | 0.82766 | 0.91146 | 0 |  | 23:58 | 0 | 0 | 5507.423 | 23:58 | 3.1751 | 2.9186 | 0.25646 | 3.4064e-05 | 0
[13 empty] | 23:58 | 0.8185 | 0.91146 | 0 |  | 23:58 | 0 | 0 | 5507.423 | 23:58 | 3.1756 | 2.919 | 0.25649 | 3.4068e-05 | 0
[13 empty] | 23:58 | 0.80952 | 0.91146 | 0 |  | 23:58 | 0 | 0 | 5507.423 | 23:58 | 3.1762 | 2.9196 | 0.25653 | 3.4074e-05 | 0
[13 empty] | 23:59 | 0.80073 | 0.91146 | 0 |  | 23:59 | 0 | 0 | 5507.423 | 23:59 | 3.1766 | 2.92 | 0.25657 | 3.408e-05 | 0
[13 empty] | 23:59 | 0.79211 | 0.91146 | 0 |  | 23:59 | 0 | 0 | 5507.423 | 23:59 | 3.177 | 2.9204 | 0.25663 | 3.4085e-05 | 0
[13 empty] | 23:59 | 0.78368 | 0.91146 | 0 |  | 23:59 | 0 | 0 | 5507.423 | 23:59 | 3.1776 | 2.9209 | 0.25667 | 3.4089e-05 | 0
[13 empty] | 24:00 | 0.77542 | 0.91146 | 0 |  | 24:00 | 0 | 0 | 5507.423 | 24:00 | 3.178 | 2.9213 | 0.25669 | 3.4095e-05 | 0
[13 empty] | 24:00 | 0.76733 | 0.91146 | 0 |  | 24:00 | 0 | 0 | 5507.423 | 24:00 | 3.1785 | 2.9217 | 0.25672 | 3.4101e-05 | 0
[13 empty] | 24:00 | 0.7594 | 0.91146 | 0 |  | 24:00 | 0 | 0 | 5507.423 | 24:00 | 3.1789 | 2.9221 | 0.25676 | 3.4104e-05 | 0
Note on S3: Paste fatima.csv file here.

## Ventilation
FaTIMA | Includes Qinf and Qdx where nano-tool did not.
m3/h
Case | Inputs | [5 empty] | Outputs |  |  |  |  | ACR |  | Check | w/ Dedicated Exhaust |  |  | ACR
| SQs | SQret | fo | Qo_min | Vol | Qinf | Q'o | Qo | Qrec | Qexh | Qbal | 1/h | Zone Air Balance | %OA | Qdx | Qbal_dx | Zone Air Balance | 1/h
[19 empty] | f *Qs | Qs-Q'oa | Qs*(1-f)
Diagram | 360 | 360 | 0 | 0 | 100 | 50 | 0 | 0 | 360 | 0 | 50 | 0.5 | Pressurized --> | 0 | 0 | 50 | Pressurized --> | 0.5 | 0 | 360 | 360
0.5
|  |  |  | Qo_min = 0 ==> |  |  | 0 |  | 360 |  |  | 0.5
Q'o=MAX(pctOA*Qsup,MIN(Qsup,QoaMin))
Qrec=MIN(Qret,Qsup-QoaPrim)
Qrec=MIN(Qret,Qsup*(1-pctOA))
Qexh = 0
Qrec = 360
Qo = 0
[5 empty] | Qs = 360 |  | Qret = 360
|  |  |  | Qdx = 0 |  |  |  | Pressurized -->
Qbal = 50
|  |  |  | Qinf = 50 | [9 empty] | `
Pressurized -->
Qbal_dx = 50
ZONE
Note on C6: Total supply airflow rate to building zones
Note on D6: Total return airflow rate from building zones
Note on E6: Outdoor Air Schedule value Between 0.0 and 1.0
Note on F6: Minimum OA Flow
Note on F8: FaTIMA does not utilize this so always set to zero.