## pHeaderMod
time
cl_t_sp_f | Temperature setpoint of the water in the condensing loop
cl_t_kp | Proportional gain for the PI controller for the temperature of the condensing loop
cl_t_ki | Integral gain for the PI controller for the temperature of the condensing loop
cl_t_kd | Derivative gain for the PI controller for the temperature of the condensing loop
cl_t_ubias | Bias term for the PI controller for the temperature of the condensing loop
cl_t_sp_high | Upper limit on the temperature setpoint in the condensing loop
cl_t_sp_low | Lower limit on the temperature setpoint in the condensing loop
cl_t_pv_f | Actual temperature being controlled in the condensing loop
cl_t_cv_v | Control signal for Valve3, the control valve, in the condensing loop
cl_t_error_f | Difference between the actual and setpoint temperatures in the condensing loop
cl_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures in the condensing loop
cl_t_prop_term | Proportional term in the PI controller for the condensing loop
cl_t_int_term | Integral term in the PI controller for the condensing loop
sl_t_sp_f | Temperature setpoint of the PG in the secondary loop
sl_t_kp | Proportional gain for the PI controller for the temperature of the secondary loop
sl_t_ki | Integral gain for the PI controller for the temperature of the secondary loop
sl_t_kd | Derivative gain for the PI controller for the temperature of the secondary loop
sl_t_ubias | Bias term for the PI controller for the temperature of the secondary loop
sl_t_sp_high | Upper limit on the temperature setpoint in the secondary loop
sl_t_sp_low | Lower limit on the temperature setpoint in the secondary loop
sl_t_pv_f | Actual temperature being controlled in the secondary loop
sl_t_cv_v | Control signal for Valve9, the control valve, in the secondary loop
sl_t_error_f | Difference between the actual and setpoint temperatures in the secondary loop
sl_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures in the secondary loop
sl_DB | No longer used
sl_vfd_sp_v | Pump speed setpoint for the secondary loop pump
sl_vfd_kp | Proportional gain for the PI controller for the pump speed in the secondary loop
sl_vfd_ki | Integral gain for the PI controller for the pump speed in the secondary loop
sl_vfd_kd | Derivative gain for the PI controller for the pump speed in the secondary loop
sl_vfd_ubias | Bias for the PI controller for the pump speed in the secondary loop
sl_vfd_sp_high | Upper limit on the pump speed in the secondary loop
sl_vfd_sp_low | Lower limit on the pump speed in the secondary loop
sl_vfd_pv_v | Actual pump speed being controlled in the secondary loop
sl_vfd_cv_hz | Control signal for Pump3, the secondary loop pump
sl_vfd_error_v | Difference between the actual and setpoint pump speeds in the secondary loop
sl_vfd_cum_error_v | Integral error term - sum of the difference between the actual and setpoint pump speeds in the secondary loop
sl_n_pr | Number of timesteps between setpoint changes for pressure reset in the secondary loop
sl_thresh_low_pr | Threshold on the cooling coil valves that indicates less cooling is needed (the positions of both valves are below this threshold)
sl_thresh_high_pr | Threshold on the cooling coil valves that indicates more cooling is needed (the position of at least one valve exceeds this threshold)
sl_delta_pr | Magnitude of the change of the pressure setpoint in the secondary loop
ts_end_charging | Flag to indicate that charging of the thermal storage tank is complete
ts_t_sp_f | Temperature setpoint of the PG leaving the thermal storage tank
ts_t_kp | Proportional gain for the PI controller for the temperature leaving the thermal storage tank
ts_t_ki | Integral gain for the PI controller for the temperature leaving the thermal storage tank
ts_t_kd | Derivative gain for the PI controller for the temperature leaving the thermal storage tank
ts_t_ubias | Bias term for the PI controller for the temperature leaving the thermal storage tank
ts_t_sp_high | Upper limit on the temperature setpoint of the PG leaving the thermal storage tank
ts_t_sp_low | Lower limit on the temperature setpoint of the PG leaving the thermal storage tank
ts_t_pv_f | Actual temperature being controlled after the thermal storage tank
ts_t_cv_v | Control signal for Valve8, the control valve, for the PG leaving the thermal storage tank
ts_t_error_f | Difference between the actual and setpoint temperatures leaving the thermal storage tank
ts_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures leaving the thermal storage tank
hx1_t_sp_f | Temperature setpoint of the PG leaving HX1
hx1_t_kp | Proportional gain for the PI controller for the temperature of the PG leaving HX1
hx1_t_ki | Integral gain for the PI controller for the temperature of the PG leaving HX1
hx1_t_kd | Derivative gain for the PI controller for the temperature of the PG leaving HX1
hx1_t_ubias | Bias term for the PI controller for the temperature of the PG leaving HX1
hx1_t_sp_high | Upper limit on the temperature setpoint of the PG leaving HX1
hx1_t_sp_low | Lower limit on the temperature setpoint of the PG leaving HX1
hx1_t_pv_f | Actual temperature of the PG being controlled in HX1
hx1_t_dt_f | No longer used
hx1_t_error_f | Difference between the actual and setpoint temperatures of the PG leaving HX1
hx1_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures of the PG leaving HX1
hx1_t_cv_v | Control signal for Valve10, the control valve, in the PG side of HX1
hx1_load_sp_kw | Load setpoint for HX1
hx1_load_pv_inst_kw | Actual load generated by HX1
hx1_load_kp | Proportional gain for the PI controller for the load generated by HX1
hx1_load_ki | Integral gain for the PI controller for the load generated by HX1
hx1_load_kd | Derivative gain for the PI controller for the load generated by HX1
hx1_load_ubias | Bias term for the PI controller for the load generated by HX1
hx1_load_sp_high | Upper limit on the load setpoint in HX1
hx1_load_sp_low | Lower limit on the load setpoint in HX1
hx1_load_pv_avg_kw | Averaged actual load generated by HX1
hx1_load_cv_v | Control signal for Valve11, the control valve, in HX1
hx1_load_dq_kw | No longer used
hx1_load_error_kw | Difference between the actual and setpoint loads in HX1
hx1_load_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint loads in HX1
ch1_t_sp_f | Temperature setpoint for Chiller1
ch2_t_sp_f | Temperature setpoint for Chiller2
oau_h_t_sp_f | Temperature setpoint of the air leaving the heating coil in the OAU
oau_h_t_kp | Proportional gain for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_ki | Integral gain for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_kd | Derivative gain for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_ubias | Bias term for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_sp_high | Upper limit on the temperature setpoint of the air leaving the heating coil in the OAU
oau_h_t_sp_low | Lower limit on the temperature setpoint of the air leaving the heating coil in the OAU
oau_h_t_pv_f | Actual temperature of the air leaving the heating coil in the OAU
oau_h_t_cv_v | Control signal for the OAU heater
oau_h_t_error_f | Difference between the actual and setpoint temperatures of the air leaving the heating coil in the OAU
oau_h_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures of the air leaving the heating coil in the OAU
oau_h_prop_term | Proportional term in the PI controller for the heating coil in the OAU
oau_h_int_term | Integral term in the PI controller for the heating coil in the OAU
oau_h_threshold | No longer used
oau_h_delay | No longer used
oau_h_dtheat | No longer used
oau_h_outdoor_rtd_mean | No longer used
oau_c_t_kd | Derivative gain for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_kp | Proportional gain for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_ki | Integral gain for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_ubias | Bias term for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_sp_high | Upper limit on the humidity ratio leaving the OAU
oau_c_t_sp_low | Lower limit on the humidity ratio leaving the OAU
oau_c_t_sp_f | Setpoint humidity ratio of the air leaving the OAU
oau_c_t_pv_f | Actual humidity ratio of the air leaving the OAU
oau_c_t_cum_error_f | Integral error term - difference between the actual and setpoint humidity ratios of the air leaving the OAU
oau_c_prop_term | Proportional term in the PI controller for the heating coil in the OAU
oau_c_int_term | Integral term in the PI controller for the heating coil in the OAU
oau_c_delay | No longer used
oau_c_t_cv_v | Control signal for Compressor1 in the cooling coil in the OAU
oau_c_t_error_f | Difference between the actual and setpoint humidity ratios of the air leaving the OAU
oau_c_dt | no longer used
oau_c_delay2 | no longer used
oau_w_rh_sp_per | Setpoint relative humidity of the air leaving the OAU
oau_w_rh_kp | Proportional gain for the humidifier PI controller in the OAU
oau_w_rh_ki | Integral gain for the humidifier PI controller in the OAU
oau_w_rh_kd | Derivative gain for the humidifier PI controller in the OAU
oau_w_rh_ubias | Bias term for the humidifier PI controller in the OAU
oau_w_rh_sp_high | Upper limit on the relative humidity leaving the OAU
oau_w_rh_sp_low | Lower limit on the relative humidity leaving the OAU
oau_w_rh_pv_per | Actual relative humidity leaving the OAU
oau_w_rh_cv_v | Control signal for Valve2, the control valve for the humidifier
oau_w_rh_error_per | Difference between the actual and setpoint relative humidity of the air leaving the OAU
oau_w_rh_cum_error_per | Integral error term - sum of the difference between the actual and setpoint relative humidity of the air leaving the OAU
oau_w_prop_term | Proportional term in the PI controller for the humidifier in the OAU
oau_w_int_term | Integral term in the PI controller for the humidifier in the OAU
oau_t_out_sp_f | Setpoint temperature of the air leaving the OAU
oau_rh_out_sp_per | Setpoint relative humidity of the air leaving the OAU
oau_read_from_file | Flag to indicate that the OAU setpoints should be read from file
bc_n_sl_on | Number of timesteps that the secondary loop pump has to be on for there to be a building load
bc_n_q_mean | Number of timesteps to include in the calculation of the average load
bc_n_chiller_fault | Number of chiller fault flags before a chiller is considered to be in a fault status
bc_n_pump3_max | No longer used
bc_n_stage_up | Number of timesteps in the current stage before a chiller can be staged up
bc_n_stage_down | Number of timesteps in the current stage before a chiller can be staged down
bc_q1_min | Minimum load that allows Chiller1 to be enabled
bc_q1_sd | Load at which Chiller1 is staged down (turned off)
bc_q1_su | No longer used
bc_q2_min | Minimum load that allows Chiller2 to be enabled
bc_q2_sd | Load at which Chiller2 is staged down (turned off)
bc_q2_su | No longer used
bc_q3_min | No longer used
bc_q3_sd | No longer used
bc_q3_su | No longer used
bc_v10_sp | No longer used
bc_dt_sl | Value by which to offset the chiller setpoint temperature for the secondary loop
bc_max_plant_load_kw | No longer used
bc_pump3_max_vfd | No longer used
bc_n_trans | Number of timesteps for transition between stages
bc_n_viol | Number of timesteps that a violation has to occur before the stage can change
stage_up_down_count | Number of timesteps when a stage up or down is requested
stage_stage | The current stage that the chillers are in
stage_allow_stage_up_time | Flag to indicate that a chiller can stage up
stage_allow_stage_down_time | Flag to indicate that a chiller can stage down
stage_allow_stage_up_pump3 | No longer used
stage_allow_stage_down_temp | No longer used
zs1_qs_sp_kw | Sensible load setpoint for ZS1
zs1_qs_pv_kw | Actual sensible load in ZS1
zs1_qs_ca_a | Control signal for the heating coil in ZS1
zs1_qs_error_kw | Difference between the actual and setpoint sensible loads in ZS1
zs1_qs_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS1
zs1_ql_sp_kw | Latent load setpoint for ZS1
zs1_ql_pv_kw | Actual latent load in ZS1
zs1_ql_cv_v | Control signal for Valve14, the control valve for the humidifier in ZS1
zs1_ql_error_kw | Difference between the actual and setpoint latent loads in ZS1
zs1_ql_cum_error_kw | Integral error - sum of the difference between the actual and setpoint latent loads in ZS1
zs1_qs_kp | Proportional gain for the PI controller for the sensible load in ZS1
zs1_qs_ki | Integral gain for the PI controller for the sensible load in ZS1
zs1_qs_kd | Derivative gain for the PI controller for the sensible load in ZS1
zs1_qs_ubias | Bias term for the PI controller for the sensible load in ZS1
zs1_qs_sp_hi | Upper limit on the sensible load setpoint in ZS1
zs1_qs_sp_low | Lower limit on the sensible load setpoint in ZS1
zs1_ql_kp | Proportional gain for the PI controller for the latent load in ZS1
zs1_ql_ki | Integral gain for the PI controller for the latent load in ZS1
zs1_ql_kd | Derivative gain for the PI controller for the latent load in ZS1
zs1_ql_ubias | Bias term for the PI controller for the latent load in ZS1
zs1_ql_sp_hi | Upper limit on the latent load setpoint in ZS1
zs1_ql_sp_low | Lower limit on the latent load setpoint in ZS1
zs1_t_sp_f | Setpoint temperature for the air leaving ZS1
zs1_rh_sp_per | Relative humidity setpoint for the air leaving ZS1
zs2_qs_sp_kw | Sensible load setpoint for ZS2
zs2_qs_pv_kw | Actual sensible load in ZS2
zs2_qs_ca_a | Control signal for the heating coil in ZS2
zs2_qs_error_kw | Difference between the actual and setpoint sensible loads in ZS2
zs2_qs_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS2
zs2_ql_sp_kw | Latent load setpoint for ZS2
zs2_ql_pv_kw | Actual latent load in ZS2
zs2_ql_cv_v | Control signal for Valve15, the control valve for the humidifier in ZS2
zs2_ql_error_kw | Difference between the actual and setpoint latent loads in ZS2
zs2_ql_cum_error_kw | Integral error - sum of the difference between the actual and setpoint latent loads in ZS2
zs2_qs_kp | Proportional gain for the PI controller for the sensible load in ZS2
zs2_qs_ki | Integral gain for the PI controller for the sensible load in ZS2
zs2_qs_kd | Derivative gain for the PI controller for the sensible load in ZS2
zs2_qs_ubias | Bias term for the PI controller for the sensible load in ZS2
zs2_qs_sp_hi | Upper limit on the sensible load setpoint in ZS2
zs2_qs_sp_low | Lower limit on the sensible load setpoint in ZS2
zs2_ql_kp | Proportional gain for the PI controller for the latent load in ZS2
zs2_ql_ki | Integral gain for the PI controller for the latent load in ZS2
zs2_ql_kd | Derivative gain for the PI controller for the latent load in ZS2
zs2_ql_ubias | Bias term for the PI controller for the latent load in ZS2
zs2_ql_sp_hi | Upper limit on the latent load setpoint in ZS2
zs2_ql_sp_low | Lower limit on the latent load setpoint in ZS2
zs2_rh_sp_per | Setpoint temperature for the air leaving ZS2
zs2_t_sp_f | Relative humidity setpoint for the air leaving ZS2
zs3_qs_sp_kw | Sensible load setpoint for ZS3
zs3_qs_pv_kw | Actual sensible load in ZS3
zs3_qs_ca_a | Control signal for the heating coil in ZS3
zs3_qs_error_kw | Difference between the actual and setpoint sensible loads in ZS3
zs3_qs_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS3
zs3_ql_sp_kw | Latent load setpoint for ZS3
zs3_ql_pv_kw | Actual latent load in ZS3
zs3_ql_cv_v | Control signal for Valve16, the control valve for the humidifier in ZS3
zs3_ql_error_kw | Difference between the actual and setpoint latent loads in ZS3
zs3_ql_cum_error_kw | Integral error - sum of the difference between the actual and setpoint latent loads in ZS3
zs3_qs_kp | Proportional gain for the PI controller for the sensible load in ZS3
zs3_qs_ki | Integral gain for the PI controller for the sensible load in ZS3
zs3_qs_kd | Derivative gain for the PI controller for the sensible load in ZS3
zs3_qs_ubias | Bias term for the PI controller for the sensible load in ZS3
zs3_qs_sp_hi | Upper limit on the sensible load setpoint in ZS3
zs3_qs_sp_low | Lower limit on the sensible load setpoint in ZS3
zs3_ql_kp | Proportional gain for the PI controller for the latent load in ZS3
zs3_ql_ki | Integral gain for the PI controller for the latent load in ZS3
zs3_ql_kd | Derivative gain for the PI controller for the latent load in ZS3
zs3_ql_ubias | Bias term for the PI controller for the latent load in ZS3
zs3_ql_sp_hi | Upper limit on the latent load setpoint in ZS3
zs3_ql_sp_low | Lower limit on the latent load setpoint in ZS3
zs3_rh_sp_per | Setpoint temperature for the air leaving ZS3
zs3_t_sp_f | Relative humidity setpoint for the air leaving ZS3
zs4_qs_sp_kw | Sensible load setpoint for ZS4
zs4_qs_pv_kw | Actual sensible load in ZS4
zs4_qs_ca_a | Control signal for the heating coil in ZS4
zs4_qs_error_kw | Difference between the actual and setpoint sensible loads in ZS4
zs4_qs_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS4
zs4_ql_sp_kw | Latent load setpoint for ZS4
zs4_ql_pv_kw | Actual latent load in ZS4
zs4_ql_cv_v | Control signal for Valve17, the control valve for the humidifier in ZS4
zs4_ql_error_kw | Difference between the actual and setpoint latent loads in ZS4
zs4_ql_cum_error_kw | Integral error - sum of the difference between the actual and setpoint latent loads in ZS4
zs4_qs_kp | Proportional gain for the PI controller for the sensible load in ZS4
zs4_qs_ki | Integral gain for the PI controller for the sensible load in ZS4
zs4_qs_kd | Derivative gain for the PI controller for the sensible load in ZS4
zs4_qs_ubias | Bias term for the PI controller for the sensible load in ZS4
zs4_qs_sp_hi | Upper limit on the sensible load setpoint in ZS4
zs4_qs_sp_low | Lower limit on the sensible load setpoint in ZS4
zs4_ql_kp | Proportional gain for the PI controller for the latent load in ZS4
zs4_ql_ki | Integral gain for the PI controller for the latent load in ZS4
zs4_ql_kd | Derivative gain for the PI controller for the latent load in ZS4
zs4_ql_ubias | Bias term for the PI controller for the latent load in ZS4
zs4_ql_sp_hi | Upper limit on the latent load setpoint in ZS4
zs4_ql_sp_low | Lower limit on the latent load setpoint in ZS4
zs4_rh_sp_per | Setpoint temperature for the air leaving ZS4
zs4_t_sp_f | Relative humidity setpoint for the air leaving ZS4
ahu1_h_sp_f | Setpoint temperature for the air leaving the heating coil in AHU1
ahu1_h_kp | Proportional gain for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_ki | Integral gain for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_kd | Derivative gain for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_ubias | Bias term for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_sp_high | Upper limit on the temperature setpoint for the heating coil in AHU1
ahu1_h_sp_low | Lower limit on the temperature setpoint for the heating coil in AHU1
ahu1_h_pv_f | Actual temperature of the air leaving the heating coil in AHU1
ahu1_h_cv_v | Control signal for the heating coil in AHU1
ahu1_h_error_f | Difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU1
ahu1_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU1
ahu1_h_prop_term | Proportional term for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_int_term | Integral term for the PI controller for the air leaving the heating coil in AHU1
ahu1_cc_sp_f | Setpoint temperature for the air leaving the cooling coil in AHU1
ahu1_cc_kp | Proportional gain for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_ki | Integral gain for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_kd | Derivative gain for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_ubias | Bias term for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_sp_high | Upper limit on the temperature setpoint for the cooling coil in AHU1
ahu1_cc_sp_low | Lower limit on the temperature setpoint for the cooling coil in AHU1
ahu1_cc_pv_f | Actual temperature of the air leaving the cooling coil in AHU1
ahu1_cc_cv_v | Control signal for the cooling coil in AHU1
ahu1_cc_error_f | Difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU1
ahu1_cc_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU1
ahu1_cc_prop_term | Proportional term for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_int_term | Integral term for the PI controller for the air leaving the cooling coil in AHU1
ahu1_fan_sp_inh2o | Pressure setpoint for the supply fan in AHU1
ahu1_fan_kp | Proportional gain for the PI controller for the supply fan in AHU1
ahu1_fan_ki | Integral gain for the PI controller for the supply fan in AHU1
ahu1_fan_kd | Derivative gain for the PI controller for the supply fan in AHU1
ahu1_fan_ubias | Bias term for the PI controller for the supply fan in AHU1
ahu1_fan_sp_high | Upper limit on the pressure setpoint for the supply fan in AHU1
ahu1_fan_sp_low | Lower limit on the pressure setpoint for the supply fan in AHU1
ahu1_fan_pv_inh2o | Actual static pressure downstream of AHU1
ahu1_fan_cv_hz | Control signal for the speed of the supply fan in AHU1
ahu1_fan_error_inh2o | Difference between the actual and setpoint pressures downstream of AHU1
ahu1_fan_cum_error_inh2o | Integral error - sum of the difference between the actual and setpoint pressures downstream of AHU1
ahu1_fan_prop_term | Proportional term for the PI controller for the speed of the supply fan in AHU1
ahu1_fan_int_term | Integral term for the PI controller for the speed of the supply fan in AHU1
ahu2_h_sp_f | Setpoint temperature for the air leaving the heating coil in AHU2
ahu2_h_kp | Proportional gain for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_ki | Integral gain for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_kd | Derivative gain for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_ubias | Bias term for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_sp_high | Upper limit on the temperature setpoint for the heating coil in AHU2
ahu2_h_sp_low | Lower limit on the temperature setpoint for the heating coil in AHU2
ahu2_h_pv_f | Actual temperature of the air leaving the heating coil in AHU2
ahu2_h_cv_v | Control signal for the heating coil in AHU2
ahu2_h_error_f | Difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU2
ahu2_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU2
ahu2_h_prop_term | Proportional term for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_int_term | Integral term for the PI controller for the air leaving the heating coil in AHU2
ahu2_cc_sp_f | Setpoint temperature for the air leaving the cooling coil in AHU2
ahu2_cc_kp | Proportional gain for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_ki | Integral gain for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_kd | Derivative gain for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_ubias | Bias term for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_sp_high | Upper limit on the temperature setpoint for the cooling coil in AHU2
ahu2_cc_sp_low | Lower limit on the temperature setpoint for the cooling coil in AHU2
ahu2_cc_pv_f | Actual temperature of the air leaving the cooling coil in AHU2
ahu2_cc_cv_v | Control signal for the cooling coil in AHU2
ahu2_cc_error_f | Difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU2
ahu2_cc_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU2
ahu2_cc_prop_term | Proportional term for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_int_term | Integral term for the PI controller for the air leaving the cooling coil in AHU2
ahu2_fan_sp_inh2o | Pressure setpoint for the supply fan in AHU2
ahu2_fan_kp | Proportional gain for the PI controller for the supply fan in AHU2
ahu2_fan_ki | Integral gain for the PI controller for the supply fan in AHU2
ahu2_fan_kd | Derivative gain for the PI controller for the supply fan in AHU2
ahu2_fan_ubias | Bias term for the PI controller for the supply fan in AHU2
ahu2_fan_sp_high | Upper limit on the pressure setpoint for the supply fan in AHU2
ahu2_fan_sp_low | Lower limit on the pressure setpoint for the supply fan in AHU2
ahu2_fan_pv_inh2o | Actual static pressure downstream of AHU2
ahu2_fan_cv_hz | Control signal for the speed of the supply fan in AHU2
ahu2_fan_error_inh2o | Difference between the actual and setpoint pressures downstream of AHU2
ahu2_fan_cum_error_inh2o | Integral error - sum of the difference between the actual and setpoint pressures downstream of AHU2
ahu2_fan_prop_term | Proportional term for the PI controller for the speed of the supply fan in AHU2
ahu2_fan_int_term | Integral term for the PI controller for the speed of the supply fan in AHU2
vav1_d_sp | Flow setpont for the PI controller for the damper in VAV1
vav1_d_kp | Proportional gain for the PI controller for the damper in VAV1
vav1_d_ki | Integral gain for the PI controller for the damper in VAV1
vav1_d_kd | Derivative gain for the PI controller for the damper in VAV1
vav1_d_ubias | Bias term for the PI controller for the damper in VAV1
vav1_d_sp_high | Upper limit on the flow setpoint for VAV1
vav1_d_sp_low | Lower limit on the flow setpoint for VAV1
vav1_d_pv | Actual airflow rate in VAV1
vav1_d_cv_output | Control signal for Damper15, the control damper, in VAV1
vav1_d_error | Difference between the actual and setpoint flows in VAV1
vav1_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV1
vav1_d_prop_term | Proportional term for the PI controller for the damper in VAV1
vav1_d_int_term | Integral term for the PI controller for the damper in VAV1
vav1_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV1
vav1_h_kp | Proportional gain for the PI controller for the heating coil in VAV1
vav1_h_ki | Integral gain for the PI controller for the heating coil in VAV1
vav1_h_kd | Derivative gain for the PI controller for the heating coil in VAV1
vav1_h_ubias | Bias term for the PI controller for the heating coil in VAV1
vav1_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV1
vav1_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV1
vav1_h_pv_f | Actual temperature of the air after the heating coil in VAV1
vav1_h_cv_v | Control signal for the heating coil in VAV1
vav1_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV1
vav1_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV1
vav1_h_prop_term | Proportional term for the PI controller for the heating coil in VAV1
vav1_h_int_term | Integral term for the PI controller for the heating coil in VAV1
vav2_d_sp | Flow setpont for the PI controller for the damper in VAV2
vav2_d_kp | Proportional gain for the PI controller for the damper in VAV2
vav2_d_ki | Integral gain for the PI controller for the damper in VAV2
vav2_d_kd | Derivative gain for the PI controller for the damper in VAV2
vav2_d_ubias | Bias term for the PI controller for the damper in VAV2
vav2_d_sp_high | Upper limit on the flow setpoint for VAV2
vav2_d_sp_low | Lower limit on the flow setpoint for VAV2
vav2_d_pv | Actual airflow rate in VAV2
vav2_d_cv_output | Control signal for Damper16, the control damper, in VAV2
vav2_d_error | Difference between the actual and setpoint flows in VAV2
vav2_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV2
vav2_d_prop_term | Proportional term for the PI controller for the damper in VAV2
vav2_d_int_term | Integral term for the PI controller for the damper in VAV2
vav2_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV2
vav2_h_kp | Proportional gain for the PI controller for the heating coil in VAV2
vav2_h_ki | Integral gain for the PI controller for the heating coil in VAV2
vav2_h_kd | Derivative gain for the PI controller for the heating coil in VAV2
vav2_h_ubias | Bias term for the PI controller for the heating coil in VAV2
vav2_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV2
vav2_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV2
vav2_h_pv_f | Actual temperature of the air after the heating coil in VAV2
vav2_h_cv_v | Control signal for the heating coil in VAV2
vav2_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV2
vav2_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV2
vav2_h_prop_term | Proportional term for the PI controller for the heating coil in VAV2
vav2_h_int_term | Integral term for the PI controller for the heating coil in VAV2
vav3_d_sp | Flow setpont for the PI controller for the damper in VAV3
vav3_d_kp | Proportional gain for the PI controller for the damper in VAV3
vav3_d_ki | Integral gain for the PI controller for the damper in VAV3
vav3_d_kd | Derivative gain for the PI controller for the damper in VAV3
vav3_d_ubias | Bias term for the PI controller for the damper in VAV3
vav3_d_sp_high | Upper limit on the flow setpoint for VAV3
vav3_d_sp_low | Lower limit on the flow setpoint for VAV3
vav3_d_pv | Actual airflow rate in VAV3
vav3_d_cv_output | Control signal for Damper17, the control damper, in VAV3
vav3_d_error | Difference between the actual and setpoint flows in VAV3
vav3_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV3
vav3_d_prop_term | Proportional term for the PI controller for the damper in VAV3
vav3_d_int_term | Integral term for the PI controller for the damper in VAV3
vav3_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV3
vav3_h_kp | Proportional gain for the PI controller for the heating coil in VAV3
vav3_h_ki | Integral gain for the PI controller for the heating coil in VAV3
vav3_h_kd | Derivative gain for the PI controller for the heating coil in VAV3
vav3_h_ubias | Bias term for the PI controller for the heating coil in VAV3
vav3_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV3
vav3_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV3
vav3_h_pv_f | Actual temperature of the air after the heating coil in VAV3
vav3_h_cv_v | Control signal for the heating coil in VAV3
vav3_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV3
vav3_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV3
vav3_h_prop_term | Proportional term for the PI controller for the heating coil in VAV3
vav3_h_int_term | Integral term for the PI controller for the heating coil in VAV3
vav4_d_sp | Flow setpont for the PI controller for the damper in VAV4
vav4_d_kp | Proportional gain for the PI controller for the damper in VAV4
vav4_d_ki | Integral gain for the PI controller for the damper in VAV4
vav4_d_kd | Derivative gain for the PI controller for the damper in VAV4
vav4_d_ubias | Bias term for the PI controller for the damper in VAV4
vav4_d_sp_high | Upper limit on the flow setpoint for VAV4
vav4_d_sp_low | Lower limit on the flow setpoint for VAV4
vav4_d_pv | Actual airflow rate in VAV4
vav4_d_cv_output | Control signal for Damper18, the control damper, in VAV4
vav4_d_error | Difference between the actual and setpoint flows in VAV4
vav4_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV4
vav4_d_prop_term | Proportional term for the PI controller for the damper in VAV4
vav4_d_int_term | Integral term for the PI controller for the damper in VAV4
vav4_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV4
vav4_h_kp | Proportional gain for the PI controller for the heating coil in VAV4
vav4_h_ki | Integral gain for the PI controller for the heating coil in VAV4
vav4_h_kd | Derivative gain for the PI controller for the heating coil in VAV4
vav4_h_ubias | Bias term for the PI controller for the heating coil in VAV4
vav4_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV4
vav4_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV4
vav4_h_pv_f | Actual temperature of the air after the heating coil in VAV4
vav4_h_cv_v | Control signal for the heating coil in VAV4
vav4_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV4
vav4_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV4
vav4_h_prop_term | Proportional term for the PI controller for the heating coil in VAV4
vav4_h_int_term | Integral term for the PI controller for the heating coil in VAV4
ahu1_sa_sp_per | Setpoint for the percent outdoor air for AHU1
ahu1_sa_kp | Proportional gain for the PI controller for the percent outdoor air for AHU1
ahu1_sa_ki | Integral gain for the PI controller for the percent outdoor air for AHU1
ahu1_sa_kd | Derivative gain for the PI controller for the percent outdoor air for AHU1
ahu1_sa_ubias | Bias term for the PI controller for the percent outdoor air for AHU1
ahu1_sa_sp_high | Upper limit on the percent outdoor air for AHU1
ahu1_sa_sp_low | Lower limit on the percent outdoor air for AHU1
ahu1_sa_pv_per | Actual percent outdoor air for AHU1
ahu1_sa_cv_v | Control signal for Damper6, the supply air damper, for AHU1
ahu1_sa_error_per | Difference between the actual and setpoint percent outdoor air for AHU1
ahu1_sa_cum_error_per | Integral error - sum of the difference between the actual and setpoint percent outdoor air for AHU1
ahu1_sa_prop_term | Proportional term for the PI controller for the percent outdoor air for AHU1
ahu1_sa_int_term | Integral term for the PI controller for the percent outdoor air for AHU1
ahu2_sa_sp_per | Setpoint for the percent outdoor air for AHU2
ahu2_sa_kp | Proportional gain for the PI controller for the percent outdoor air for AHU2
ahu2_sa_ki | Integral gain for the PI controller for the percent outdoor air for AHU2
ahu2_sa_kd | Derivative gain for the PI controller for the percent outdoor air for AHU2
ahu2_sa_ubias | Bias term for the PI controller for the percent outdoor air for AHU2
ahu2_sa_sp_high | Upper limit on the percent outdoor air for AHU2
ahu2_sa_sp_low | Lower limit on the percent outdoor air for AHU2
ahu2_sa_pv_per | Actual percent outdoor air for AHU2
ahu2_sa_cv_v | Control signal for Damper7, the supply air damper, for AHU2
ahu2_sa_error_per | Difference between the actual and setpoint percent outdoor air for AHU2
ahu2_sa_cum_error_per | Integral error - sum of the difference between the actual and setpoint percent outdoor air for AHU2
ahu2_sa_prop_term | Proportional term for the PI controller for the percent outdoor air for AHU2
ahu2_sa_int_term | Integral term for the PI controller for the percent outdoor air for AHU2
ahu1_n_pr | Number of timesteps between setpoint changes for pressure reset for the supply fan in AHU1
ahu1_thresh_high_pr | Threshold on the VAV dampers that indicates more cooling is needed (the positions of either damper is above this threshold)
ahu1_thresh_low_pr | Threshold on the VAV dampers that indicates less cooling is needed (the positions of both dampers are below this threshold)
ahu1_delta_pr | Magnitude of the change of the pressure setpoint for the supply fan in AHU1
ahu2_n_pr | Number of timesteps between setpoint changes for pressure reset for the supply fan in AHU2
ahu2_thresh_high_pr | Threshold on the VAV dampers that indicates more cooling is needed (the positions of either damper is above this threshold)
ahu2_thresh_low_pr | Threshold on the VAV dampers that indicates less cooling is needed (the positions of both dampers are below this threshold)
ahu2_delta_pr | Magnitude of the change of the pressure setpoint for the supply fan in AHU2
vav1_fr_sp | Temperature setpont for the air leaving ZS1
vav1_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV1
vav1_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV1
vav1_fr_pv | Actual temperature leaving ZS1
vav1_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV1
vav1_fr_error | Difference between the actual and setpoint temperatures for ZS1
vav1_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS1
vav1_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV1
vav2_fr_sp | Temperature setpont for the air leaving ZS2
vav2_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV2
vav2_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV2
vav2_fr_pv | Actual temperature leaving ZS2
vav2_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV2
vav2_fr_error | Difference between the actual and setpoint temperatures for ZS2
vav2_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS2
vav2_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV2
vav3_fr_sp | Temperature setpont for the air leaving ZS3
vav3_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV3
vav3_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV3
vav3_fr_pv | Actual temperature leaving ZS3
vav3_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV3
vav3_fr_error | Difference between the actual and setpoint temperatures for ZS3
vav3_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS3
vav3_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV3
vav4_fr_sp | Temperature setpont for the air leaving ZS4
vav4_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV4
vav4_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV4
vav4_fr_pv | Actual temperature leaving ZS4
vav4_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV4
vav4_fr_error | Difference between the actual and setpoint temperatures for ZS4
vav4_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS4
vav4_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV4
vav1_tr_sp | Temperature setpont for the air leaving ZS1
vav1_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV1
vav1_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV1
vav1_tr_pv | Actual temperature leaving ZS1
vav1_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV1
vav1_tr_error | Difference between the actual and setpoint temperatures for ZS1
vav1_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS1
vav1_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav2_tr_sp | Temperature setpont for the air leaving ZS2
vav2_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV2
vav2_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV2
vav2_tr_pv | Actual temperature leaving ZS2
vav2_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV2
vav2_tr_error | Difference between the actual and setpoint temperatures for ZS2
vav2_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS2
vav2_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav3_tr_sp | Temperature setpont for the air leaving ZS3
vav3_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV3
vav3_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV3
vav3_tr_pv | Actual temperature leaving ZS3
vav3_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV3
vav3_tr_error | Difference between the actual and setpoint temperatures for ZS3
vav3_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS3
vav3_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav4_tr_sp | Temperature setpont for the air leaving ZS4
vav4_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV4
vav4_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV4
vav4_tr_pv | Actual temperature leaving ZS4
vav4_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV4
vav4_tr_error | Difference between the actual and setpoint temperatures for ZS4
vav4_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS4
vav4_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
zs1_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs1_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs1_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS1
zs1_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs1_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs2_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs2_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs2_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS2
zs2_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs2_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs4_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs4_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs4_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS4
zs4_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs4_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs3_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV3
zs3_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV3
zs3_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS3
zs3_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV3
zs3_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV3