## MZ320air
[5 empty] | MZ320 plus Airflow (w/ AHS and Window A/C) Analytical Solution | [9 empty] | k wall | 1.2 | W/mK
Software: | Analytical Solution | [13 empty] | t wall | 0.15 | m
Version: | Neymark modified by Dols |  |  |  | Lwall1 | 6 | m | Acom | 21.6 | m2 | Cp | 1005.6 | J/kg-C | Common Walls
Date: | June 2005 / May 2014 |  |  |  | Lwall2 | 8 | m | AextAC | 150 | m2 | Tair | 20 |  |  | Conductivity | Thickness | Conductance | Resistance | Density | Specific Heat
[5 empty] | Hzone | 2.7 | m | AextB | 128.4 | m2 | RHOoa | 1.204 | kg/m3 | Element | (W/(m·K)) | (m) | (W/(m2·K)) | (m2·K/W) | (kg/m3) | (J/(kg·K))
[5 empty] | Vzone | 129.6 | m3 |  |  |  | ACH | 0.5 | 1/h | Int Combined Surf Coef |  |  | 8.29 | 0.12063
|  | MZ320af1 Steady State Results |  |  | RHOstdEplus | 1.204 |  | UAcom | 58.9754 | W/K | Qinf | 0.018 | m3/s | Common Wall Material | 1.2 | 0.15 | 8 | 0.125 | 1400 | 1000
|  |  |  | Cooling |  |  |  | UAextAC | 192.6961 | W/K | MdotMix | 0.021672 | kg/s | Int Combined Surf Coef |  |  | 8.29 | 0.12063
|  | Zone Air Temperatures |  | Load |  |  |  | UAextB | 164.9478 | W/K |  | 78.02 | kg/h | Total air-air |  |  | 2.7303 | 0.36625
| TA | TB | TC | qC |  |  |  | Rat | 3.7724 |  |  | 0.018 | m3/s
Case | (°C) | (°C) | (°C) | (W or Wh/h) | [6 empty] | MdotOA-C | 0.021672 | kg/s | IP using ASHRAE (2001) Conversion Factors
MZ320air | 30.3092 | 23.952 | 15 | 1600.3957 |  |  |  | To | 20 | °C |  |  |  |  | Conductivity | Thickness | Conductance | Resistance | Density | Specific Heat
[14 empty] | Element | (Btu/(h·ft°·F)) | (ft) | (Btu/(h·ft2·°F)) | (h·ft2·°F/Btu) | (lb/ft3) | (Btu/(lb·°F))
[14 empty] | Int Combined Surf Coef |  |  | 1.46 | 0.68492
[7 empty] | -74.4708 |  |  | -37.2068 | 0 | kg/s |  | Common Wall Material | 0.69324 | 0.49213 | 1.4089 | 0.70975 | 87.5 | 0.23901
[14 empty] | Int Combined Surf Coef |  |  | 1.46 | 0.68492
[5 empty] | qAO | -1986.5374 | W | qBO | -651.8734 | W | qCO | 963.4804 | W | Total air-air |  |  | 0.48086 | 2.0796
[6 empty] | -62.6474 | GJ |  | -20.5575 | GJ |  | 30.3843 | GJ
[5 empty] | qintA | 2500 | W | qintB | 1000 | W | qintC | 0 | W | Exterior walls/roof/floor
[6 empty] | 78.84 | GJ |  | 31.536 | GJ |  |  |  |  | Conductivity | Thickness | Conductance | Resistance | Density | Specific Heat
[5 empty] | qAB | -374.9169 | W | qBC | -527.9474 | W |  |  |  | Element | (W/(m·K)) | (m) | (W/(m2·K)) | (m2·K/W) | (kg/m3) | (J/(kg·K))
[6 empty] | -11.8234 | GJ |  | -16.6494 | GJ | Tc | 15 | °C | Int Combined Surf Coef |  |  | 8.29 | 0.12063
[5 empty] | TA | 30.3092 | °C | TB | 23.952 | °C | qC | 1600.3957 | W | Exterior Wall Material | 0.24 | 0.15 | 1.6 | 0.625 | 1400 | 1000
[12 empty] | 50.4701 | GJ | Ext Combined Surf Coef |  |  | 30.4872 | 0.032801
[6 empty] | -138.5456 | W |  | -195.0961 | W |  | 108.9679 | W | Total air-air |  |  | 1.2846 | 0.77843
[6 empty] | -4.3692 | GJ |  | -6.1525 | GJ |  | 3.4364 | GJ | ext coeff corresponds w/ | windspeed | 4.3 | m/s
[6 empty] | 0.021672 | kg/s |  | 0.021672 | kg/s |  | 0.021672 | kg/s |  | surf coeff | 30.4872 | W/m2K | brick/rough plaster
[6 empty] | 78.02 |  |  | 78.02 |  |  | 78.02 | kg/h
[6 empty] | Zone A |  |  | Zone B |  |  | Zone C |  | IP using ASHRAE (2001) Conversion Factors
[5 empty] | NOTES | [9 empty] | Conductivity | Thickness | Conductance | Resistance | Density | Specific Heat
[5 empty] | Zone C uses a ZoneHVAC:WindowAirConditioner to provide cooling. | [8 empty] | Element | (Btu/(h·ft°·F)) | (ft) | (Btu/(h·ft2·°F)) | (h·ft2·°F/Btu) | (lb/ft3) | (Btu/(lb·°F))
[5 empty] | The A/C was obtained from BESTEST CE100 (figure at bottom left). | [8 empty] | Int Combined Surf Coef |  |  | 1.46 | 0.68492
[5 empty] | A simple air handling system in CONTAM is utilized in ZoneC. | [8 empty] | Exterior Wall Material | 0.13865 | 0.49213 | 0.28179 | 3.5488 | 87.5 | 0.23901
[5 empty] | A Fan:ZoneExhaust is used to provide an imbalance of flow out of ZoneC thus leading to Mixed airflow into ZoneB | [8 empty] | Ext Combined Surf Coef |  |  | 5.3694 | 0.18624
[5 empty] | It employs a Balanced Exhaust Fraction Schedule of 0.0 to drive overpressurizaton of the zone. | [8 empty] | Total air-air |  |  | 0.22625 | 4.4199
[5 empty] | Balanced => exhaust flow is balanced by Mixing/Infiltration flows. So a schedule of 0.0 => OA is brought in via | [12 empty] | MZ-Results-Annuals.xls!Analytical-MZ320
the OASystem to make up for the exhaust flow: Qoa = QoaMin + Qexh_unbalance
Perhaps this could be implemented via a control/fmu item.
EnergyPlus IDF Input
[9 empty] | ZoneInfiltrationDesignFlowRate | 0.018 | m3/s
[10 empty] | 0.5 | 1/h
kg/m3
[9 empty] | RHOzoneC | 1.2249
[9 empty] | RHOzoneB | 1.188
[9 empty] | RHOzoneA | 1.1631
ZoneMixing (Qij, from j-into-i)
[6 empty] | Qij-EP = ACR V rj/ri |  |  | QmixZoneCtoB | 0.018243 | m3/s
[9 empty] | QmixZoneBtoA | 0.018633 | m3/s
Sensible Heat Gain Summary (…Table.html)
[10 empty] | Zone A | Zone B | Zone C
[8 empty] | Interzone Air Transfer Heat Removal | [GJ] | -4.3692 | -6.1525 | 0
[8 empty] | Infiltration Heat Addition | [GJ] | - | - | 3.4364
[8 empty] | Opaque Surface Conduction and Other Heat Removal | [W] | -74.4708 | -25.3835 | -
[8 empty] | Opaque Surface Conduction and Other Heat Addition | [GJ] | - | - | 47.0337
Note on R19: Ideally zero. Set fan pressure rises to 0.00 in Eplus to implement zero-energy fans. So, either enter Fan energy added to zone/air stream, i.e., exh, sup, window a/c, here OR Subtract it from cooling energy simulation results OR set Pressure Rise to 0.0.
Note on P42: Converted to mass flow rate using outdoor air density.

## EPlusResultTables
MZ320-WindowACTable.csv |  |  | MZ320-IdealLoadsTable.csv
Annual and Peak Values - Other |  |  | Site and Source Energy
|  | Annual Value [GJ] |  |  | Total Energy [GJ]
| EnergyTransfer:Facility | 97.52 |  | Total Site Energy | 50.48
| EnergyTransfer:Building | 47.04
| EnergyTransfer:Zone:1_ZONEA | 0
| Heating:EnergyTransfer | 0
| Heating:EnergyTransfer:Zone:1_ZONEA | 0
| Cooling:EnergyTransfer | 47.04
| Cooling:EnergyTransfer:Zone:1_ZONEA | 0
| EnergyTransfer:Zone:1_ZONEB | 0
| Heating:EnergyTransfer:Zone:1_ZONEB | 0
| Cooling:EnergyTransfer:Zone:1_ZONEB | 0
| EnergyTransfer:Zone:1_ZONEC | 47.04
| Heating:EnergyTransfer:Zone:1_ZONEC | 0
| Cooling:EnergyTransfer:Zone:1_ZONEC | 47.04
| EnergyTransfer:HVAC | 50.48
| CoolingCoils:EnergyTransfer | 50.48

## Reference
Dols, W.S., S.J. Emmerich, and B.J. Polidoro, Coupling the Multizone Airflow and Contaminant Transport Software CONTAM with EnergyPlus using Co-simulation. Building Simulation, 2016. 9: p. 469-479.