## I 01-14
Alarm Model - Unit | worst-case orientation (1) |  |  | worst-case orientation (2) |  |  | worst-case orientation (3) |  |  | worst-case orientation 2X velocity |  |  | best-case orientation
| Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA
I-01-1 | 294 | 1.55 | 55.8
I-01-2 | 222 | 1.1 | 59.1
I-01-3 | 303 | 1.53 | 54.7
I-01-4 | 247 | 1.29 | 58.9
I-01-5 | 263 | 1.42 | 55.6
I-01-6 | 203 | 1.08 | 62.2 | 199 | 1.01 | 59.7 | 185 | 1.11 | 62.3 | 204 | 1.22 | 64.3 | 135 | 0.69 | 67.7
I-02-1 | 145 | 0.89 | 71.2
I-02-2 | 146 | 0.82 | 73.3
I-02-3 | 124 | 0.75 | 72.8
I-02-4 | 190 | 1.01 | 69.2
I-02-5 | 159 | 0.96 | 69.3
I-02-6 | 132 | 0.75 | 70.5 | 143 | 0.76 | 71.1 | 167 | 0.93 | 68.7 | 92 | 0.54 | 78.7 | 92 | 0.5 | 78.3
I-03-1 | 84 | 0.46 | 82.9
I-03-2 | 104 | 0.55 | 77.9
I-03-3 | 72 | 0.51 | 85.8
I-03-4 | 116 | 0.69 | 77.4
I-03-5 | 119 | 0.67 | 76.4
I-03-6 | 102 | 0.5 | 78.1 | 109 | 0.63 | 76.2 | 95 | 0.53 | 77.7 | 81 | 0.46 | 83.8 | 95 | 0.47 | 80.9
I-04-1 | 65 | 0.42 | 87.4
I-04-2 | 62 | 0.36 | 86.6
I-04-3 | 83 | 0.48 | 83
I-04-4 | 54 | 0.34 | 90.5
I-04-5 | 64 | 0.43 | 88
I-04-6 | 75 | 0.56 | 86.5 | 75 | 0.41 | 85.5 | 65 | 0.38 | 86.4 | 60 | 0.38 | 88.4 | 54 | 0.33 | 87.5
I-05-1 | 295 | 1.32 | 58.6
I-05-2 | 195 | 1.09 | 63.3
I-05-3 | 230 | 1.14 | 60.8
I-05-4 | 221 | 1.07 | 61.1
I-05-5 | 217 | 1.13 | 60.4
I-05-6 | 239 | 1.18 | 60.2 | 214 | 1.17 | 58.8 | 232 | 1.27 | 61.2 | 147 | 0.99 | 66.6 | 193 | 0.87 | 67.6
I-06-1 | 195 | 1.07 | 64.1
I-06-2 | 210 | 1.07 | 61.7
I-06-3 | 189 | 0.92 | 63.5
I-06-4 | 178 | 0.92 | 63.9
I-06-5 | 257 | 1.35 | 58.1
I-06-6 | 263 | 1.43 | 58.5 | 241 | 1.2 | 59.1 | 246 | 1.3 | 57.2 | 182 | 1.11 | 61.4 | 194 | 1.01 | 62.5
I-07-1 | 134 | 0.8 | 70.3
I-07-2 | 166 | 0.9 | 65.2
I-07-3 | 179 | 1.02 | 66.7
I-07-4 | 166 | 0.92 | 67.9
I-07-5 | 177 | 0.88 | 68.6
I-07-6 | 156 | 0.78 | 69.3 | 164 | 0.87 | 69.8 | 140 | 0.9 | 69.8 | 96 | 0.53 | 81 | 92 | 0.45 | 77.3
I-08-1 | 152 | 0.8 | 70.8
I-08-2 | 129 | 0.69 | 72.4
I-08-3 | 141 | 0.87 | 71.4
I-08-4 | 151 | 0.86 | 70.2
I-08-5 | 125 | 0.73 | 72.6
I-08-6 | 141 | 0.77 | 71 | 127 | 0.7 | 70.7 | 157 | 0.79 | 69.4 | 130 | 0.68 | 73.3 | 141 | 0.69 | 71.4
I-09-1 | 133 | 0.68 | 71.4
I-09-2 | 135 | 0.71 | 71.9
I-09-3 | 147 | 0.76 | 69.8
I-09-4 | 147 | 0.86 | 72.1
I-09-5 | 114 | 0.64 | 74.3
I-09-6 | 125 | 0.66 | 73.4 | 146 | 0.75 | 73.1 | 138 | 0.85 | 72.7 | 99 | 0.52 | 77.5 | 106 | 0.57 | 76.3
I-10-1 | 154 | 0.87 | 66.2
I-10-2 | 155 | 0.82 | 67.1
I-10-3 | 160 | 0.78 | 67.7
I-10-4 | 147 | 0.87 | 68.6
I-10-5 | 201 | 1.06 | 66.6
I-10-6 | 174 | 0.99 | 65.5 | 183 | 0.9 | 67.6 | 164 | 0.87 | 66 | 104 | 0.49 | 77.5 | 137 | 0.63 | 74.4
I-11-1 | 241 | 1.38 | 56.9
I-11-2 | 181 | 1.06 | 63.1
I-11-3 | 212 | 1.15 | 59.8
I-11-4 | 273 | 1.39 | 56
I-11-5 | 265 | 1.33 | 57.9
I-11-6 | 212 | 1.22 | 61.9 | 250 | 1.2 | 58.2 | 220 | 1.17 | 58.6 | 186 | 0.93 | 68 | 146 | 0.65 | 69.2
I-12-1 | 217 | 1.26 | 63.6
I-12-2 | 281 | 1.53 | 58.2
I-12-3 | 187 | 0.97 | 65.1
I-12-4 | 218 | 1.12 | 60.1
I-12-5 | 217 | 1.14 | 61.4
I-12-6 | 209 | 1.24 | 62.5 | 198 | 0.99 | 64.3 | 163 | 0.95 | 64.2 | 159 | 0.87 | 70.7 | 132 | 0.7 | 71.4
I-13-1 | 284 | 1.31 | 56.9
I-13-2 | 422 | 1.99 | 49.9
I-13-3 | 277 | 1.25 | 55
I-13-4 | 352 | 1.71 | 52.6
I-13-5 | 383 | 1.84 | 50.4
I-13-6 | 287 | 1.47 | 55.4 | 364 | 1.8 | 51.1 | 286 | 1.43 | 55.2 | 293 | 1.5 | 57.4 | 218 | 1.03 | 59.1
I-14-1 | 312 | 1.41 | 53.9
I-14-2 | 390 | 1.8 | 51
I-14-3 | 254 | 1.21 | 60.4
I-14-4 | 317 | 1.47 | 54.7
I-14-5 | 284 | 1.33 | 54.1
I-14-6 | 310 | 1.51 | 55.3 | 309 | 1.67 | 53.1 | 342 | 1.76 | 54 | 215 | 1.23 | 59 | 252 | 1.15 | 56.6

## PI01-04
Alarm Model - Unit | worst-case orientation (1) |  |  | worst-case orientation (2) |  |  | worst-case orientation (3) |  |  | worst-case orientation 2X velocity |  |  | best-case orientation
| Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA
PI-01-1 | 169 | 0.92 | 67.9
PI-01-2 | 198 | 1 | 68.3
PI-01-3 | 204 | 1.02 | 67.8
PI-01-4 | 204 | 1.14 | 66.2
PI-01-5 | 172 | 1.05 | 66.8
PI-01-6 | 201 | 1.03 | 65.6 | 172 | 0.92 | 67.6 | 190 | 0.97 | 68.7 | 151 | 0.8 | 72.2 | 140 | 0.78 | 70
PI-02-1 | 234 | 1.16 | 62.3
PI-02-2 | 176 | 0.98 | 67.4
PI-02-3 | 198 | 1 | 64.6
PI-02-4 | 158 | 0.82 | 69
PI-02-5 | 169 | 0.89 | 70.4
PI-02-6 | 169 | 0.87 | 68.3 | 191 | 0.98 | 68.8 | 160 | 0.79 | 66.2 | 150 | 0.81 | 73 | 138 | 0.72 | 68.1
PI-03-1 | 97 | 0.68 | 79.2
PI-03-2 | 138 | 0.78 | 70.1
PI-03-3 | 102 | 0.67 | 77.2
PI-03-4 | 118 | 0.75 | 74.7
PI-03-5 | 154 | 0.95 | 69 | 163 | 0.88 | 68.4 | 154 | 0.91 | 69.5
PI-03-6 | 112 | 0.6 | 75.1 | 126 | 0.75 | 75.7 | 119 | 0.7 | 77.8 | 86 | 0.52 | 83.7 | 84 | 0.42 | 81
PI-04-1 | 204 | 1.05 | 63
PI-04-2 | 193 | 1.05 | 63.4
PI-04-3 | 180 | 1.18 | 62.6
PI-04-4 | 157 | 0.97 | 66.5
PI-04-5 | 189 | 0.87 | 70.3
PI-04-6 | 192 | 1.02 | 66.9 | 179 | 0.91 | 66.2 | 167 | 0.86 | 66.2 | 106 | 0.65 | 76.5 | 82 | 0.46 | 81.1

## IC001-04
Alarm Model - Unit | worst-case orientation (1) |  |  | worst-case orientation (2) |  |  | worst-case orientation (3) |  |  | worst-case orientation 2X velocity |  |  | best-case orientation
| Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA
ICO-01-1 | 186 | 1.04 | 66.3
ICO-01-2 | 189 | 1.04 | 65.4
ICO-01-3 | 183 | 1.04 | 66
ICO-01-4 | 198 | 0.95 | 62.9
ICO-01-5 | 187 | 1.02 | 68.1
ICO-01-6 | 203 | 1.04 | 63.1 | 196 | 1.02 | 62.8 | 195 | 1.05 | 62.1 | 142 | 0.79 | 70 | 156 | 0.78 | 66.8
ICO-02-1 | 183 | 1.03 | 66.6
ICO-02-2 | 193 | 1.04 | 67.9
ICO-02-3 | 180 | 1.09 | 68.3
ICO-02-4 | 189 | 0.92 | 66
ICO-02-5 | 426 | 2.18 | 47.6 | 424 | 2.16 | 49.3 | 285 | 1.41 | 54.4
ICO-02-6 | 204 | 1.06 | 66 | 203 | 1.08 | 64.4 | 198 | 1.07 | 66.2 | 175 | 0.95 | 65.8 | 165 | 0.74 | 66.6
ICO-03-1 | 129 | 0.77 | 72.2
ICO-03-2 | 153 | 0.83 | 70
ICO-03-3 | 157 | 0.81 | 69.3
ICO-03-4 | 139 | 0.82 | 70.4
ICO-03-5 | 141 | 0.95 | 68.4
ICO-03-6 | 171 | 0.86 | 70.3 | 144 | 0.87 | 71.8 | 163 | 0.89 | 67.1 | 167 | 0.97 | 65.6 | 133 | 0.64 | 74.2
ICO-04-1 | 135 | 0.77 | 71.2
ICO-04-2 | 159 | 0.87 | 69.2
ICO-04-3 | 173 | 0.91 | 67.4
ICO-04-4 | 155 | 0.87 | 68.6
ICO-04-5 | 157 | 0.77 | 67.9
ICO-04-6 | 164 | 0.84 | 71.1 | 154 | 0.78 | 69 | 147 | 0.75 | 69.3 | 142 | 0.75 | 74 | 115 | 0.64 | 71.2

## P01-14
Alarm Model - Unit | worst-case orientation (1) |  |  | worst-case orientation (2) |  |  | worst-case orientation (3) |  |  | worst-case orientation 2X velocity |  |  | best-case orientation
| Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA
P-01-1 | 465 | 2.26 | 46 | 574 | 2.75 | 41.9
P-01-2 | 702 | 3.27 | 39.9
P-01-3 | 673 | 3.36 | 40.7
P-01-d | 713 | 3.32 | 39
P-01-5 | 808 | 3.77 | 38.6
P-01-6 | 569 | 2.68 | 44 | 689 | 2.93 | 42.4 | 602 | 2.84 | 42.1 | 695 | 3.19 | 40.6 | 637 | 2.67 | 40.8
P-02-1 | 505 | 2.42 | 43.7
P-02-2 | 485 | 2.53 | 43.6
P-02-3 | 622 | 2.82 | 42.9
P-02-4 | 798 | 3.85 | 37.9 | 849 | 3.89 | 38.2 | 717 | 3.43 | 40.1
P-02-5 | 572 | 2.86 | 42.1
P-02-6 | 363 | 1.83 | 50.9 | 391 | 1.94 | 49.5 | 397 | 1.9 | 47.1 | 185 | 1.02 | 66.8 | 211 | 0.98 | 56.5
P-03-1 | 598 | 2.84 | 40.9
P-03-2 | 525 | 2.52 | 42.6
P-03-c | 723 | 3.48 | 38.1
P-03-4 | 888 | 3.84 | 37.7 | 910 | 3.89 | 38.2
P-03-5 | 516 | 2.45 | 42.4
P-03-6 | 651 | 3.1 | 39.7 | 662 | 3.19 | 39.1 | 609 | 2.78 | 44.4 | 609 | 2.97 | 40.8 | 552 | 2.23 | 44.7
P-04-1 | 517 | 2.75 | 42.2
P-04-2 | 609 | 2.92 | 41.1
P-04-3 | 532 | 2.83 | 41
P-04-4 | 452 | 2.33 | 44.6
P-04-5 | 560 | 2.83 | 40.6
P-04-6 | 577 | 2.87 | 40 | 445 | 2.43 | 46.4 | 557 | 2.62 | 40.4 | 433 | 2.02 | 50.2 | 348 | 1.61 | 52
P-05-a | 447 | 2.13 | 44.7
P-05-b | 515 | 2.4 | 43.2
P-05-3 | 398 | 1.88 | 51.1
P-05-4 | 412 | 1.93 | 48.9
P-05-5 | 658 | 2.58 | 45.9
P-05-6 | 269 | 1.34 | 61.7 | 348 | 1.89 | 49.3 | 424 | 2.01 | 44.7 | 348 | 1.68 | 51.6 | 215 | 1.07 | 63.8
P-06-1 | 522 | 2.28 | 43
P-06-2 | 573 | 2.37 | 42.7
P-06-3 | 493 | 2.07 | 48.1
P-06-4 | 857 | 3.33 | 41.5 | 756 | 3.55 | 37.7
P-06-5 | 433 | 1.86 | 46.7
P-06-6 | 547 | 2.56 | 41.3 | 482 | 2.31 | 43.8 | 500 | 2.46 | 42 | 465 | 2.16 | 45.9 | 347 | 1.52 | 52.6
P-07-1 | 762 | 3.56 | 38.5
P-07-2 | 579 | 2.53 | 42.8
P-07-3 | 704 | 3.12 | 40.6
P-07-4 | 598 | 2.63 | 43.7
P-07-5 | 849 | 3.87 | 38.6 | 794 | 3.74 | 38.7
P-07-6 | 596 | 2.72 | 42.9 | 559 | 2.58 | 44.8 | 580 | 2.72 | 41.7 | 535 | 2.69 | 43.7 | 504 | 2.02 | 45.9
P-08-1` | 491 | 2.39 | 43.7
P-08-2 | 441 | 2.34 | 44.9
P-08-3 | 460 | 2.36 | 45.1
P-08-4 | 444 | 2.27 | 45.3
P-08-5 | 489 | 2.35 | 43.2
P-08-6 | 415 | 2.05 | 49.5 | 469 | 2.13 | 45.5 | 465 | 2.09 | 48.2 | 403 | 2.02 | 47.6 | 331 | 1.43 | 56.9
P-09-1 | 379 | 1.81 | 50.4
P-09-2 | 448 | 2.08 | 50.1
P-09-3 | 422 | 2.14 | 48.8
P-09-4 | 782 | 3.47 | 38.9 | 556 | 2.57 | 42.5
P-09-5 | 485 | 2.35 | 44.7
P-09-6 | 428 | 2.15 | 48.3 | 478 | 2.31 | 44.5 | 488 | 2.08 | 49.2 | 311 | 1.71 | 51.3 | 388 | 1.64 | 44.7
P-10-1 | 330 | 1.78 | 49.7
P-10-2 | 253 | 1.42 | 57.2
P-10-3 | 390 | 2.03 | 51.2
P-10-4 | 317 | 1.72 | 50.9
P-10-5 | 374 | 1.98 | 48.9
P-10-6 | 335 | 1.69 | 53.4 | 358 | 1.97 | 48.4 | 436 | 2.02 | 46.8 | 240 | 1.31 | 61.7 | 270 | 1.26 | 54.5
P-11-1 | 298 | 1.54 | 55.3
P-11-2 | 377 | 1.87 | 49
P-11-3 | 391 | 2.01 | 48
P-11-4 | 481 | 2.47 | 42.1
P-11-5 | 429 | 2.18 | 45.6
P-11-6 | 339 | 1.74 | 49.6 | 273 | 1.49 | 56.7 | 343 | 1.69 | 49.8 | 281 | 1.5 | 57.7 | 263 | 1.21 | 54
P-12-1 | 543 | 2.51 | 42.9
P-12-2 | 428 | 2.06 | 46
P-12-3 | 480 | 2.49 | 43
P-12-4 | 481 | 2.27 | 46.4
P-12-5 | 372 | 2.03 | 49.2
P-12-6 | 428 | 2.21 | 47.1 | 511 | 2.22 | 45.9 | 468 | 2.45 | 43.4 | 390 | 2.01 | 48.4 | 374 | 1.57 | 48.3
P-13-1 | NA | NA | NA
P-13-2 | NA | NA | NA
P-13-3 | NA | NA | NA
P-13-4 | NA | NA | NA
P-13-5 | NA | NA | NA
P-13-6 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
P-14-1 | 766 | 3.43 | 41.9
P-14-2 | 766 | 3.55 | 38.3
P-14-3 | 719 | 3.35 | 39
P-14-4 | 631 | 3.25 | 40.2
P-14-5 | 752 | 3.62 | 38.6
P-14-6 | 611 | 2.86 | 39.7 | 595 | 2.93 | 39.2 | 554 | 2.67 | 42.8 | 526 | 2.44 | 44.1 | 409 | 1.64 | 52

## PCO01-07
Alarm Model - Unit | worst-case orientation (1) |  |  | worst-case orientation (2) |  |  | worst-case orientation (3) |  |  | worst-case orientation 2X velocity |  |  | best-case orientation
| Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA
PCO-01-1 | 738 | 3 | 42.2
PCO-01-2 | 614 | 2.76 | 40.5
PCO-01-3 | 716 | 3.04 | 40.4
PCO-01-4 | 650 | 2.71 | 41.1
PCO-01-5 | 741 | 3.02 | 40.1
PCO-01-6 | 671 | 3.06 | 39.4 | 683 | 2.84 | 41.9 | 671 | 3.14 | 40.4 | 503 | 2.43 | 42.7 | 461 | 2.08 | 43.6
PCO-02-1 | 1011 | 3.63 | 39.9
PCO-02-2 | 849 | 3.45 | 38.4
PCO-02-3 | 881 | 3.88 | 37.4
PCO-02-4 | 964 | 4.18 | 37.2
PCO-02-5 | 1084 | 4.31 | 41.6
PCO-02-6 | 948 | 3.79 | 37.9 | 867 | 3.86 | 37.1 | 912 | 4.08 | 38.5 | 421 | 2.21 | 46.8 | 499 | 1.93 | 45.5
PCO-03-1 | 508 | 2.43 | 47.9
PCO-03-2 | 647 | 3.04 | 42
PCO-03-3 | 526 | 2.57 | 44.7
PCO-03-4 | 422 | 2.22 | 48.6
PCO-03-5 | 563 | 2.86 | 42.7
PCO-03-6 | 568 | 2.78 | 41.8 | 659 | 3.25 | 39 | 601 | 3.02 | 40.3 | 445 | 2.28 | 44 | 301 | 1.37 | 56.9
PCO-04-1 | 806 | 3.58 | 38.8
PCO-04-2 | 793 | 3.51 | 38.8
PCO-04-3 | 553 | 2.7 | 41.8
PCO-04-4 | 738 | 3.21 | 40
PCO-04-5 | 684 | 3.11 | 39.8
PCO-04-6 | 643 | 2.9 | 40.3 | 623 | 2.92 | 41.1 | 626 | 3.07 | 39.4 | 473 | 2.23 | 45.6 | 539 | 2.14 | 40.8
PCO-05-1 | 225 | 1.18 | 62.7
PCO-05-2 | 285 | 1.56 | 56.8
PCO-05-3 | 307 | 1.63 | 53.3
PCO-05-4 | 297 | 1.47 | 52.5
PCO-05-5 | 320 | 1.67 | 51.9
PCO-05-6 | 237 | 1.28 | 61.7 | 319 | 1.52 | 52.1 | 254 | 1.43 | 56.5 | 262 | 1.27 | 58.4 | 215 | 1.08 | 61.7
PCO-06-1 | 234 | 1.15 | 58.3
PCO-06-2 | 217 | 1.16 | 62.6
PCO-06-3 | 213 | 1.21 | 59.2
PCO-06-4 | 246 | 1.12 | 58.7
PCO-06-5 | 210 | 1.1 | 61.9
PCO-06-6 | 215 | 1.06 | 64.6 | 229 | 1.14 | 61.5 | 228 | 1.23 | 59.4 | 210 | 1.12 | 61.6 | 174 | 0.82 | 65.5
PCO-07-1 | 638 | 2.95 | 40.9
PCO-07-2 | 568 | 2.87 | 41.2
PCO-07-3 | 733 | 3.36 | 40.1
PCO-07-4 | 627 | 2.88 | 40.8
PCO-07-5 | 607 | 2.94 | 40.6
PCO-07-6 | 582 | 2.72 | 43.2 | 576 | 2.92 | 41.1 | 603 | 2.77 | 42.1 | 589 | 2.94 | 40.1 | 1.92 | 46.5 | 46.5

## PT01-02
Alarm Model - Unit | worst-case orientation (1) |  |  | worst-case orientation (2) |  |  | worst-case orientation (3) |  |  | worst-case orientation 2X velocity |  |  | best-case orientation
| Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA | Talarm, s | Obs, %/ft | MIC, pA
PT-01-1 | 594 | 3.02 | 40.4
PT-01-2 | 615 | 3.24 | 38.7
PT-01-3 | 573 | 2.8 | 40.5
PT-01-4 | 406 | 2.14 | 47.8
PT-01-5 | 716 | 3.38 | 38.5
PT-01-6 | 582 | 2.86 | 40.9 | 581 | 2.82 | 42 | 556 | 2.88 | 41.2 | 386 | 1.88 | 52.1 | 373 | 1.58 | 55.9
PT-02-1 | 497 | 2.38 | 44.3
PT-02-2 | 400 | 2.17 | 47.3
PT-02-3 | 445 | 2.22 | 45.9
PT-02-4 | 462 | 2.01 | 50
PT-02-5 | 361 | 1.88 | 49.5
PT-02-6 | 480 | 2.36 | 42.9 | 532 | 2.45 | 42.3 | 519 | 2.36 | 45.4 | 429 | 2.25 | 44.4 | 421 | 1.7 | 46.3

## Room I01-14
| Flaming Polyurethane Foam |  |  |  |  | Smoldering Polyurethane Foam |  |  |  |  | Broiling Hamburgers |  |  |  |  | Frying Hamburger |  |  |  |  | Stir-frying Vegetables |  |  |  |  | Toasting Bread
|  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name
|  | Model-Unit | FFoamG#T# |  |  |  | Model-Unit | SFoamG#T# |  |  |  | Model-Unit | BHBG#T# |  |  |  | Model-Unit | FryHBG#T# |  |  |  | Model-Unit | SFG#T# |  |  |  | Model-Unit | ToastG#T#
|  | I01-6 | 1,1 | 1,2 | 1,3 |  | I01-4 | 1,1 | 1,2 | 1,3 |  | I01-5 | 1,1 | 1,2 | 1,3 |  | I01-3 | 1,1 | 1,1 | 1,1 |  | I01-2 | 1,1 | 1,1 | 1,1 |  | I01-1 | 1,1 | 1,2 | 1,3
Alarm Time (s) |  |  | 147 | 134 | 152 |  |  | NA | NA | NA |  |  | 1177 | 1346 | 1285 |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 2.144 | 2.16 | 2.166 |  |  | 10.447 | 10.981 | 13.511 |  |  | 1.0891 | 1.3243 | 1.42 |  |  | 1.6532 | 1.2159 | 1.2993 |  |  | 2.6414 | 2.6856 | 1.7068 |  |  | 0.088519 | 0.11194 | 0.074377
MIC (pA) |  |  | 72.788 | 71.075 | 67.308 |  |  | 63.727 | 67.194 | 63.32 |  |  | 64.016 | 60.062 | 59.481 |  |  | 78.887 | 81.099 | 81.804 |  |  | 65.16 | 84.635 | 75.634 |  |  | 75.282 | 70.765 | 71.806
|  | I02-6 | 1,1 | 1,2 | 1,3 |  | I02-4 | 1,1 | 1,2 | 1,3 |  | I02-5 | 1,1 | 1,2 | 1,3 |  | I02-3 | 1,1 | 1,1 | 1,1 |  | I02-2 | 1,1 | 1,1 | 1,1 |  | I02-1 | 1,1 | 1,2 | 1,3
Alarm Time (s) |  |  | 133 | 142 | 145 |  |  | 1139 | 1098 | 971 |  |  | 864 | 837 | 756 |  |  | NA | NA | NA |  |  | 288 | NA | 343 |  |  | NA | 230 | NA
Obscuration (%/ft) |  |  | 1.4711 | 2.6395 | 1.7145 |  |  | 9.811 | 9.8433 | 10.495 |  |  | 0.62237 | 0.4192 | 0.5014 |  |  | 1.6532 | 1.2159 | 1.2993 |  |  | 2.3477 | 2.6856 | 1.695 |  |  | 0.088519 | 0.022892 | 0.074377
MIC (pA) |  |  | 79.119 | 66.474 | 70.702 |  |  | 64.969 | 71.563 | 71.006 |  |  | 72.113 | 72.659 | 72.543 |  |  | 78.887 | 81.099 | 81.804 |  |  | 72.846 | 84.635 | 78.451 |  |  | 75.282 | 75.505 | 71.806
|  | I03-6 | 1,1 | 1,2 | 1,3 |  | I03-4 | 1,1 | 1,2 | 1,3 |  | I03-5 | 1,1 | 1,2 | 1,3 |  | I03-3 | 1,1 | 1,1 | 1,1 |  | I03-2 | 1,1 | 1,1 | 1,1 |  | I03-1 | 1,1 | 1,2 | 1,3
Alarm Time (s) |  |  | 112 | 113 | 123 |  |  | 906 | 946 | 912 |  |  | 608 | 678 | 649 |  |  | 162 | 186 | 174 |  |  | 226 | NA | 391 |  |  | 187 | 177 | 178
Obscuration (%/ft) |  |  | 0.83555 | 1.103 | 0.93856 |  |  | 4.7782 | 5.3082 | 8.2138 |  |  | 0.29416 | 0.28543 | 0.42151 |  |  | 0.015791 | 0.34975 | 0.26033 |  |  | 0.82005 | 2.6856 | 0.94573 |  |  | 0.039957 | -0.018865 | 0.01121
MIC (pA) |  |  | 88.39 | 81.64 | 79.93 |  |  | 76.718 | 79.775 | 76.62 |  |  | 81.589 | 77.358 | 77.178 |  |  | 98.113 | 92.002 | 95.378 |  |  | 83.229 | 84.635 | 79.954 |  |  | 84.665 | 86.901 | 85.185
|  | I04-6 | 2,1 | 2,2 | 2,3 |  | I04-4 | 2,1 | 2,2 | 2,3 |  | I04-5 | 2,1 | 2,2 | 2,3 |  | I04-3 | 2,1 | 2,2 | 2,3 |  | I04-2 | 2,1 | 2,2 | 2,3 |  | I04-1 | 2,1 | 2,2 | 2,3
Alarm Time (s) |  |  | 114 | 109 | 99 |  |  | 636 | 775 | 799 |  |  | 456 | 499 | 458 |  |  | 203 | 208 | 167 |  |  | 276 | 267 | 244 |  |  | 183 | 165 | 176
Obscuration (%/ft) |  |  | 0.59656 | 0.65341 | 0.87277 |  |  | 1.2084 | 2.5657 | 3.2243 |  |  | 0.15162 | 0.053543 | 0.0263 |  |  | 1.0303 | 1.0922 | 0.15947 |  |  | 1.4025 | 1.8395 | 1.7763 |  |  | 0.0090966 | 0.05859 | -0.0045819
MIC (pA) |  |  | 86.622 | 85.12 | 86.052 |  |  | 92.266 | 87.146 | 84.873 |  |  | 87.447 | 87.906 | 88.899 |  |  | 83.629 | 85.138 | 91.705 |  |  | 87.945 | 86.582 | 89.597 |  |  | 86.906 | 87.133 | 88.208
|  | I05-6 | 2,1 | 2,2 | 2,3 |  | I05-4 | 2,1 | 2,2 | 2,3 |  | I05-5 | 2,1 | 2,2 | 2,3 |  | I05-3 | 2,1 | 2,2 | 2,3 |  | I05-2 | 2,1 | 2,2 | 2,3 |  | I05-1 | 2,1 | 2,2 | 2,3
Alarm Time (s) |  |  | 148 | 143 | 119 |  |  | 889 | 867 | 845 |  |  | 944 | 900 | 903 |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 1.6021 | 1.4559 | 1.9923 |  |  | 6.2516 | 6.3793 | 4.6022 |  |  | 0.69866 | 0.58446 | 0.53177 |  |  | 1.3518 | 1.1587 | 1.4001 |  |  | 1.9448 | 2.0104 | 2.2597 |  |  | 0.027208 | 0.12184 | 0.056466
MIC (pA) |  |  | 73.77 | 72.259 | 74.121 |  |  | 79.174 | 79.127 | 81.65 |  |  | 66.887 | 68.043 | 69.613 |  |  | 79.539 | 81.116 | 80.513 |  |  | 74.366 | 73.7 | 72.802 |  |  | 74.088 | 72.861 | 70.913
|  | I06-6 | 2,1 | 2,2 | 2,3 |  | I06-4 | 2,1 | 2,2 | 2,3 |  | I06-5 | 2,1 | 2,2 | 2,3 |  | I06-3 | 2,1 | 2,2 | 2,3 |  | I06-2 | 2,1 | 2,2 | 2,3 |  | I06-1 | 2,1 | 2,2 | 2,3
Alarm Time (s) |  |  | 156 | 159 | 121 |  |  | 676 | 923 | 1022 |  |  | 981 | 1083 | 1176 |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 1.9456 | 2.2517 | 2.1028 |  |  | 1.8326 | 8.3978 | 10.05 |  |  | 0.78032 | 0.93657 | 0.81392 |  |  | 1.3518 | 1.1587 | 1.4001 |  |  | 1.9448 | 2.0104 | 2.2597 |  |  | 0.027208 | 0.12184 | 0.056466
MIC (pA) |  |  | 69.857 | 64.377 | 72.82 |  |  | 90.484 | 73.278 | 70.581 |  |  | 65.574 | 61.95 | 62.225 |  |  | 79.539 | 81.116 | 80.513 |  |  | 74.366 | 73.7 | 72.802 |  |  | 74.088 | 72.861 | 70.913
|  | I07-6 | 3,1 | 3,2 | 3,3 |  | I07-4 | 3,1 | 3,2 | 3,3 |  | I07-5 | 3,1 | 3,2 | 3,3 |  | I07-3 | 3,1 | 3,2 | 3,3 |  | I07-2 | 3,1 | 3,2 | 3,3 |  | I07-1 | 3,1 | 3,2 | 3,3
Alarm Time (s) |  |  | 143 | 156 | 157 |  |  | 905 | 992 | 1013 |  |  | 754 | 773 | 652 |  |  | 218 | 233 | NA |  |  | 341 | 334 | 319 |  |  | 219 | 251 | 234
Obscuration (%/ft) |  |  | 1.4724 | 1.2753 | 1.8897 |  |  | 6.6923 | 10.507 | 11.752 |  |  | 0.19293 | 0.23129 | 0.35706 |  |  | 1.1859 | 1.071 | 1.214 |  |  | 1.9009 | 1.8233 | 2.1611 |  |  | 0.045136 | 0.066697 | 0.043358
MIC (pA) |  |  | 72.648 | 74.069 | 70.576 |  |  | 72.387 | 68.811 | 66.686 |  |  | 78.204 | 75.78 | 78.806 |  |  | 87.365 | 84.97 | 82.505 |  |  | 76.72 | 78.137 | 77.623 |  |  | 79.966 | 76.103 | 78.074
|  | I08-6 | 3,1 | 3,2 | 3,3 |  | I08-4 | 3,1 | 3,2 | 3,3 |  | I08-5 | 3,1 | 3,2 | 3,3 |  | I08-3 | 3,1 | 3,2 | 3,3 |  | I08-2 | 3,1 | 3,2 | 3,3 |  | I08-1 | 3,1 | 3,2 | 3,3
Alarm Time (s) |  |  | 145 | 159 | 151 |  |  | 966 | 985 | 821 |  |  | 906 | 810 | 736 |  |  | NA | 198 | 223 |  |  | 332 | 328 | 324 |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 1.5235 | 1.3662 | 1.5929 |  |  | 9.0959 | 10.293 | 6.53 |  |  | 0.36078 | 0.27605 | 0.43948 |  |  | 1.2617 | 0.7487 | 1.1938 |  |  | 1.8217 | 1.7721 | 2.2066 |  |  | 0.047746 | 0.089111 | 0.056014
MIC (pA) |  |  | 71.794 | 73.378 | 74.218 |  |  | 69.207 | 69.316 | 76.623 |  |  | 72.139 | 73.77 | 73.851 |  |  | 81.106 | 88.076 | 85.653 |  |  | 78.799 | 79.693 | 76.284 |  |  | 76.504 | 72.373 | 72.827
|  | I09-6 | 3,1 | 3,2 | 3,3 |  | I09-4 | 3,1 | 3,2 | 3,3 |  | I09-5 | 3,1 | 3,2 | 3,3 |  | I09-3 | 3,1 | 3,2 | 3,3 |  | I09-2 | 3,1 | 3,2 | 3,3 |  | I09-1 | 3,1 | 3,2 | 3,3
Alarm Time (s) |  |  | 145 | 171 | 157 |  |  | 922 | 1001 | 859 |  |  | 792 | 751 | 679 |  |  | 221 | 218 | NA |  |  | 340 | 329 | 323 |  |  | 240 | 249 | 238
Obscuration (%/ft) |  |  | 1.5235 | 2.0386 | 1.8897 |  |  | 7.2597 | 10.772 | 7.4077 |  |  | 0.24341 | 0.23434 | 0.40968 |  |  | 1.2238 | 1.128 | 1.214 |  |  | 1.8938 | 1.7842 | 2.1975 |  |  | 0.046381 | 0.065483 | 0.038738
MIC (pA) |  |  | 71.794 | 66.49 | 70.576 |  |  | 71.333 | 68.164 | 74.455 |  |  | 76.895 | 76.587 | 76.944 |  |  | 86.939 | 85.772 | 82.505 |  |  | 76.901 | 79.431 | 76.552 |  |  | 76.609 | 76.491 | 77.028
|  | I10-6 | 4,1 | 4,2 | 4,3 |  | I10-4 | 4,1 | 4,2 | 4,3 |  | I10-5 | 4,1 | 4,2 | 4,3 |  | I10-3 | 4,1 | 4,2 | 4,3 |  | I10-2 | 4,1 | 4,2 | 4,3 |  | I10-1 | 4,1 | 4,2 | 4,3
Alarm Time (s) |  |  | 175 | 141 | 155 |  |  | 859 | 1028 | 983 |  |  | 756 | 976 | 960 |  |  | 182 | NA | NA |  |  | 345 | 328 | 324 |  |  | 236 | 245 | NA
Obscuration (%/ft) |  |  | 2.3647 | 2.2798 | 2.072 |  |  | 8.6859 | 8.5159 | 9.9328 |  |  | 0.32265 | 0.43946 | 0.45645 |  |  | 0.12271 | 1.0818 | 1.2392 |  |  | 1.9119 | 2.469 | 2.0848 |  |  | 0.021916 | 0.055887 | 0.11527
MIC (pA) |  |  | 68.027 | 69.823 | 67.512 |  |  | 73.395 | 70.344 | 69.695 |  |  | 75.242 | 71.435 | 74.279 |  |  | 95.825 | 83.192 | 80.161 |  |  | 78.461 | 77.325 | 77.212 |  |  | 79.432 | 75.002 | 74.008
|  | I11-6 | 4,1 | 4,2 | 4,3 |  | I11-4 | 4,1 | 4,2 | 4,3 |  | I11-5 | 4,1 | 4,2 | 4,3 |  | I11-3 | 4,1 | 4,2 | 4,3 |  | I11-2 | 4,1 | 4,2 | 4,3 |  | I11-1 | 4,1 | 4,2 | 4,3
Alarm Time (s) |  |  | 167 | 140 | 156 |  |  | 968 | 1119 | 1015 |  |  | 1008 | 1020 | 1137 |  |  | NA | NA | NA |  |  | NA | 344 | NA |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 1.6002 | 2.2095 | 2.129 |  |  | 14.174 | 10.618 | 10.91 |  |  | 0.66461 | 0.58774 | 0.60412 |  |  | 1.0168 | 1.0818 | 1.2392 |  |  | 1.9768 | 2.6456 | 2.2039 |  |  | 0.022224 | 0.056176 | 0.11527
MIC (pA) |  |  | 73.016 | 70.436 | 66.928 |  |  | 64.779 | 66.03 | 67.703 |  |  | 65.838 | 70.011 | 68.829 |  |  | 83.371 | 83.192 | 80.161 |  |  | 75.157 | 73.726 | 73.292 |  |  | 76.122 | 72.847 | 74.008
|  | I12-6 | 4,1 | 4,2 | 4,3 |  | I12-4 | 4,1 | 4,2 | 4,3 |  | I12-5 | 4,1 | 4,2 | 4,3 |  | I12-3 | 4,1 | 4,2 | 4,3 |  | I12-2 | 4,1 | 4,2 | 4,3 |  | I12-1 | 4,1 | 4,2 | 4,3
Alarm Time (s) |  |  | 174 | 150 | 151 |  |  | 988 | NA | NA |  |  | 920 | 1060 | 1120 |  |  | 227 | NA | 218 |  |  | NA | NA | NA |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 2.271 | 3.0455 | 1.8655 |  |  | 14.902 | 10.665 | 11.502 |  |  | 0.56343 | 0.64817 | 0.58422 |  |  | 0.86166 | 1.0818 | 1.1375 |  |  | 1.9768 | 2.651 | 2.2039 |  |  | 0.022224 | 0.056176 | 0.11527
MIC (pA) |  |  | 68.821 | 63.369 | 69.79 |  |  | 63.329 | 64.581 | 64.071 |  |  | 69.846 | 68.596 | 69.34 |  |  | 87.902 | 83.192 | 80.733 |  |  | 75.157 | 73.014 | 73.292 |  |  | 76.122 | 72.847 | 74.008
|  | I13-6 | 5,1 | 5,2 | 5,3 |  | I13-4 | 5,1 | 5,2 | 5,3 |  | I13-5 | 5,1 | 5,2 | 5,3 |  | I13-3 | 5,1 | 5,2 | 5,3 |  | I13-2 | 5,1 | 5,2 | 5,3 |  | I13-1 | 5,1 | 5,2 | 5,3
Alarm Time (s) |  |  | 165 | 160 | 144 |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 3.0767 | 2.7034 | 3.2276 |  |  | 9.0649 | 9.7937 | 9.2731 |  |  | 1.1856 | 1.4018 | 1.5735 |  |  | 1.8629 | 1.4843 | 1.346 |  |  | 2.512 | 2.0985 | 2.2335 |  |  | 0.10284 | 0.14779 | 0.12005
MIC (pA) |  |  | 58.868 | 61.17 | 60.763 |  |  | 64.998 | 64.778 | 63.931 |  |  | 59.576 | 58.617 | 56.725 |  |  | 76.812 | 80.405 | 81.231 |  |  | 71.559 | 74.99 | 74.765 |  |  | 71.901 | 73.534 | 72.748
|  | I14-6 | 5,1 | 5,2 | 5,3 |  | I14-4 | 5,1 | 5,2 | 5,3 |  | I14-5 | 5,1 | 5,2 | 5,3 |  | I14-3 | 5,1 | 5,2 | 5,3 |  | I14-2 | 5,1 | 5,2 | 5,3 |  | I14-1 | 5,1 | 5,2 | 5,3
Alarm Time (s) |  |  | 164 | 161 | 145 |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 2.9831 | 2.7959 | 3.3117 |  |  | 9.0649 | 9.7937 | 9.2731 |  |  | 1.1856 | 1.4018 | 1.5735 |  |  | 1.8629 | 1.4843 | 1.346 |  |  | 2.512 | 2.0985 | 2.2335 |  |  | 0.10284 | 0.14779 | 0.12005
MIC (pA) |  |  | 59.505 | 60.525 | 60.057 |  |  | 64.998 | 64.778 | 63.931 |  |  | 59.576 | 58.617 | 56.725 |  |  | 76.812 | 80.405 | 81.231 |  |  | 71.559 | 74.99 | 74.765 |  |  | 71.901 | 73.534 | 72.748

## Room ICO01-04
| Flaming Polyurethane Foam |  |  |  |  | Smoldering Polyurethane Foam |  |  |  |  | Broiling Hamburgers |  |  |  |  | Frying Hamburger |  |  |  |  | Stir-frying Vegetables |  |  |  |  | Toasting Bread
|  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name
|  | Model-Unit | FFoamG#T# |  |  |  | Model-Unit | SFoamG#T# |  |  |  | Model-Unit | BHBG#T# |  |  |  | Model-Unit | FryHBG#T# |  |  |  | Model-Unit | SFG#T# |  |  |  | Model-Unit | ToastG#T#
|  | ICO01-6 | 3,1 | 3,2 | 3,3 |  | ICO01-4 | 3,1 | 3,2 | 3,3 |  | ICO01-5 | 3,1 | 3,2 | 3,3 |  | ICO01-3 | 3,1 | 3,2 | 3,3 |  | ICO01-2 | 3,1 | 3,2 | 3,3 |  | ICO01-1 | 3,1 | 3,2 | 3,3
Alarm Time (s) |  |  | 156 | 172 | 163 |  |  | 1007 | 1018 | 958 |  |  | 1021 | 995 | 737 |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 2.0378 | 2.1219 | 2.2313 |  |  | 11.021 | 11.207 | 10.298 |  |  | 0.58924 | 0.5911 | 0.44025 |  |  | 1.2617 | 1.1698 | 1.214 |  |  | 1.9079 | 1.8386 | 2.2274 |  |  | 0.047746 | 0.089111 | 0.056014
MIC (pA) |  |  | 67.265 | 65.871 | 66.919 |  |  | 67.258 | 66.948 | 70.784 |  |  | 67.489 | 67.744 | 73.81 |  |  | 81.106 | 82.454 | 82.505 |  |  | 74.692 | 74.956 | 73.387 |  |  | 76.504 | 72.373 | 72.827
|  | ICO02-6 | 1,1 | 1,2 | 1,3 |  | ICO02-4 | 1,1 | 1,2 | 1,3 |  | ICO02-5 | 1,1 | 1,2 | 1,3 |  | ICO02-3 | 1,1 | 1,1 | 1,1 |  | ICO02-2 | 1,1 | 1,1 | 1,1 |  | ICO02-1 | 1,1 | 1,2 | 1,3
Alarm Time (s) |  |  | 168 | 159 | 174 |  |  | 1142 | 1108 | 988 |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | 308 | NA | NA |  |  | NA | NA | 221
Obscuration (%/ft) |  |  | 4.2211 | 3.8688 | 4.1055 |  |  | 9.8322 | 10.115 | 10.97 |  |  | 1.7809 | 1.6427 | 1.6191 |  |  | 1.6532 | 1.2159 | 1.2993 |  |  | 2.6263 | 2.6856 | 1.7068 |  |  | 0.088519 | 0.11194 | -0.015819
MIC (pA) |  |  | 64.7 | 57.113 | 54.034 |  |  | 64.837 | 71.006 | 69.894 |  |  | 56.269 | 58.75 | 58.065 |  |  | 78.887 | 81.099 | 81.804 |  |  | 68.189 | 84.635 | 75.634 |  |  | 75.282 | 70.765 | 76.24
|  | ICO03-6 | 3,1 | 3,2 | 3,3 |  | ICO03-4 | 3,1 | 3,2 | 3,3 |  | ICO03-5 | 3,1 | 3,2 | 3,3 |  | ICO03-3 | 3,1 | 3,2 | 3,3 |  | ICO03-2 | 3,1 | 3,2 | 3,3 |  | ICO03-1 | 3,1 | 3,2 | 3,3
Alarm Time (s) |  |  | 155 | 174 | 149 |  |  | 965 | 929 | 969 |  |  | 946 | 962 | 964 |  |  | NA | NA | NA |  |  | NA | NA | 332 |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 1.973 | 2.2886 | 1.4982 |  |  | 9.0507 | 8.0503 | 10.646 |  |  | 0.43195 | 0.52548 | 0.69368 |  |  | 1.2617 | 1.1698 | 1.214 |  |  | 1.9079 | 1.8386 | 2.2233 |  |  | 0.047746 | 0.089111 | 0.056014
MIC (pA) |  |  | 67.707 | 64.633 | 75.378 |  |  | 69.251 | 73.139 | 69.973 |  |  | 70.509 | 68.853 | 69.002 |  |  | 81.106 | 82.454 | 82.505 |  |  | 74.692 | 74.956 | 74.656 |  |  | 76.504 | 72.373 | 72.827
|  | ICO04-6 | 1,1 | 1,2 | 1,3 |  | ICO04-4 | 1,1 | 1,2 | 1,3 |  | ICO04-5 | 1,1 | 1,2 | 1,3 |  | ICO04-3 | 1,1 | 1,1 | 1,1 |  | ICO04-2 | 1,1 | 1,1 | 1,1 |  | ICO04-1 | 1,1 | 1,2 | 1,3
Alarm Time (s) |  |  | 138 | 135 | 150 |  |  | 1098 | 1062 | 958 |  |  | 953 | 917 | 972 |  |  | 215 | NA | NA |  |  | 283 | NA | NA |  |  | NA | 244 | 237
Obscuration (%/ft) |  |  | 1.6849 | 2.2186 | 1.9743 |  |  | 9.3835 | 8.7749 | 10.07 |  |  | 0.68129 | 0.56009 | 0.9507 |  |  | 1.1178 | 1.2159 | 1.2993 |  |  | 2.2491 | 2.6856 | 1.7068 |  |  | 0.088519 | 0.032796 | 0.019748
MIC (pA) |  |  | 76.813 | 70.496 | 68.326 |  |  | 66.519 | 73.616 | 72.065 |  |  | 68.906 | 69.273 | 65.249 |  |  | 86.685 | 81.099 | 81.804 |  |  | 74.06 | 84.635 | 75.634 |  |  | 75.282 | 73.285 | 73.002

## Room PI01-04
| Flaming Polyurethane Foam |  |  |  |  | Smoldering Polyurethane Foam |  |  |  |  | Broiling Hamburgers |  |  |  |  | Frying Hamburger |  |  |  |  | Stir-frying Vegetables |  |  |  |  | Toasting Bread
|  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name
|  | Model-Unit | FFoamG#T# |  |  |  | Model-Unit | SFoamG#T# |  |  |  | Model-Unit | BHBG#T# |  |  |  | Model-Unit | FryHBG#T# |  |  |  | Model-Unit | SFG#T# |  |  |  | Model-Unit | ToastG#T#
|  | PI01-6 | 2,1 | 2,2 | 2,3 |  | PI01-4 | 2,1 | 2,2 | 2,3 |  | PI01-5 | 2,1 | 2,2 | 2,3 |  | PI01-3 | 2,1 | 2,2 | 2,3 |  | PI01-2 | 2,1 | 2,2 | 2,3 |  | PI01-1 | 2,1 | 2,2 | 2,3
Alarm Time (s) |  |  | 155 | 147 | 122 |  |  | 728 | 769 | 714 |  |  | 883 | 849 | 821 |  |  | 208 | 230 | 212 |  |  | 182 | 184 | 243 |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 1.8998 | 1.6173 | 2.1581 |  |  | 2.9143 | 2.4188 | 1.9163 |  |  | 0.55334 | 0.45029 | 0.32506 |  |  | 1.1698 | 1.0463 | 1.2565 |  |  | 0.70374 | 0.68895 | 1.7492 |  |  | 0.027208 | 0.12184 | 0.056466
MIC (pA) |  |  | 70.375 | 70.494 | 72.169 |  |  | 87.432 | 87.389 | 88.952 |  |  | 69.078 | 70.767 | 72.915 |  |  | 82.096 | 82.928 | 81.413 |  |  | 91.774 | 93.257 | 89.876 |  |  | 74.088 | 72.861 | 70.913
|  | PI02-6 | 2,1 | 2,2 | 2,3 |  | PI02-4 | 2,1 | 2,2 | 2,3 |  | PI02-5 | 2,1 | 2,2 | 2,3 |  | PI02-3 | 2,1 | 2,2 | 2,3 |  | PI02-2 | 2,1 | 2,2 | 2,3 |  | PI02-1 | 2,1 | 2,2 | 2,3
Alarm Time (s) |  |  | 167 | 165 | 170 |  |  | 703 | 785 | 742 |  |  | 755 | 809 | 819 |  |  | 205 | 223 | 232 |  |  | 195 | 253 | 258 |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 2.6498 | 2.6792 | 5.8 |  |  | 2.3716 | 2.8882 | 2.2585 |  |  | 0.34806 | 0.37699 | 0.32613 |  |  | 1.0861 | 1.1209 | 1.3652 |  |  | 0.66751 | 1.6637 | 2.1092 |  |  | 0.027208 | 0.12184 | 0.056466
MIC (pA) |  |  | 63.676 | 61.027 | 0 |  |  | 89.008 | 86.636 | 87.457 |  |  | 75.441 | 73.229 | 73.009 |  |  | 83.016 | 83.946 | 80.722 |  |  | 91.604 | 89.319 | 85.997 |  |  | 74.088 | 72.861 | 70.913
|  | PI03-6 | 3,1 | 3,2 | 3,3 |  | PI03-4 | 3,1 | 3,2 | 3,3 |  | PI03-5 | 3,1 | 3,2 | 3,3 |  | PI03-3 | 3,1 | 3,2 | 3,3 |  | PI03-2 | 3,1 | 3,2 | 3,3 |  | PI03-1 | 3,1 | 3,2 | 3,3
Alarm Time (s) |  |  | 140 | 121 | 155 |  |  | 646 | 641 | 646 |  |  | 794 | 777 | 670 |  |  | 219 | 208 | 188 |  |  | 326 | 326 | 194 |  |  | 201 | 213 | 190
Obscuration (%/ft) |  |  | 1.3957 | 0.767 | 1.7854 |  |  | 1.3714 | 1.3881 | 1.7137 |  |  | 0.24631 | 0.23204 | 0.39443 |  |  | 1.1985 | 0.96727 | 0.33033 |  |  | 1.7374 | 1.7479 | 0.69597 |  |  | 0.039299 | 0.042777 | 0.022746
MIC (pA) |  |  | 73.93 | 82.934 | 71.789 |  |  | 88.002 | 89.625 | 89.267 |  |  | 76.802 | 75.6 | 77.565 |  |  | 87.223 | 86.683 | 90.491 |  |  | 80.734 | 80.217 | 90.332 |  |  | 83.104 | 82.365 | 86.046
|  | PI04-6 | 5,1 | 5,2 | 5,3 |  | PI04-4 | 5,1 | 5,2 | 5,3 |  | PI04-5 | 5,1 | 5,2 | 5,3 |  | PI04-3 | 5,1 | 5,2 | 5,3 |  | PI04-2 | 5,1 | 5,2 | 5,3 |  | PI04-1 | 5,1 | 5,2 | 5,3
Alarm Time (s) |  |  | 134 | 144 | 130 |  |  | 681 | 657 | 787 |  |  | 707 | 733 | 707 |  |  | 217 | 242 | 317 |  |  | 204 | 278 | 194 |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 1.2729 | 1.8024 | 2.0873 |  |  | 2.3816 | 2.2154 | 3.2112 |  |  | 0.23476 | 0.37142 | 0.24741 |  |  | 1.624 | 1.4531 | 1.0939 |  |  | 0.45462 | 1.3202 | 0.49274 |  |  | 0.10284 | 0.14779 | 0.12005
MIC (pA) |  |  | 75.162 | 70.77 | 70.76 |  |  | 87.234 | 88.839 | 82.739 |  |  | 79.166 | 76.84 | 80.665 |  |  | 81.405 | 81.789 | 82.165 |  |  | 92.308 | 87.619 | 91.553 |  |  | 71.901 | 73.534 | 72.748

## Room P01-14
| Flaming Polyurethane Foam |  |  |  |  | Smoldering Polyurethane Foam |  |  |  |  | Broiling Hamburgers |  |  |  |  | Frying Hamburger |  |  |  |  | Stir-frying Vegetables
|  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name
|  | Model-Unit | FFoamG#T# |  |  |  | Model-Unit | SFoamG#T# |  |  |  | Model-Unit | BHBG#T# |  |  |  | Model-Unit | FryHBG#T# |  |  |  | Model-Unit | SFG#T#
|  | P01-6 | 5,1 | 5,2 | 5,3 |  | P01-4 | 5,1 | 5,2 | 5,3 |  | P01-5 | 5,1 | 5,2 | 5,3 |  | P01-3 | 5,1 | 5,2 | 5,3 |  | P01-2 | 5,1 | 5,2 | 5,3
Alarm Time (s) |  |  | 209 | 202 | 182 |  |  | 645 | 649 | 698 |  |  | NA | NA | NA |  |  | 224 | 216 | 229 |  |  | 265 | 238 | 231
Obscuration (%/ft) |  |  | 7.8465 | 7.4188 | 7.1988 |  |  | 1.737 | 2.0557 | 1.6673 |  |  | 1.1856 | 1.4018 | 1.5735 |  |  | 1.7934 | 1.3044 | 1.3205 |  |  | 1.6025 | 1.4474 | 1.3882
MIC (pA) |  |  | 32.973 | 35.76 | 37.799 |  |  | 89.28 | 89.281 | 88.421 |  |  | 59.576 | 58.617 | 56.725 |  |  | 79.953 | 84.033 | 84.021 |  |  | 89.701 | 91.331 | 91.66
|  | P02-6 | 4,1 | 4,2 | 4,3 |  | P02-4 | 4,1 | 4,2 | 4,3 |  | P02-5 | 4,1 | 4,2 | 4,3 |  | P02-3 | 4,1 | 4,2 | 4,3 |  | P02-2 | 4,1 | 4,2 | 4,3
Alarm Time (s) |  |  | 183 | 169 | 199 |  |  | 729 | 786 | 696 |  |  | 1108 | 1158 | 1289 |  |  | 262 | 268 | 241 |  |  | 366 | 263 | 214
Obscuration (%/ft) |  |  | 3.155 | 5.021 | 6.1927 |  |  | 3.8025 | 3.7684 | 2.7916 |  |  | 0.58969 | 0.52191 | 0.56697 |  |  | 0.8727 | 1.0816 | 1.1455 |  |  | 0.76346 | 0.55259 | 0.72451
MIC (pA) |  |  | 61.618 | 49.768 | 40.783 |  |  | 82.473 | 82.313 | 85.148 |  |  | 67.792 | 70.734 | 69.868 |  |  | 87.548 | 85.713 | 80.638 |  |  | 91.962 | 93.679 | 92.017
|  | P03-6 | 5,1 | 5,2 | 5,3 |  | P03-4 | 5,1 | 5,2 | 5,3 |  | P03-5 | 5,1 | 5,2 | 5,3 |  | P03-3 | 5,1 | 5,2 | 5,3 |  | P03-2 | 5,1 | 5,2 | 5,3
Alarm Time (s) |  |  | 194 | 198 | 179 |  |  | 721 | 674 | 784 |  |  | 1352 | 1187 | 1310 |  |  | 234 | 210 | 217 |  |  | 180 | 175 | 185
Obscuration (%/ft) |  |  | 6.3367 | 6.9515 | 6.8851 |  |  | 3.0751 | 2.6114 | 3.1515 |  |  | 0.93645 | 0.77846 | 0.9574 |  |  | 1.8605 | 1.1672 | 1.1433 |  |  | 0.44972 | 0.56936 | 0.65395
MIC (pA) |  |  | 40.689 | 37.534 | 39.189 |  |  | 84.67 | 87.818 | 82.987 |  |  | 65.255 | 66.892 | 64.112 |  |  | 77.996 | 85.496 | 86.213 |  |  | 94.047 | 93.433 | 91.204
|  | P04-6 | 4,1 | 4,2 | 4,3 |  | P04-4 | 4,1 | 4,2 | 4,3 |  | P04-5 | 4,1 | 4,2 | 4,3 |  | P04-3 | 4,1 | 4,2 | 4,3 |  | P04-2 | 4,1 | 4,2 | 4,3
Alarm Time (s) |  |  | 206 | 200 | 209 |  |  | 839 | 1101 | 1015 |  |  | 1155 | 1115 | 1185 |  |  | 232 | 401 | 299 |  |  | 189 | 305 | 312
Obscuration (%/ft) |  |  | 6.2549 | 8.5071 | 7.2575 |  |  | 7.6405 | 10.422 | 10.91 |  |  | 0.93867 | 0.77485 | 0.64162 |  |  | 0.88926 | 0.83428 | 1.0144 |  |  | 0.78074 | 2.0826 | 1.9397
MIC (pA) |  |  | 42.99 | 33.425 | 35.467 |  |  | 74.597 | 66.762 | 67.703 |  |  | 61.117 | 66.188 | 67.94 |  |  | 87.016 | 83.26 | 85.149 |  |  | 92.184 | 82.66 | 80.66
|  | P05-6 | 3,1 | 3,2 | 3,3 |  | P05-4 | 3,1 | 3,2 | 3,3 |  | P05-5 | 3,1 | 3,2 | 3,3 |  | P05-3 | 3,1 | 3,2 | 3,3 |  | P05-2 | 3,1 | 3,2 | 3,3
Alarm Time (s) |  |  | 191 | 205 | 198 |  |  | 733 | 698 | 687 |  |  | 1196 | 1446 | 1308 |  |  | 225 | 223 | 232 |  |  | 324 | 188 | 184
Obscuration (%/ft) |  |  | 5.4062 | 6.0258 | 5.7004 |  |  | 2.5201 | 2.1453 | 2.4112 |  |  | 1.3246 | 1.0897 | 1.1942 |  |  | 1.2576 | 1.1628 | 1.214 |  |  | 1.7062 | 0.72537 | 0.74073
MIC (pA) |  |  | 46.442 | 43.628 | 43.59 |  |  | 84.157 | 87.193 | 87.25 |  |  | 58.903 | 59.862 | 59.39 |  |  | 86.44 | 85.537 | 84.418 |  |  | 81.409 | 92.229 | 91.061
|  | P06-6 | 4,1 | 4,2 | 4,3 |  | P06-4 | 4,1 | 4,2 | 4,3 |  | P06-5 | 4,1 | 4,2 | 4,3 |  | P06-3 | 4,1 | 4,2 | 4,3 |  | P06-2 | 4,1 | 4,2 | 4,3
Alarm Time (s) |  |  | 205 | 184 | 185 |  |  | 1036 | 1033 | 1257 |  |  | 981 | 1077 | 1173 |  |  | 222 | 217 | 197 |  |  | 180 | 187 | 330
Obscuration (%/ft) |  |  | 6.1154 | 6.9317 | 4.6675 |  |  | 15.33 | 8.6671 | 7.7428 |  |  | 0.61143 | 0.67904 | 0.6417 |  |  | 0.82433 | 1.0178 | 0.8142 |  |  | 0.68032 | 0.56497 | 2.1407
MIC (pA) |  |  | 43.758 | 40.037 | 49.079 |  |  | 61.166 | 70.086 | 71.293 |  |  | 67.12 | 67.861 | 68.128 |  |  | 88.872 | 86.616 | 83.012 |  |  | 93.286 | 93.021 | 75.477
|  | P07-6 | 3,1 | 3,2 | 3,3 |  | P07-4 | 3,1 | 3,2 | 3,3 |  | P07-5 | 3,1 | 3,2 | 3,3 |  | P07-3 | 3,1 | 3,2 | 3,3 |  | P07-2 | 3,1 | 3,2 | 3,3
Alarm Time (s) |  |  | 263 | 229 | 211 |  |  | 796 | 756 | 680 |  |  | NA | NA | NA |  |  | 236 | 238 | 254 |  |  | 340 | 345 | 191
Obscuration (%/ft) |  |  | 10.63 | 8.5591 | 7.441 |  |  | 3.7902 | 3.3556 | 2.2783 |  |  | 2.3393 | 1.1546 | 1.41 |  |  | 1.1787 | 0.98152 | 0.99073 |  |  | 1.8938 | 1.8265 | 0.73661
MIC (pA) |  |  | 23.44 | 29.726 | 35.541 |  |  | 80.393 | 83.547 | 87.598 |  |  | 51.98 | 58.815 | 56.61 |  |  | 85.685 | 84.906 | 82.828 |  |  | 76.901 | 75.704 | 90.5
|  | P08-6 | 3,1 | 3,2 | 3,3 |  | P08-4 | 3,1 | 3,2 | 3,3 |  | P08-5 | 3,1 | 3,2 | 3,3 |  | P08-3 | 3,1 | 3,2 | 3,3 |  | P08-2 | 3,1 | 3,2 | 3,3
Alarm Time (s) |  |  | 203 | 208 | 205 |  |  | 805 | 740 | 790 |  |  | NA | 1224 | 1162 |  |  | 225 | 209 | 242 |  |  | 189 | 188 | 188
Obscuration (%/ft) |  |  | 6.9281 | 6.4006 | 6.6537 |  |  | 4.0008 | 2.9867 | 5.6891 |  |  | 2.3393 | 0.88799 | 1.0234 |  |  | 1.2576 | 0.98562 | 1.1093 |  |  | 0.46562 | 0.72537 | 0.74431
MIC (pA) |  |  | 38.688 | 42.271 | 39.012 |  |  | 79.792 | 84.683 | 79.15 |  |  | 51.98 | 62.15 | 60.762 |  |  | 86.44 | 86.581 | 83.496 |  |  | 92.348 | 92.229 | 90.653
|  | P09-6 | 2,1 | 2,2 | 2,3 |  | P09-4 | 2,1 | 2,2 | 2,3 |  | P09-5 | 2,1 | 2,2 | 2,3 |  | P09-3 | 2,1 | 2,2 | 2,3 |  | P09-2 | 2,1 | 2,2 | 2,3
Alarm Time (s) |  |  | 201 | 188 | 171 |  |  | 797 | 838 | 876 |  |  | 1149 | 1251 | 1300 |  |  | 220 | 265 | 232 |  |  | 204 | 307 | 368
Obscuration (%/ft) |  |  | 6.2467 | 4.6259 | 6.1562 |  |  | 4.3289 | 5.1121 | 5.5532 |  |  | 1.17 | 1.1205 | 1.0266 |  |  | 1.3335 | 0.81652 | 1.3652 |  |  | 0.54547 | 1.8025 | 2.2471
MIC (pA) |  |  | 43.305 | 47.878 | 44.15 |  |  | 83.31 | 82.583 | 78.623 |  |  | 60.129 | 58.424 | 60.132 |  |  | 79.728 | 85.27 | 80.722 |  |  | 91.507 | 81.342 | 72.859
|  | P10-6 | 2,1 | 2,2 | 2,3 |  | P10-4 | 2,1 | 2,2 | 2,3 |  | P10-5 | 2,1 | 2,2 | 2,3 |  | P10-3 | 2,1 | 2,2 | 2,3 |  | P10-2 | 2,1 | 2,2 | 2,3
Alarm Time (s) |  |  | 153 | 193 | 175 |  |  | 916 | 940 | 916 |  |  | 925 | 976 | 1015 |  |  | 215 | 232 | 243 |  |  | 173 | 172 | 209
Obscuration (%/ft) |  |  | 1.8081 | 5.0897 | 6.6335 |  |  | 6.983 | 8.8066 | 6.7402 |  |  | 0.6541 | 0.78611 | 0.66482 |  |  | 1.2971 | 1.0215 | 1.1626 |  |  | 0.6156 | 0.55338 | 0.73918
MIC (pA) |  |  | 71.411 | 45.056 | 42.021 |  |  | 78.212 | 71.715 | 75.29 |  |  | 67.56 | 65.288 | 66.558 |  |  | 80.19 | 82.603 | 81.028 |  |  | 93.07 | 95.363 | 92.994
|  | P11-6 | 2,1 | 2,2 | 2,3 |  | P11-4 | 2,1 | 2,2 | 2,3 |  | P11-5 | 2,1 | 2,2 | 2,3 |  | P11-3 | 2,1 | 2,2 | 2,3 |  | P11-2 | 2,1 | 2,2 | 2,3
Alarm Time (s) |  |  | 197 | 198 | 179 |  |  | 693 | 787 | 715 |  |  | 1151 | 1331 | 1470 |  |  | 223 | 254 | 228 |  |  | 284 | 264 | 240
Obscuration (%/ft) |  |  | 5.8175 | 5.5796 | 7.0746 |  |  | 2.1648 | 2.9544 | 5.1915 |  |  | 1.1758 | 1.3016 | 1.1228 |  |  | 1.3473 | 0.84851 | 1.3827 |  |  | 1.387 | 1.8081 | 1.668
MIC (pA) |  |  | 45.129 | 42.255 | 39.985 |  |  | 89.583 | 86.532 | 80.726 |  |  | 60.094 | 56.198 | 58.742 |  |  | 79.587 | 84.552 | 80.618 |  |  | 87.483 | 87.078 | 90.712
|  | P12-6 | 1,1 | 1,2 | 1,3 |  | P12-4 | 1,1 | 1,2 | 1,3 |  | P12-5 | 1,1 | 1,2 | 1,3 |  | P12-3 | 1,1 | 1,1 | 1,1 |  | P12-2 | 1,1 | 1,1 | 1,1
Alarm Time (s) |  |  | 189 | 186 | 184 |  |  | 854 | 757 | 828 |  |  | 1039 | 1003 | 988 |  |  | 237 | 215 | 253 |  |  | 193 | 212 | 201
Obscuration (%/ft) |  |  | 6.9772 | 6.8567 | 5.1598 |  |  | 3.5065 | 2.1374 | 4.2694 |  |  | 0.90229 | 0.76053 | 0.99698 |  |  | 1.6238 | 1.0545 | 1.1466 |  |  | 0.77529 | 0.56003 | 0.56797
MIC (pA) |  |  | 57.279 | 44.413 | 47.789 |  |  | 81.37 | 88.273 | 85.314 |  |  | 66.446 | 65.539 | 64.541 |  |  | 83.255 | 87.684 | 85.29 |  |  | 87.157 | 92.026 | 92.394
|  | P13-6 | 1,1 | 1,2 | 1,3 |  | P13-4 | 1,1 | 1,2 | 1,3 |  | P13-5 | 1,1 | 1,2 | 1,3 |  | P13-3 | 1,1 | 1,1 | 1,1 |  | P13-2 | 1,1 | 1,1 | 1,1
Alarm Time (s) |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 11.28 | 11.138 | 11.058 |  |  | 10.447 | 10.981 | 13.511 |  |  | 1.7809 | 1.6427 | 1.6191 |  |  | 1.6532 | 1.2159 | 1.2993 |  |  | 2.6414 | 2.6856 | 1.7068
MIC (pA) |  |  | 19.575 | 20.751 | 20.323 |  |  | 63.727 | 67.194 | 63.32 |  |  | 56.269 | 58.75 | 58.065 |  |  | 78.887 | 81.099 | 81.804 |  |  | 65.16 | 84.635 | 75.634
|  | P14-6 | 1,1 | 1,2 | 1,3 |  | P14-4 | 1,1 | 1,2 | 1,3 |  | P14-5 | 1,1 | 1,2 | 1,3 |  | P14-3 | 1,1 | 1,1 | 1,1 |  | P14-2 | 1,1 | 1,1 | 1,1
Alarm Time (s) |  |  | 192 | 192 | 200 |  |  | 856 | 818 | 829 |  |  | 1643 | 1531 | NA |  |  | 236 | NA | 241 |  |  | NA | NA | NA
Obscuration (%/ft) |  |  | 7.3421 | 7.5278 | 6.7869 |  |  | 3.5557 | 2.7778 | 4.3121 |  |  | 1.5814 | 1.5632 | 1.6191 |  |  | 1.6172 | 1.2159 | 1.1577 |  |  | 2.6414 | 2.6856 | 1.7068
MIC (pA) |  |  | 56.134 | 41.785 | 38.69 |  |  | 81.19 | 85.972 | 85.23 |  |  | 57.821 | 59.002 | 58.065 |  |  | 83.397 | 81.099 | 85.79 |  |  | 65.16 | 84.635 | 75.634

## Room PCO01-07
| Flaming Polyurethane Foam |  |  |  |  | Smoldering Polyurethane Foam |  |  |  |  | Broiling Hamburgers |  |  |  |  | Frying Hamburger |  |  |  |  | Stir-frying Vegetables
|  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name
|  | Model-Unit | FFoamG#T# |  |  |  | Model-Unit | SFoamG#T# |  |  |  | Model-Unit | BHBG#T# |  |  |  | Model-Unit | FryHBG#T# |  |  |  | Model-Unit | SFG#T#
|  | PCO01-6 | 4,1 | 4,2 | 4,3 |  | PCO01-4 | 4,1 | 4,2 | 4,3 |  | PCO01-5 | 4,1 | 4,2 | 4,3 |  | PCO01-3 | 4,1 | 4,2 | 4,3 |  | PCO01-2 | 4,1 | 4,2 | 4,3
Alarm Time (s) |  |  | 203 | 178 | 189 |  |  | 605 | 667 | 599 |  |  | 1204 | 1060 | 1359 |  |  | 209 | 242 | 216 |  |  | 180 | 199 | 187
Obscuration (%/ft) |  |  | 5.8362 | 6.1695 | 5.1055 |  |  | 1.4256 | 1.5257 | 1.4848 |  |  | 1.0257 | 0.64817 | 1.0329 |  |  | 0.64515 | 1.0114 | 1.1216 |  |  | 0.68032 | 0.57521 | 0.69314
MIC (pA) |  |  | 45.296 | 43.732 | 46.754 |  |  | 89.23 | 90.257 | 90.434 |  |  | 59.796 | 68.596 | 63.55 |  |  | 91.623 | 84.093 | 80.924 |  |  | 93.286 | 92.684 | 92.225
|  | PCO02-6 | 4,1 | 4,2 | 4,3 |  | PCO02-4 | 4,1 | 4,2 | 4,3 |  | PCO02-5 | 4,1 | 4,2 | 4,3 |  | PCO02-3 | 4,1 | 4,2 | 4,3 |  | PCO02-2 | 4,1 | 4,2 | 4,3
Alarm Time (s) |  |  | 224 | 198 | 208 |  |  | 767 | 835 | 760 |  |  | 1108 | 1158 | 1289 |  |  | 262 | 268 | 241 |  |  | 366 | 263 | 214
Obscuration (%/ft) |  |  | 8.3294 | 8.3409 | 7.1512 |  |  | 4.9874 | 4.4438 | 4.381 |  |  | 0.81052 | 0.94754 | 0.97635 |  |  | 0.9608 | 0.85562 | 1.154 |  |  | 1.933 | 1.8873 | 0.71334
MIC (pA) |  |  | 31.983 | 34.16 | 35.967 |  |  | 79.757 | 78.131 | 81.568 |  |  | 62.711 | 64.535 | 65.079 |  |  | 85.559 | 84.88 | 82.072 |  |  | 75.332 | 88.722 | 92.404
|  | PCO03-6 | 4,1 | 4,2 | 4,3 |  | PCO03-4 | 4,1 | 4,2 | 4,3 |  | PCO03-5 | 4,1 | 4,2 | 4,3 |  | PCO03-3 | 4,1 | 4,2 | 4,3 |  | PCO03-2 | 4,1 | 4,2 | 4,3
Alarm Time (s) |  |  | 226 | 201 | 214 |  |  | 713 | 1224 | 717 |  |  | 959 | 1115 | 1152 |  |  | 224 | 225 | 225 |  |  | 212 | 222 | 213
Obscuration (%/ft) |  |  | 8.5051 | 8.5902 | 7.7564 |  |  | 3.3695 | 9.3368 | 3.216 |  |  | 0.58173 | 0.77485 | 0.62594 |  |  | 0.8451 | 1.0817 | 1.1882 |  |  | 0.73127 | 0.91515 | 0.70489
MIC (pA) |  |  | 31.37 | 33.058 | 33.439 |  |  | 83.557 | 65.407 | 84.013 |  |  | 68.167 | 66.188 | 68.482 |  |  | 88.434 | 85.928 | 80.243 |  |  | 92.268 | 93.622 | 92.323
|  | PCO04-6 | 2,1 | 2,2 | 2,3 |  | PCO04-4 | 2,1 | 2,2 | 2,3 |  | PCO04-5 | 2,1 | 2,2 | 2,3 |  | PCO04-3 | 2,1 | 2,2 | 2,3 |  | PCO04-2 | 2,1 | 2,2 | 2,3
Alarm Time (s) |  |  | 196 | 202 | 170 |  |  | 676 | 754 | 686 |  |  | 1100 | 1179 | 1239 |  |  | 221 | 244 | 210 |  |  | 371 | 318 | 186
Obscuration (%/ft) |  |  | 5.7102 | 5.9853 | 6.0339 |  |  | 1.8326 | 2.0574 | 1.5543 |  |  | 1.0602 | 1.0714 | 0.90707 |  |  | 1.3381 | 0.89958 | 1.2181 |  |  | 1.6279 | 1.8425 | 0.69837
MIC (pA) |  |  | 45.585 | 40.027 | 44.691 |  |  | 90.484 | 87.99 | 90.313 |  |  | 61.351 | 59.61 | 60.915 |  |  | 79.681 | 83.657 | 81.602 |  |  | 74.686 | 79.392 | 93.231
|  | PCO05-6 | 5,1 | 5,2 | 5,3 |  | PCO05-4 | 5,1 | 5,2 | 5,3 |  | PCO05-5 | 5,1 | 5,2 | 5,3 |  | PCO05-3 | 5,1 | 5,2 | 5,3 |  | PCO05-2 | 5,1 | 5,2 | 5,3
Alarm Time (s) |  |  | 182 | 180 | 169 |  |  | 717 | 735 | 735 |  |  | 1347 | 1327 | 1174 |  |  | 262 | 216 | 213 |  |  | 324 | 177 | 176
Obscuration (%/ft) |  |  | 4.9564 | 4.6965 | 5.7903 |  |  | 3.0117 | 4.4776 | 2.207 |  |  | 0.92228 | 1.0376 | 0.8359 |  |  | 1.5902 | 1.3044 | 1.0426 |  |  | 2.4096 | 0.59026 | 0.62486
MIC (pA) |  |  | 46.964 | 47.934 | 44.56 |  |  | 84.906 | 82.276 | 86.444 |  |  | 65.387 | 64.52 | 66.042 |  |  | 76.875 | 84.033 | 87.111 |  |  | 77.137 | 93.156 | 91.66
|  | PCO06-6 | 5,1 | 5,2 | 5,3 |  | PCO06-4 | 5,1 | 5,2 | 5,3 |  | PCO06-5 | 5,1 | 5,2 | 5,3 |  | PCO06-3 | 5,1 | 5,2 | 5,3 |  | PCO06-2 | 5,1 | 5,2 | 5,3
Alarm Time (s) |  |  | 182 | 184 | 164 |  |  | 650 | 590 | 624 |  |  | 1322 | 1193 | 1209 |  |  | 303 | 263 | 221 |  |  | 285 | 188 | 333
Obscuration (%/ft) |  |  | 4.9564 | 5.1989 | 5.2347 |  |  | 1.8209 | 1.3091 | 1.0241 |  |  | 0.86761 | 0.79941 | 0.86275 |  |  | 1.2481 | 1.4841 | 1.2203 |  |  | 1.8831 | 0.67264 | 2.1668
MIC (pA) |  |  | 46.964 | 45.212 | 47.648 |  |  | 89.026 | 91.472 | 91.084 |  |  | 65.864 | 66.814 | 65.529 |  |  | 79.33 | 80.677 | 85.457 |  |  | 85.863 | 92.332 | 78.302
|  | PCO07-6 | 5,1 | 5,2 | 5,3 |  | PCO07-4 | 5,1 | 5,2 | 5,3 |  | PCO07-5 | 5,1 | 5,2 | 5,3 |  | PCO07-3 | 5,1 | 5,2 | 5,3 |  | PCO07-2 | 5,1 | 5,2 | 5,3
Alarm Time (s) |  |  | 255 | 222 | 219 |  |  | 752 | 745 | 839 |  |  | 1616 | NA | NA |  |  | 236 | 223 | NA |  |  | 184 | 390 | 350
Obscuration (%/ft) |  |  | 10.793 | 9.2276 | 10.582 |  |  | 3.5518 | 4.8046 | 4.1473 |  |  | 1.1779 | 1.4018 | 1.5735 |  |  | 1.8558 | 1.4092 | 1.4843 |  |  | 0.48684 | 1.4473 | 2.2122
MIC (pA) |  |  | 21.35 | 27.405 | 24.504 |  |  | 83.109 | 81.158 | 78.653 |  |  | 59.698 | 58.617 | 56.725 |  |  | 77.747 | 83.287 | 80.405 |  |  | 93.583 | 77.692 | 75.781

## Room PT01-02
| Flaming Polyurethane Foam |  |  |  |  | Smoldering Polyurethane Foam |  |  |  |  | Broiling Hamburgers |  |  |  |  | Frying Hamburger |  |  |  |  | Stir-frying Vegetables
|  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name |  |  |  | Alarm | file name
|  | Model-Unit | FFoamG#T# |  |  |  | Model-Unit | SFoamG#T# |  |  |  | Model-Unit | BHBG#T# |  |  |  | Model-Unit | FryHBG#T# |  |  |  | Model-Unit | SFG#T#
|  | PT01-6 | 5,1 | 5,2 | 5,3 |  | PT01-4 | 5,1 | 5,2 | 5,3 |  | PT01-5 | 5,1 | 5,2 | 5,3 |  | PT01-3 | 5,1 | 5,2 | 5,3 |  | PT01-2 | 5,1 | 5,2 | 5,3
Alarm Time (s) |  |  | NA | NA | 238 |  |  | 831 | 738 | 862 |  |  | NA | NA | NA |  |  | 317 | 232 | NA |  |  | 341 | 379 | 397
Obscuration (%/ft) |  |  | 11.149 | 11.744 | 11.77 |  |  | 5.3058 | 4.5757 | 4.5377 |  |  | 1.1856 | 1.4018 | 1.5735 |  |  | 1.3032 | 1.4644 | 1.346 |  |  | 2.5084 | 1.7021 | 1.2935
MIC (pA) |  |  | 19.868 | 18.595 | 20.753 |  |  | 78.848 | 81.94 | 77.076 |  |  | 59.576 | 58.617 | 56.725 |  |  | 79.979 | 82.577 | 81.231 |  |  | 73.51 | 76.306 | 77.697
|  | PT02-6 | 1,1 | 1,2 | 1,3 |  | PT02-4 | 1,1 | 1,2 | 1,3 |  | PT02-5 | 1,1 | 1,2 | 1,3 |  | PT02-3 | 1,1 | 1,1 | 1,1 |  | PT02-2 | 1,1 | 1,1 | 1,1
Alarm Time (s) |  |  | 190 | 179 | 190 |  |  | 924 | 832 | 740 |  |  | 1643 | 1113 | 981 |  |  | 256 | 237 | 263 |  |  | 347 | NA | 391
Obscuration (%/ft) |  |  | 7.0989 | 6.0112 | 5.7681 |  |  | 5.2181 | 2.9576 | 1.7459 |  |  | 1.5814 | 0.9764 | 0.97856 |  |  | 1.6375 | 1.172 | 1.1428 |  |  | 2.3959 | 2.6856 | 0.94573
MIC (pA) |  |  | 56.897 | 47.546 | 44.563 |  |  | 75.262 | 85.457 | 89.503 |  |  | 57.821 | 62.73 | 64.863 |  |  | 81.94 | 85.387 | 85.118 |  |  | 65.318 | 84.635 | 79.954