## License
Tool for Evaluation of Vaporized Hydrogen Peroxide Disinfection of N95 Masks in Rooms
This tool was developed by employees of the National Institute of Standards and Technology (NIST), an agency of the Federal Government, and is being made available as a public service. Pursuant to title 17 United States Code section 105, works of NIST employees are not subject to copyright protection in the United States. This tool may be subject to foreign copyright. Permission in the United States and in foreign countries, to the extent that NIST may hold copyright, to use, copy, modify, create derivative works, and distribute this tool and its documentation without fee is hereby granted on a non-exclusive basis, provided that this notice and disclaimer of warranty appears in all copies
THE TOOL IS PROVIDED 'AS IS' WITHOUT ANY WARRANTY OF ANY KIND, EITHER EXPRESS, IMPLIED, OR STATUTORY, INCLUDING, BUT NOT LIMITED TO, ANY WARRANTY THAT THE TOOL WILL CONFORM TO SPECIFICATIONS, ANY IMPLIED WARRANTIES OF MERCHANTABILITY, FITNESS FOR A PARTICULAR PURPOSE, AND FREEDOM FROM INFRINGEMENT, AND ANY WARRANTY THAT THE DOCUMENTATION WILL CONFORM TO THE TOOL, OR ANY WARRANTY THAT THE TOOL WILL BE ERROR-FREE. IN NO EVENT SHALL NIST BE LIABLE FOR ANY DAMAGES, INCLUDING, BUT NOT LIMITED TO, DIRECT, INDIRECT, SPECIAL OR CONSEQUENTIAL DAMAGES, ARISING OUT OF, RESULTING FROM, OR IN ANY WAY CONNECTED WITH THIS TOOL, WHETHER OR NOT BASED UPON WARRANTY, CONTRACT, TORT, OR OTHERWISE, WHETHER OR NOT INJURY WAS SUSTAINED BY PERSONS OR PROPERTY OR OTHERWISE, AND WHETHER OR NOT LOSS WAS SUSTAINED FROM, OR AROSE OUT OF THE RESULTS OF, OR USE OF, THE TOOL PROVIDED HEREUNDER

## General Room
Tool for Evaluation of Vaporized Hydrogen Peroxide Disinfection of N95 Masks in Rooms
Dustin Poppendieck, dustin.poppendieck@nist.gov, Indoor Air Quality and Ventilation Group, Enginering Lab, National Institute of Standards and Technology
This spreadsheet can be used to estimate the target chemical concentration in air of a single disinfecting room. Inputs include the air change rate, room size, and deposition rates onto materials for the target chemical. The deposition rate data provided below is for vaporized hydrogen peroxide. More information on using this tool can be found at https://doi.org/10.6028/NIST.TN. 2091
Input Data in Green Cells
Calculations in Red Cells
Inputs | [5 empty] | Results
1) Gassing Phase |  |  | Masks |  |  | Maximum predicted room concentration with surface losses, g m-3 |  |  |  |  | 0.52683
Duration, h | 0.33 |  | Diameter, m | 0.15 |  | Maximum predicted room concentration with no surface losses, g m-3 |  |  |  |  | 12.5977
Mechanical Flow, m3 h-1 | 1 |  | Number | 100 |  | Ratio of maximum predicted room concentration with surface deposition and predicted room concentration with no surface deposition |  |  |  |  | 4.182%
Total Air change rate, λ, h-1 | 0.16667
a) In Room Source |  |  | Room |  |  | Cumulative predicted disinfectant dose with surface losses (g m-3 h) |  |  |  |  | 1.0358
Emission source in room E, g h-1 | 120 |  | Length, m | 2 |  | Percent of disinfectant mass injected/emitted into room deposited onto masks |  |  |  |  | 9.089%
b) Injection Source |  |  | Width, m | 3 |  | Percent of disinfectant mass injected/emitted into room deposited onto room surfaces |  |  |  |  | 86.73%
Concentration in injected air, Cinj, g m-3 | 0 |  | Height, m | 2.5
Flow rate of injected air, Qinj, m3 h-1 | 0 |  | Initial Concentration, Cinitial, g m-3 | 0
2) Dwell Phase |  |  | Infiltration rate, λ, h-1 | 0.1
Duration, h | 2.5
Mechanical Flow, m3 h-1 | 1
Total Air change rate, λ, h-1 | 0.16667
a) In Room Source
Emission source in room E, g h-1 | 80
b) Injection Source
Concentration in injected air, Cinj, g m-3 | 0
Flow rate of injected air, Qinj, m3 h-1 | 0
3) Aeration Phase
Duration, h | 0.5
Mechanical Flow, m3 h-1 | 200
Total Air change rate, λ, h-1 | 13.4333
Surfaces | Surface adsorption area, A, m2 | Surface material | Deposition Velocity, Vd, cm h-1 | Vd*A/V, h-1
Walls | 25 | Concrete w/Sealer | 600 | 10
Ceiling | 6 | Concrete | 800 | 3.2
Floor | 6 | VCT | 75 | 0.3
Masks | 3.5343 | Paper/HVAC Duct | 600 | 1.4137
Other Surfaces with Large Areas | 0 | - | 0 | 0
|  |  | Note: Hydrogen Peroxide deposition values determined at air change rate of 2.4 h-1 and a concentration of roughly 1 g m-3. The deposistion value may result in higher mass transfer and deposition values than at lower air change rates. Report for data available upon request. Data published in Indoor Air 2008 Conference Abstracts. R.L. Corsi, H. Hubbard, D. Poppendieck. Hydrogen peroxide vapor as a building disinfectant: Removal to indoor materials and formation of building disinfection by-products |  |  |  | Room volume, V, m3 |  | 15
[7 empty] | Total gassing airflow, m3 h-1 |  | 2.5
[7 empty] | Total dwell airflow, m3 h-1 |  | 2.5
[7 empty] | Total aeration airflow, m3 h-1 |  | 201.5
[7 empty] | Total gassing loss rate, k, h-1 |  | 15.0804
[7 empty] | Total dwell loss rate, k, h-1 |  | 15.0804
[7 empty] | Total aeration loss rate, k, h-1 |  | 28.3471
[7 empty] | Total duration, h |  | 3.33
[7 empty] | Individual mask surface area (both sides), m3 |  | 0.035343
Equations
The model is based upon a Mass Balance for a room accounting for ventilation, source and deposition. Definitions can be found in associated documentation. Each equations is solved for the phase defined above.
Mass Balance
Total Loss rate, h-1
Concentration in room air with deposition to surfaces
Concentration in room air without deposition to sufaces
Cumulative disinfectant dose
Cumulative deposited mass onto surfaces
Calculations
Phase | Time From Initial Injection, h | Phase Time, h | Concentration in room air without loss, g m3 | Concentration in room air with loss, g m-3 | Cumulative disinfectant dose, g m-3 h | Cumulative deposited mass on Walls, g | Cumulative deposited mass on ceiling, g | Cumulative deposited mass on floor, g | Cumulative deposited mass on mask, g | Cumulative deposited mass on other surfaces, g
Gassing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gassing | 0.00825 | 0.00825 | 0.065955 | 0.062059 | 0.0002613 | 0.65648 | 0.21007 | 0.019694 | 0.092808 | 0
Gassing | 0.0165 | 0.0165 | 0.13182 | 0.11686 | 0.001004 | 1.313 | 0.42015 | 0.039389 | 0.18562 | 0
Gassing | 0.02475 | 0.02475 | 0.19759 | 0.16525 | 0.0021719 | 1.9694 | 0.63022 | 0.059083 | 0.27842 | 0
Gassing | 0.033 | 0.033 | 0.26328 | 0.20798 | 0.0037151 | 2.6259 | 0.8403 | 0.078778 | 0.37123 | 0
Gassing | 0.04125 | 0.04125 | 0.32887 | 0.24571 | 0.0055897 | 3.2824 | 1.0504 | 0.098472 | 0.46404 | 0
Gassing | 0.0495 | 0.0495 | 0.39437 | 0.27902 | 0.0077571 | 3.9389 | 1.2604 | 0.11817 | 0.55685 | 0
Gassing | 0.05775 | 0.05775 | 0.45978 | 0.30844 | 0.010183 | 4.5954 | 1.4705 | 0.13786 | 0.64966 | 0
Gassing | 0.066 | 0.066 | 0.52511 | 0.33442 | 0.012837 | 5.2519 | 1.6806 | 0.15756 | 0.74246 | 0
Gassing | 0.07425 | 0.07425 | 0.59034 | 0.35735 | 0.015692 | 5.9083 | 1.8907 | 0.17725 | 0.83527 | 0
Gassing | 0.0825 | 0.0825 | 0.65548 | 0.37761 | 0.018726 | 6.5648 | 2.1007 | 0.19694 | 0.92808 | 0
Gassing | 0.09075 | 0.09075 | 0.72054 | 0.39549 | 0.021916 | 7.2213 | 2.3108 | 0.21664 | 1.0209 | 0
Gassing | 0.099 | 0.099 | 0.7855 | 0.41129 | 0.025246 | 7.8778 | 2.5209 | 0.23633 | 1.1137 | 0
Gassing | 0.10725 | 0.10725 | 0.85038 | 0.42523 | 0.028697 | 8.5343 | 2.731 | 0.25603 | 1.2065 | 0
Gassing | 0.1155 | 0.1155 | 0.91516 | 0.43754 | 0.032257 | 9.1907 | 2.941 | 0.27572 | 1.2993 | 0
Gassing | 0.12375 | 0.12375 | 0.97986 | 0.44842 | 0.035913 | 9.8472 | 3.1511 | 0.29542 | 1.3921 | 0
Gassing | 0.132 | 0.132 | 1.0445 | 0.45802 | 0.039653 | 10.5037 | 3.3612 | 0.31511 | 1.4849 | 0
Gassing | 0.14025 | 0.14025 | 1.109 | 0.4665 | 0.043467 | 11.1602 | 3.5713 | 0.33481 | 1.5777 | 0
Gassing | 0.1485 | 0.1485 | 1.1734 | 0.47398 | 0.047347 | 11.8167 | 3.7813 | 0.3545 | 1.6705 | 0
Gassing | 0.15675 | 0.15675 | 1.2378 | 0.48059 | 0.051286 | 12.4732 | 3.9914 | 0.37419 | 1.7634 | 0
Gassing | 0.165 | 0.165 | 1.302 | 0.48643 | 0.055275 | 13.1296 | 4.2015 | 0.39389 | 1.8562 | 0
Gassing | 0.17325 | 0.17325 | 1.3662 | 0.49159 | 0.05931 | 13.7861 | 4.4116 | 0.41358 | 1.949 | 0
Gassing | 0.1815 | 0.1815 | 1.4303 | 0.49614 | 0.063385 | 14.4426 | 4.6216 | 0.43328 | 2.0418 | 0
Gassing | 0.18975 | 0.18975 | 1.4942 | 0.50016 | 0.067495 | 15.0991 | 4.8317 | 0.45297 | 2.1346 | 0
Gassing | 0.198 | 0.198 | 1.5581 | 0.5037 | 0.071636 | 15.7556 | 5.0418 | 0.47267 | 2.2274 | 0
Gassing | 0.20625 | 0.20625 | 1.622 | 0.50684 | 0.075805 | 16.412 | 5.2519 | 0.49236 | 2.3202 | 0
Gassing | 0.2145 | 0.2145 | 1.6857 | 0.5096 | 0.079998 | 17.0685 | 5.4619 | 0.51206 | 2.413 | 0
Gassing | 0.22275 | 0.22275 | 1.7493 | 0.51205 | 0.084212 | 17.725 | 5.672 | 0.53175 | 2.5058 | 0
Gassing | 0.231 | 0.231 | 1.8129 | 0.51421 | 0.088446 | 18.3815 | 5.8821 | 0.55144 | 2.5986 | 0
Gassing | 0.23925 | 0.23925 | 1.8763 | 0.51611 | 0.092696 | 19.038 | 6.0922 | 0.57114 | 2.6914 | 0
Gassing | 0.2475 | 0.2475 | 1.9397 | 0.51779 | 0.096961 | 19.6945 | 6.3022 | 0.59083 | 2.7842 | 0
Gassing | 0.25575 | 0.25575 | 2.003 | 0.51928 | 0.10124 | 20.3509 | 6.5123 | 0.61053 | 2.877 | 0
Gassing | 0.264 | 0.264 | 2.0662 | 0.52059 | 0.10553 | 21.0074 | 6.7224 | 0.63022 | 2.9699 | 0
Gassing | 0.27225 | 0.27225 | 2.1293 | 0.52175 | 0.10983 | 21.6639 | 6.9324 | 0.64992 | 3.0627 | 0
Gassing | 0.2805 | 0.2805 | 2.1924 | 0.52277 | 0.11414 | 22.3204 | 7.1425 | 0.66961 | 3.1555 | 0
Gassing | 0.28875 | 0.28875 | 2.2553 | 0.52367 | 0.11845 | 22.9769 | 7.3526 | 0.68931 | 3.2483 | 0
Gassing | 0.297 | 0.297 | 2.3182 | 0.52447 | 0.12278 | 23.6334 | 7.5627 | 0.709 | 3.3411 | 0
Gassing | 0.30525 | 0.30525 | 2.3809 | 0.52518 | 0.12711 | 24.2898 | 7.7727 | 0.7287 | 3.4339 | 0
Gassing | 0.3135 | 0.3135 | 2.4436 | 0.5258 | 0.13144 | 24.9463 | 7.9828 | 0.74839 | 3.5267 | 0
Gassing | 0.32175 | 0.32175 | 2.5062 | 0.52635 | 0.13578 | 25.6028 | 8.1929 | 0.76808 | 3.6195 | 0
Gassing | 0.33 | 0.33 | 2.5687 | 0.52683 | 0.14013 | 26.2593 | 8.403 | 0.78778 | 3.7123 | 0
Dwell | 0.3925 | 0.0625 | 2.8737 | 0.42114 | 0.16924 | 32.7733 | 10.4874 | 0.88725 | 4.6332 | 0
Dwell | 0.455 | 0.125 | 3.1755 | 0.37995 | 0.19407 | 37.3351 | 11.9472 | 0.98671 | 5.2781 | 0
Dwell | 0.5175 | 0.1875 | 3.4742 | 0.3639 | 0.21724 | 41.1362 | 13.1636 | 1.0862 | 5.8155 | 0
Dwell | 0.58 | 0.25 | 3.7698 | 0.35765 | 0.23976 | 44.641 | 14.2851 | 1.1856 | 6.311 | 0
Dwell | 0.6425 | 0.3125 | 4.0624 | 0.35522 | 0.26203 | 48.0303 | 15.3697 | 1.2851 | 6.7901 | 0
Dwell | 0.705 | 0.375 | 4.3519 | 0.35427 | 0.28419 | 51.3746 | 16.4399 | 1.3846 | 7.2629 | 0
Dwell | 0.7675 | 0.4375 | 4.6384 | 0.3539 | 0.30632 | 54.7013 | 17.5044 | 1.484 | 7.7332 | 0
Dwell | 0.83 | 0.5 | 4.9219 | 0.35375 | 0.32843 | 58.0212 | 18.5668 | 1.5835 | 8.2026 | 0
Dwell | 0.8925 | 0.5625 | 5.2025 | 0.3537 | 0.35054 | 61.3385 | 19.6283 | 1.683 | 8.6715 | 0
Dwell | 0.955 | 0.625 | 5.4802 | 0.35367 | 0.37265 | 64.6547 | 20.6895 | 1.7824 | 9.1403 | 0
Dwell | 1.0175 | 0.6875 | 5.755 | 0.35367 | 0.39475 | 67.9706 | 21.7506 | 1.8819 | 9.6091 | 0
Dwell | 1.08 | 0.75 | 6.027 | 0.35366 | 0.41686 | 71.2862 | 22.8116 | 1.9814 | 10.0779 | 0
Dwell | 1.1425 | 0.8125 | 6.2961 | 0.35366 | 0.43896 | 74.6018 | 23.8726 | 2.0808 | 10.5466 | 0
Dwell | 1.205 | 0.875 | 6.5625 | 0.35366 | 0.46106 | 77.9174 | 24.9336 | 2.1803 | 11.0153 | 0
Dwell | 1.2675 | 0.9375 | 6.8261 | 0.35366 | 0.48317 | 81.233 | 25.9946 | 2.2798 | 11.484 | 0
Dwell | 1.33 | 1 | 7.087 | 0.35366 | 0.50527 | 84.5486 | 27.0555 | 2.3792 | 11.9528 | 0
Dwell | 1.3925 | 1.0625 | 7.3451 | 0.35366 | 0.52737 | 87.8641 | 28.1165 | 2.4787 | 12.4215 | 0
Dwell | 1.455 | 1.125 | 7.6006 | 0.35366 | 0.54948 | 91.1797 | 29.1775 | 2.5782 | 12.8902 | 0
Dwell | 1.5175 | 1.1875 | 7.8534 | 0.35366 | 0.57158 | 94.4953 | 30.2385 | 2.6777 | 13.359 | 0
Dwell | 1.58 | 1.25 | 8.1037 | 0.35366 | 0.59369 | 97.8108 | 31.2995 | 2.7771 | 13.8277 | 0
Dwell | 1.6425 | 1.3125 | 8.3513 | 0.35366 | 0.61579 | 101.1264 | 32.3604 | 2.8766 | 14.2964 | 0
Dwell | 1.705 | 1.375 | 8.5964 | 0.35366 | 0.63789 | 104.442 | 33.4214 | 2.9761 | 14.7651 | 0
Dwell | 1.7675 | 1.4375 | 8.8389 | 0.35366 | 0.66 | 107.7575 | 34.4824 | 3.0755 | 15.2339 | 0
Dwell | 1.83 | 1.5 | 9.0789 | 0.35366 | 0.6821 | 111.0731 | 35.5434 | 3.175 | 15.7026 | 0
Dwell | 1.8925 | 1.5625 | 9.3164 | 0.35366 | 0.7042 | 114.3886 | 36.6044 | 3.2745 | 16.1713 | 0
Dwell | 1.955 | 1.625 | 9.5515 | 0.35366 | 0.72631 | 117.7042 | 37.6653 | 3.3739 | 16.64 | 0
Dwell | 2.0175 | 1.6875 | 9.7841 | 0.35366 | 0.74841 | 121.0198 | 38.7263 | 3.4734 | 17.1088 | 0
Dwell | 2.08 | 1.75 | 10.0143 | 0.35366 | 0.77052 | 124.3353 | 39.7873 | 3.5729 | 17.5775 | 0
Dwell | 2.1425 | 1.8125 | 10.2421 | 0.35366 | 0.79262 | 127.6509 | 40.8483 | 3.6723 | 18.0462 | 0
Dwell | 2.205 | 1.875 | 10.4676 | 0.35366 | 0.81472 | 130.9665 | 41.9093 | 3.7718 | 18.5149 | 0
Dwell | 2.2675 | 1.9375 | 10.6907 | 0.35366 | 0.83683 | 134.282 | 42.9703 | 3.8713 | 18.9837 | 0
Dwell | 2.33 | 2 | 10.9116 | 0.35366 | 0.85893 | 137.5976 | 44.0312 | 3.9707 | 19.4524 | 0
Dwell | 2.3925 | 2.0625 | 11.1301 | 0.35366 | 0.88103 | 140.9132 | 45.0922 | 4.0702 | 19.9211 | 0
Dwell | 2.455 | 2.125 | 11.3464 | 0.35366 | 0.90314 | 144.2287 | 46.1532 | 4.1697 | 20.3899 | 0
Dwell | 2.5175 | 2.1875 | 11.5604 | 0.35366 | 0.92524 | 147.5443 | 47.2142 | 4.2691 | 20.8586 | 0
Dwell | 2.58 | 2.25 | 11.7722 | 0.35366 | 0.94735 | 150.8599 | 48.2752 | 4.3686 | 21.3273 | 0
Dwell | 2.6425 | 2.3125 | 11.9818 | 0.35366 | 0.96945 | 154.1754 | 49.3361 | 4.4681 | 21.796 | 0
Dwell | 2.705 | 2.375 | 12.1892 | 0.35366 | 0.99155 | 157.491 | 50.3971 | 4.5675 | 22.2648 | 0
Dwell | 2.7675 | 2.4375 | 12.3945 | 0.35366 | 1.0137 | 160.8066 | 51.4581 | 4.667 | 22.7335 | 0
Dwell | 2.83 | 2.5 | 12.5977 | 0.35366 | 1.0358 | 164.1221 | 52.5191 | 4.7665 | 23.2022 | 0
Aeration | 2.8425 | 0.0125 | 10.6504 | 0.24814
Aeration | 2.855 | 0.025 | 9.0041 | 0.17411
Aeration | 2.8675 | 0.0375 | 7.6123 | 0.12216
Aeration | 2.88 | 0.05 | 6.4356 | 0.085711
Aeration | 2.8925 | 0.0625 | 5.4408 | 0.060138
Aeration | 2.905 | 0.075 | 4.5998 | 0.042195
Aeration | 2.9175 | 0.0875 | 3.8888 | 0.029606
Aeration | 2.93 | 0.1 | 3.2877 | 0.020773
Aeration | 2.9425 | 0.1125 | 2.7795 | 0.014575
Aeration | 2.955 | 0.125 | 2.3498 | 0.010226
Aeration | 2.9675 | 0.1375 | 1.9866 | 0.0071751
Aeration | 2.98 | 0.15 | 1.6795 | 0.0050343
Aeration | 2.9925 | 0.1625 | 1.4199 | 0.0035323
Aeration | 3.005 | 0.175 | 1.2004 | 0.0024784
Aeration | 3.0175 | 0.1875 | 1.0149 | 0.0017389
Aeration | 3.03 | 0.2 | 0.858 | 0.0012201
Aeration | 3.0425 | 0.2125 | 0.72537 | 0.00085606
Aeration | 3.055 | 0.225 | 0.61325 | 0.00060065
Aeration | 3.0675 | 0.2375 | 0.51845 | 0.00042144
Aeration | 3.08 | 0.25 | 0.43831 | 0.0002957
Aeration | 3.0925 | 0.2625 | 0.37056 | 0.00020747
Aeration | 3.105 | 0.275 | 0.31328 | 0.00014557
Aeration | 3.1175 | 0.2875 | 0.26486 | 0.00010214
Aeration | 3.13 | 0.3 | 0.22392 | 7.1663e-05
Aeration | 3.1425 | 0.3125 | 0.1893 | 5.0282e-05
Aeration | 3.155 | 0.325 | 0.16004 | 3.5279e-05
Aeration | 3.1675 | 0.3375 | 0.1353 | 2.4753e-05
Aeration | 3.18 | 0.35 | 0.11439 | 1.7368e-05
Aeration | 3.1925 | 0.3625 | 0.096707 | 1.2186e-05
Aeration | 3.205 | 0.375 | 0.081758 | 8.5501e-06
Aeration | 3.2175 | 0.3875 | 0.069121 | 5.9991e-06
Aeration | 3.23 | 0.4 | 0.058436 | 4.2092e-06
Aeration | 3.2425 | 0.4125 | 0.049403 | 2.9533e-06
Aeration | 3.255 | 0.425 | 0.041767 | 2.0722e-06
Aeration | 3.2675 | 0.4375 | 0.035311 | 1.4539e-06
Aeration | 3.28 | 0.45 | 0.029853 | 1.0201e-06
Aeration | 3.2925 | 0.4625 | 0.025238 | 7.1575e-07
Aeration | 3.305 | 0.475 | 0.021337 | 5.022e-07
Aeration | 3.3175 | 0.4875 | 0.018039 | 3.5236e-07
Aeration | 3.33 | 0.5 | 0.01525 | 2.4723e-07

## Shipping Container
Tool for Evaluation of Vaporized Hydrogen Peroxide Disinfection of N95 Masks in Rooms
Dustin Poppendieck, dustin.poppendieck@nist.gov, Indoor Air Quality and Ventilation Group, Enginering Lab, National Institute of Standards and Technology
This spreadsheet can be used to estimate the target chemical concentration in air of a single disinfecting room. Inputs include the air change rate, room size, and deposition rates onto materials for the target chemical. The deposition rate data provided below is for vaporized hydrogen peroxide. More information on using this tool can be found at https://doi.org/10.6028/NIST.TN. 2091
Input Data in Green Cells
Calculations in Red Cells
Inputs | [5 empty] | Results
1) Gassing Phase |  |  | Masks |  |  | Maximum predicted room concentration with surface losses, g m-3 |  |  |  |  | 0.69669
Duration, h | 0.33 |  | Diameter, m | 0.15 |  | Maximum predicted room concentration with no surface losses, g m-3 |  |  |  |  | 7.0577
Mechanical Flow, m3 h-1 | 1 |  | Number | 500 |  | Ratio of maximum predicted room concentration with surface deposition and predicted room concentration with no surface deposition |  |  |  |  | 9.871%
Total Air change rate, λ, h-1 | 0.1463
a) In Room Source |  |  | Room |  |  | Cumulative predicted disinfectant dose with surface losses (g m-3 h) |  |  |  |  | 1.1588
Emission source in room E, g h-1 | 120 |  | Length, m | 3.6 |  | Percent of disinfectant mass injected/emitted into room deposited onto masks |  |  |  |  | 62.59%
b) Injection Source |  |  | Width, m | 2.4 |  | Percent of disinfectant mass injected/emitted into room deposited onto room surfaces |  |  |  |  | 27.54%
Concentration in injected air, Cinj, g m-3 | 0 |  | Height, m | 2.5
Flow rate of injected air, Qinj, m3 h-1 | 0 |  | Initial Concentration, Cinitial, g m-3 | 0
2) Dwell Phase |  |  | Infiltration rate, λ, h-1 | 0.1
Duration, h | 2.5
Mechanical Flow, m3 h-1 | 1
Total Air change rate, λ, h-1 | 0.1463
a) In Room Source
Emission source in room E, g h-1 | 60
b) Injection Source
Concentration in injected air, Cinj, g m-3 | 0
Flow rate of injected air, Qinj, m3 h-1 | 0
3) Aeration Phase
Duration, h | 0.5
Mechanical Flow, m3 h-1 | 200
Total Air change rate, λ, h-1 | 9.3593
Surfaces | Surface adsorption area, A, m2 | Surface material | Deposition Velocity, Vd, cm h-1 | Vd*A/V, h-1
Walls | 30 | Metal File Cabinet | 100 | 1.3889
Ceiling | 8.64 | Metal File Cabinet | 100 | 0.4
Floor | 8.64 | Metal File Cabinet | 100 | 0.4
Masks | 17.6715 | Paper/HVAC Duct | 600 | 4.9087
Other Surfaces with Large Areas | 0 | - | 0 | 0
|  |  | Note: Hydrogen Peroxide deposition values determined at air change rate of 2.4 h-1 and a concentration of roughly 1 g m-3. The deposistion value may result in higher mass transfer and deposition values than at lower air change rates. Report for data available upon request. Data published in Indoor Air 2008 Conference Abstracts. R.L. Corsi, H. Hubbard, D. Poppendieck. Hydrogen peroxide vapor as a building disinfectant: Removal to indoor materials and formation of building disinfection by-products |  |  |  | Room volume, V, m3 |  | 21.6
[7 empty] | Total gassing airflow, m3 h-1 |  | 3.16
[7 empty] | Total dwell airflow, m3 h-1 |  | 3.16
[7 empty] | Total aeration airflow, m3 h-1 |  | 202.16
[7 empty] | Total gassing loss rate, k, h-1 |  | 7.2439
[7 empty] | Total dwell loss rate, k, h-1 |  | 7.2439
[7 empty] | Total aeration loss rate, k, h-1 |  | 16.4569
[7 empty] | Total duration, h |  | 3.33
[7 empty] | Individual mask surface area (both sides), m3 |  | 0.035343
Equations
The model is based upon a Mass Balance for a room accounting for ventilation, source and deposition. Definitions can be found in associated documentation. Each equations is solved for the phase defined above.
Mass Balance
Total Loss rate, h-1
Concentration in room air with deposition to surfaces
Concentration in room air without deposition to sufaces
Cumulative disinfectant dose
Cumulative deposited mass onto surfaces
Calculations
Phase | Time From Initial Injection, h | Phase Time, h | Concentration in room air without loss, g m3 | Concentration in room air with loss, g m-3 | Cumulative disinfectant dose, g m-3 h | Cumulative deposited mass on Walls, g | Cumulative deposited mass on ceiling, g | Cumulative deposited mass on floor, g | Cumulative deposited mass on mask, g | Cumulative deposited mass on other surfaces, g
Gassing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gassing | 0.00825 | 0.00825 | 0.045806 | 0.044491 | 0.00018535 | 0.18981 | 0.054667 | 0.054667 | 0.67086 | 0
Gassing | 0.0165 | 0.0165 | 0.091556 | 0.0864 | 0.000727 | 0.37963 | 0.10933 | 0.10933 | 1.3417 | 0
Gassing | 0.02475 | 0.02475 | 0.13725 | 0.12588 | 0.0016043 | 0.56944 | 0.164 | 0.164 | 2.0126 | 0
Gassing | 0.033 | 0.033 | 0.18289 | 0.16307 | 0.0027977 | 0.75926 | 0.21867 | 0.21867 | 2.6834 | 0
Gassing | 0.04125 | 0.04125 | 0.22848 | 0.1981 | 0.0042889 | 0.94907 | 0.27333 | 0.27333 | 3.3543 | 0
Gassing | 0.0495 | 0.0495 | 0.27401 | 0.2311 | 0.0060607 | 1.1389 | 0.328 | 0.328 | 4.0252 | 0
Gassing | 0.05775 | 0.05775 | 0.31948 | 0.26218 | 0.0080968 | 1.3287 | 0.38267 | 0.38267 | 4.696 | 0
Gassing | 0.066 | 0.066 | 0.3649 | 0.29146 | 0.010382 | 1.5185 | 0.43733 | 0.43733 | 5.3669 | 0
Gassing | 0.07425 | 0.07425 | 0.41027 | 0.31904 | 0.012901 | 1.7083 | 0.492 | 0.492 | 6.0377 | 0
Gassing | 0.0825 | 0.0825 | 0.45558 | 0.34503 | 0.015642 | 1.8981 | 0.54667 | 0.54667 | 6.7086 | 0
Gassing | 0.09075 | 0.09075 | 0.50083 | 0.3695 | 0.01859 | 2.088 | 0.60133 | 0.60133 | 7.3794 | 0
Gassing | 0.099 | 0.099 | 0.54604 | 0.39256 | 0.021734 | 2.2778 | 0.656 | 0.656 | 8.0503 | 0
Gassing | 0.10725 | 0.10725 | 0.59118 | 0.41427 | 0.025064 | 2.4676 | 0.71066 | 0.71066 | 8.7212 | 0
Gassing | 0.1155 | 0.1155 | 0.63628 | 0.43473 | 0.028567 | 2.6574 | 0.76533 | 0.76533 | 9.392 | 0
Gassing | 0.12375 | 0.12375 | 0.68131 | 0.454 | 0.032233 | 2.8472 | 0.82 | 0.82 | 10.0629 | 0
Gassing | 0.132 | 0.132 | 0.7263 | 0.47216 | 0.036055 | 3.037 | 0.87466 | 0.87466 | 10.7337 | 0
Gassing | 0.14025 | 0.14025 | 0.77123 | 0.48926 | 0.040021 | 3.2268 | 0.92933 | 0.92933 | 11.4046 | 0
Gassing | 0.1485 | 0.1485 | 0.8161 | 0.50537 | 0.044125 | 3.4167 | 0.984 | 0.984 | 12.0755 | 0
Gassing | 0.15675 | 0.15675 | 0.86092 | 0.52054 | 0.048357 | 3.6065 | 1.0387 | 1.0387 | 12.7463 | 0
Gassing | 0.165 | 0.165 | 0.90569 | 0.53483 | 0.052711 | 3.7963 | 1.0933 | 1.0933 | 13.4172 | 0
Gassing | 0.17325 | 0.17325 | 0.9504 | 0.5483 | 0.057179 | 3.9861 | 1.148 | 1.148 | 14.088 | 0
Gassing | 0.1815 | 0.1815 | 0.99506 | 0.56098 | 0.061756 | 4.1759 | 1.2027 | 1.2027 | 14.7589 | 0
Gassing | 0.18975 | 0.18975 | 1.0397 | 0.57293 | 0.066434 | 4.3657 | 1.2573 | 1.2573 | 15.4298 | 0
Gassing | 0.198 | 0.198 | 1.0842 | 0.58418 | 0.071207 | 4.5555 | 1.312 | 1.312 | 16.1006 | 0
Gassing | 0.20625 | 0.20625 | 1.1287 | 0.59478 | 0.076071 | 4.7454 | 1.3667 | 1.3667 | 16.7715 | 0
Gassing | 0.2145 | 0.2145 | 1.1732 | 0.60477 | 0.081019 | 4.9352 | 1.4213 | 1.4213 | 17.4423 | 0
Gassing | 0.22275 | 0.22275 | 1.2176 | 0.61418 | 0.086048 | 5.125 | 1.476 | 1.476 | 18.1132 | 0
Gassing | 0.231 | 0.231 | 1.2619 | 0.62304 | 0.091152 | 5.3148 | 1.5307 | 1.5307 | 18.7841 | 0
Gassing | 0.23925 | 0.23925 | 1.3062 | 0.63138 | 0.096327 | 5.5046 | 1.5853 | 1.5853 | 19.4549 | 0
Gassing | 0.2475 | 0.2475 | 1.3504 | 0.63925 | 0.10157 | 5.6944 | 1.64 | 1.64 | 20.1258 | 0
Gassing | 0.25575 | 0.25575 | 1.3946 | 0.64665 | 0.10687 | 5.8842 | 1.6947 | 1.6947 | 20.7966 | 0
Gassing | 0.264 | 0.264 | 1.4387 | 0.65363 | 0.11224 | 6.0741 | 1.7493 | 1.7493 | 21.4675 | 0
Gassing | 0.27225 | 0.27225 | 1.4828 | 0.6602 | 0.11766 | 6.2639 | 1.804 | 1.804 | 22.1383 | 0
Gassing | 0.2805 | 0.2805 | 1.5268 | 0.66639 | 0.12313 | 6.4537 | 1.8587 | 1.8587 | 22.8092 | 0
Gassing | 0.28875 | 0.28875 | 1.5708 | 0.67223 | 0.12865 | 6.6435 | 1.9133 | 1.9133 | 23.4801 | 0
Gassing | 0.297 | 0.297 | 1.6147 | 0.67772 | 0.13422 | 6.8333 | 1.968 | 1.968 | 24.1509 | 0
Gassing | 0.30525 | 0.30525 | 1.6585 | 0.6829 | 0.13983 | 7.0231 | 2.0227 | 2.0227 | 24.8218 | 0
Gassing | 0.3135 | 0.3135 | 1.7023 | 0.68777 | 0.14549 | 7.2129 | 2.0773 | 2.0773 | 25.4926 | 0
Gassing | 0.32175 | 0.32175 | 1.7461 | 0.69236 | 0.15118 | 7.4028 | 2.132 | 2.132 | 26.1635 | 0
Gassing | 0.33 | 0.33 | 1.7898 | 0.69669 | 0.15691 | 7.5926 | 2.1867 | 2.1867 | 26.8344 | 0
Dwell | 0.3925 | 0.0625 | 1.9463 | 0.58264 | 0.19662 | 9.3621 | 2.6963 | 2.3937 | 33.0886 | 0
Dwell | 0.455 | 0.125 | 2.1014 | 0.51011 | 0.2306 | 10.7492 | 3.0958 | 2.6008 | 37.9908 | 0
Dwell | 0.5175 | 0.1875 | 2.2551 | 0.464 | 0.26093 | 11.893 | 3.4252 | 2.8079 | 42.0332 | 0
Dwell | 0.58 | 0.25 | 2.4074 | 0.43467 | 0.28895 | 12.8821 | 3.71 | 3.0149 | 45.529 | 0
Dwell | 0.6425 | 0.3125 | 2.5583 | 0.41603 | 0.31549 | 13.7728 | 3.9666 | 3.222 | 48.6772 | 0
Dwell | 0.705 | 0.375 | 2.7078 | 0.40417 | 0.34109 | 14.6011 | 4.2051 | 3.4291 | 51.6044 | 0
Dwell | 0.7675 | 0.4375 | 2.856 | 0.39663 | 0.3661 | 15.3895 | 4.4322 | 3.6362 | 54.391 | 0
Dwell | 0.83 | 0.5 | 3.0028 | 0.39184 | 0.39073 | 16.1527 | 4.652 | 3.8432 | 57.0882 | 0
Dwell | 0.8925 | 0.5625 | 3.1483 | 0.38879 | 0.41511 | 16.8997 | 4.8671 | 4.0503 | 59.7286 | 0
Dwell | 0.955 | 0.625 | 3.2925 | 0.38685 | 0.43935 | 17.6366 | 5.0793 | 4.2574 | 62.3328 | 0
Dwell | 1.0175 | 0.6875 | 3.4353 | 0.38562 | 0.46348 | 18.3669 | 5.2897 | 4.4644 | 64.9141 | 0
Dwell | 1.08 | 0.75 | 3.5769 | 0.38483 | 0.48756 | 19.0931 | 5.4988 | 4.6715 | 67.4807 | 0
Dwell | 1.1425 | 0.8125 | 3.7172 | 0.38433 | 0.51159 | 19.8167 | 5.7072 | 4.8786 | 70.0381 | 0
Dwell | 1.205 | 0.875 | 3.8562 | 0.38402 | 0.5356 | 20.5386 | 5.9151 | 5.0856 | 72.5896 | 0
Dwell | 1.2675 | 0.9375 | 3.9939 | 0.38382 | 0.5596 | 21.2595 | 6.1227 | 5.2927 | 75.1373 | 0
Dwell | 1.33 | 1 | 4.1303 | 0.38369 | 0.58358 | 21.9797 | 6.3301 | 5.4998 | 77.6826 | 0
Dwell | 1.3925 | 1.0625 | 4.2656 | 0.38361 | 0.60756 | 22.6994 | 6.5374 | 5.7069 | 80.2263 | 0
Dwell | 1.455 | 1.125 | 4.3996 | 0.38355 | 0.63153 | 23.4189 | 6.7446 | 5.9139 | 82.7692 | 0
Dwell | 1.5175 | 1.1875 | 4.5323 | 0.38352 | 0.6555 | 24.1382 | 6.9518 | 6.121 | 85.3114 | 0
Dwell | 1.58 | 1.25 | 4.6639 | 0.3835 | 0.67947 | 24.8574 | 7.1589 | 6.3281 | 87.8532 | 0
Dwell | 1.6425 | 1.3125 | 4.7943 | 0.38349 | 0.70344 | 25.5765 | 7.366 | 6.5351 | 90.3947 | 0
Dwell | 1.705 | 1.375 | 4.9235 | 0.38348 | 0.72741 | 26.2956 | 7.5731 | 6.7422 | 92.9362 | 0
Dwell | 1.7675 | 1.4375 | 5.0515 | 0.38347 | 0.75138 | 27.0146 | 7.7802 | 6.9493 | 95.4775 | 0
Dwell | 1.83 | 1.5 | 5.1783 | 0.38347 | 0.77534 | 27.7336 | 7.9873 | 7.1563 | 98.0187 | 0
Dwell | 1.8925 | 1.5625 | 5.304 | 0.38347 | 0.79931 | 28.4526 | 8.1944 | 7.3634 | 100.5599 | 0
Dwell | 1.955 | 1.625 | 5.4285 | 0.38347 | 0.82328 | 29.1716 | 8.4014 | 7.5705 | 103.1011 | 0
Dwell | 2.0175 | 1.6875 | 5.5519 | 0.38346 | 0.84724 | 29.8906 | 8.6085 | 7.7776 | 105.6423 | 0
Dwell | 2.08 | 1.75 | 5.6742 | 0.38346 | 0.87121 | 30.6096 | 8.8156 | 7.9846 | 108.1834 | 0
Dwell | 2.1425 | 1.8125 | 5.7954 | 0.38346 | 0.89518 | 31.3286 | 9.0226 | 8.1917 | 110.7245 | 0
Dwell | 2.205 | 1.875 | 5.9155 | 0.38346 | 0.91914 | 32.0476 | 9.2297 | 8.3988 | 113.2657 | 0
Dwell | 2.2675 | 1.9375 | 6.0345 | 0.38346 | 0.94311 | 32.7666 | 9.4368 | 8.6058 | 115.8068 | 0
Dwell | 2.33 | 2 | 6.1524 | 0.38346 | 0.96708 | 33.4856 | 9.6439 | 8.8129 | 118.348 | 0
Dwell | 2.3925 | 2.0625 | 6.2692 | 0.38346 | 0.99104 | 34.2046 | 9.8509 | 9.02 | 120.8891 | 0
Dwell | 2.455 | 2.125 | 6.3849 | 0.38346 | 1.015 | 34.9236 | 10.058 | 9.227 | 123.4302 | 0
Dwell | 2.5175 | 2.1875 | 6.4996 | 0.38346 | 1.039 | 35.6426 | 10.2651 | 9.4341 | 125.9714 | 0
Dwell | 2.58 | 2.25 | 6.6133 | 0.38346 | 1.0629 | 36.3616 | 10.4721 | 9.6412 | 128.5125 | 0
Dwell | 2.6425 | 2.3125 | 6.7259 | 0.38346 | 1.0869 | 37.0806 | 10.6792 | 9.8483 | 131.0536 | 0
Dwell | 2.705 | 2.375 | 6.8375 | 0.38346 | 1.1109 | 37.7996 | 10.8863 | 10.0553 | 133.5948 | 0
Dwell | 2.7675 | 2.4375 | 6.9481 | 0.38346 | 1.1348 | 38.5186 | 11.0934 | 10.2624 | 136.1359 | 0
Dwell | 2.83 | 2.5 | 7.0577 | 0.38346 | 1.1588 | 39.2376 | 11.3004 | 10.4695 | 138.677 | 0
Aeration | 2.8425 | 0.0125 | 6.2785 | 0.31217
Aeration | 2.855 | 0.025 | 5.5853 | 0.25412
Aeration | 2.8675 | 0.0375 | 4.9686 | 0.20687
Aeration | 2.88 | 0.05 | 4.4201 | 0.16841
Aeration | 2.8925 | 0.0625 | 3.9321 | 0.1371
Aeration | 2.905 | 0.075 | 3.4979 | 0.11161
Aeration | 2.9175 | 0.0875 | 3.1117 | 0.090855
Aeration | 2.93 | 0.1 | 2.7682 | 0.073962
Aeration | 2.9425 | 0.1125 | 2.4626 | 0.06021
Aeration | 2.955 | 0.125 | 2.1907 | 0.049015
Aeration | 2.9675 | 0.1375 | 1.9488 | 0.039902
Aeration | 2.98 | 0.15 | 1.7337 | 0.032483
Aeration | 2.9925 | 0.1625 | 1.5422 | 0.026443
Aeration | 3.005 | 0.175 | 1.372 | 0.021527
Aeration | 3.0175 | 0.1875 | 1.2205 | 0.017524
Aeration | 3.03 | 0.2 | 1.0857 | 0.014266
Aeration | 3.0425 | 0.2125 | 0.96587 | 0.011613
Aeration | 3.055 | 0.225 | 0.85923 | 0.0094541
Aeration | 3.0675 | 0.2375 | 0.76437 | 0.0076962
Aeration | 3.08 | 0.25 | 0.67998 | 0.0062653
Aeration | 3.0925 | 0.2625 | 0.6049 | 0.0051004
Aeration | 3.105 | 0.275 | 0.53812 | 0.004152
Aeration | 3.1175 | 0.2875 | 0.47871 | 0.00338
Aeration | 3.13 | 0.3 | 0.42585 | 0.0027516
Aeration | 3.1425 | 0.3125 | 0.37884 | 0.00224
Aeration | 3.155 | 0.325 | 0.33701 | 0.0018235
Aeration | 3.1675 | 0.3375 | 0.2998 | 0.0014844
Aeration | 3.18 | 0.35 | 0.2667 | 0.0012084
Aeration | 3.1925 | 0.3625 | 0.23726 | 0.00098376
Aeration | 3.205 | 0.375 | 0.21106 | 0.00080084
Aeration | 3.2175 | 0.3875 | 0.18776 | 0.00065194
Aeration | 3.23 | 0.4 | 0.16703 | 0.00053073
Aeration | 3.2425 | 0.4125 | 0.14859 | 0.00043205
Aeration | 3.255 | 0.425 | 0.13218 | 0.00035172
Aeration | 3.2675 | 0.4375 | 0.11759 | 0.00028632
Aeration | 3.28 | 0.45 | 0.10461 | 0.00023308
Aeration | 3.2925 | 0.4625 | 0.093057 | 0.00018975
Aeration | 3.305 | 0.475 | 0.082783 | 0.00015447
Aeration | 3.3175 | 0.4875 | 0.073643 | 0.00012575
Aeration | 3.33 | 0.5 | 0.065513 | 0.00010237